## UNIT#1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | ALA84CF1_1 | ALA84CF1_1 | 11HLA84CF101 | Lower CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
2 | Manipulated Variable | Secondary Air Flow | ALA85CF1_1 | ALA85CF1_1 | 11HLA85CF101 | Upper CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
3 | Disturbance Variable | Coal Flow | AFY10FF001 | AFY10FF001 | 11HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
4 | Disturbance Variable | Coal Flow | AFY20FF001 | AFY20FF001 | 11HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
5 | Disturbance Variable | Load | AC02FE001 | AC02FE001 | 11BAB02FE001 | Generator Active Power | AI | 0 | 45.5 | MW
6 | Disturbance Variable | Primary Air Flow | ALA15CF1_1 | ALA15CF1_1 | 11HLA15CF101 | Sponge Coal Feeder Air Flow | AI | 0 | 5500 | Nm3/h
7 | Disturbance Variable | Primary Air Flow | ALA50CF1_1 | ALA50CF1_1 | 11HLA50CF101 | Feeder Air Flow | AI | 0 | 9000 | NmJ/h
8 | Disturbance Variable | Primary Air Flow | ALA31CF1_1 | ALA31CF1_1 | 11HLA31CF101 | Duct Ignition Burner 1 Air Flow | AI | 0 | 40000 | Nm3/h
9 | Disturbance Variable | Primary Air Flow | ALA32CF1_1 | ALA32CF1_1 | 11HLA32CF101 | Duct Ignition Burner 2 Air Flow | AI | 0 | 40000 | Nm3/h
10 | Constrain Variable | Oxygen Sensor | ANA20CQ101 | ANA20CQ101 | 11HNA20CQ101 | Primary superheater outlet Oxygen(left) | AI | 0 | 25 | %
11 | Constrain Variable | Oxygen Sensor | ANA20CQ102 | ANA20CQ102 | 11HNA20CQ102 | Primary superheater outlet Oxygen(right) | AI | 0 | 25 | %
12 | Constrain Variable | Furnace Pressure | ABK10CP107 | ABK10CP107 | 11HBK10CP107 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
13 | Constrain Variable | Furnace Pressure | ABK10CP108 | ABK10CP108 | 11HBK10CP108 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
14 | Constrain Variable | Furnace Pressure | ABK10CP109 | ABK10CP109 | 11HBK10CP109 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
15 | Constrain Variable | Furnace Pressure | ABK10CP110 | ABK10CP110 | 11HBK10CP110 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
16 | Constrain Variable | Furnace Pressure | ABK10CP111 | ABK10CP111 | 11HBK10CP111 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
17 | Constrain Variable | Furnace Pressure | ABK10CP112 | ABK10CP112 | 11HBK10CP112 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
18 | Constrain Variable | Bed Differential Pressure | ABK10DP105 | ABK10DP105 | 11HBK10DP105 | Furnace DP.(left) | AI | -5 | 5 | KPa
19 | Constrain Variable | Bed Differential Pressure | ABK10DP106 | ABK10DP106 | 11HBK10DP106 | Furnace D.P.(right) | AI | -5 | 5 | KPa
20 | Constrain Variable | Bed Temperature | ABK10T621A | ABK10T621A | 11HBK10CT621A | Furnace bed temperature 1a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
21 | Constrain Variable | Bed Temperature | ABK10T621B | ABK10T621B | 11HBK10CT621B | Furnace bed temperature 1b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
22 | Constrain Variable | Bed Temperature | ABK10T622A | ABK10T622A | 11HBK10CT622A | Furnace bed temperature 2a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
23 | Constrain Variable | Bed Temperature | ABK10T622B | ABK10T622B | 11HBK10CT622B | Furnace bed temperature 2b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
24 | Constrain Variable | Bed Temperature | ABK10T623A | ABK10T623A | 11HBK10CT623A | Furnace bed temperature 3a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
25 | Constrain Variable | Bed Temperature | ABK10T623B | ABK10T623B | 11HBK10CT623B | Furnace bed temperature 3b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
26 | Constrain Variable | Bed Temperature | ABK10T624A | ABK10T624A | 11HBK10CT624A | Furnace bed temperature 4a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
27 | Constrain Variable | Bed Temperature | ABK10T624B | ABK10T624B | 11HBK10CT624B | Furnace bed temperature 4b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
28 | Constrain Variable | Bed Temperature | ABK10T625A | ABK10T625A | 11HBK10CT625A | Furnace bed temperature 5a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
29 | Constrain Variable | Bed Temperature | ABK10T625B | ABK10T625B | 11HBK10CT625B | Furnace bed temperature 5b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
30 | Constrain Variable | Bed Temperature | ABK10T626A | ABK10T626A | 11HBK10CT626A | Furnace bed temperature 6a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
31 | Constrain Variable | Bed Temperature | ABK10T626B | ABK10T626B | 11HBK10CT626B | Furnace bed temperature 6b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
32 | Constrain Variable | Bed Temperature | ABK10T627A | ABK10T627A | 11HBK10CT627A | Furnace bed temperature 7a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
33 | Constrain Variable | Bed Temperature | ABK10T627B | ABK10T627B | 11HBK10CT627B | Furnace bed temperature 7b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
34 | Constrain Variable | Bed Temperature | ABK10T628A | ABK10T628A | 11HBK10CT628A | Furnace bed temperature 8a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
35 | Constrain Variable | Bed Temperature | ABK10T628B | ABK10T628B | 11HBK10CT628B | Furnace bed temperature 8b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
36 | Constrain Variable | Bed Temperature | ABK10T629A | ABK10T629A | 11HBK10CT629A | Furnace bed temperature 9a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
37 | Constrain Variable | Bed Temperature | ABK10T629B | ABK10T629B | 11HBK10CT629B | Furnace bed temperature 9b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
38 | Constrain Variable | Bed Temperature | ABK10T630A | ABK10T630A | 11HBK10CT630A | Furnace bed temperature 10a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
39 | Constrain Variable | Bed Temperature | ABK10T630B | ABK10T630B | 11HBK10CT630B | Furnace bed temperature 10b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
40 | Constrain Variable | Bed Temperature | ABK10T631A | ABK10T631A | 11HBK10CT631A | Furnace bed temperature 11a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
41 | Constrain Variable | Bed Temperature | ABK10T631B | ABK10T631B | 11HBK10CT631B | Furnace bed temperature 11b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
42 | Constrain Variable | Bed Temperature | ABK10T632A | ABK10T632A | 11HBK10CT632A | Furnace bed temperature 12a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
43 | Constrain Variable | Bed Temperature | ABK10T632B | ABK10T632B | 11HBK10CT632B | Furnace bed temperature 12b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
44 | Constrain Variable | Furnace Temperature | ABK10CT611 | ABK10CT611 | 11HBK10CT611 | Furnace outlet temperature(left) | AI | 0 | 1200 | °C
45 | Constrain Variable | Furnace Temperature | ABK10CT612 | ABK10CT612 | 11HBK10CT612 | Furnace outlet temperature(right) | AI | 0 | 1200 | °C
46 | Constrain Variable | Stack NOx | ANE31CQ103 | ANE31CQ103 | 11HNE31CQ103 | Stack flue gas NOx | AI | 0 | 1200 | mg/Nm
47 | Constrain Variable | Stack CO | ANE31CQ102 | ANE31CQ102 | 11HNE31CQ102 | Stack flue gas CO | AI | 0 | 1400 | mg/Nm
48 | Efficiency Variable | Coal Flow | AFY10FF001 | AFY10FF001 | 11HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
49 | Efficiency Variable | Coal Flow | AFY20FF001 | AFY20FF001 | 11HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
50 | Efficiency Variable | Main Steam Pressure | ABA10CP101 | ABA10CP101 | 11LBA10CP101 | Boiler outlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
51 | Efficiency Variable | Main Steam Pressure | ABA10CP113 | ABA10CP113 | 11LBA10CP113 | Turbine inlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
52 | Efficiency Variable | Feed Water Pressure | AAB10CP121 | AAB10CP121 | 11LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
53 | Efficiency Variable | Feed Water Pressure | AAB10CP122 | AAB10CP122 | 11LAB10CP122 | Economizer inlet water pressure | AI | 0 | 20 | MPa
54 | Efficiency Variable | SH Spray Water Pressure | AAB10CP121 | AAB10CP121 | 11LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
55 | Efficiency Variable | Main Steam Temperature | ABA10CT601 | ABA10CT601 | 11LBA10CT601 | Boiler outlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
56 | Efficiency Variable | Main Steam Temperature | ABA10CT611 | ABA10CT611 | 11LBA10CT611 | Turbine inlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
57 | Efficiency Variable | Feed Water Temperature | AAB10T621 | AAB10T621 | 11LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
58 | Efficiency Variable | Feed Water Temperature | AAB10T622 | AAB10T622 | 11LAB10CT622 | Economizer inlet water temperature | AI | 0 | 600 | °C
59 | Efficiency Variable | SH Spray Temperature | AAB10T621 | AAB10T621 | 11LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
60 | Efficiency Variable | Main Steam Flow | ABA10CF101 | ABA10CF101 | 11LBA10CF101 | Main steam flow | AI | 0 | 150 | t/h
61 | Efficiency Variable | Feed Water Flow | AAB10CF1_1 | AAB10CF1_1 | 11LAB10CF121 | Main feedwater flow | AI | 0 | 150 | t/h
62 | Efficiency Variable | SH Spray Water Flow | A_B10CF131 | A_B10CF131 | 11LAB10CF131 | First stage desuperheater spray water flow | AI | 0 | 8 | t/h
63 | Efficiency Variable | SH Spray Water Flow | A_B10CF141 | A_B10CF141 | 11LAB10CF141 | Second stage desuperheater spray water flow | AI | 0 | 8 | t/h
64 | Control Variable | FD Fan Air Flow | AL81A101MV | AL81A101MV | 11HLA81AA101AO | Second air fan inlet control damp control | AO | 0 | 100 | %

## UNIT#2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | BLA84CF1_1 | BLA84CF1_1 | 12HLA84CF101 | Lower CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
2 | Manipulated Variable | Secondary Air Flow | BLA85CF1_1 | BLA85CF1_1 | 12HLA85CF101 | Upper CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
3 | Disturbance Variable | Coal Flow | BFY10FF001 | BFY10FF001 | 12HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
4 | Disturbance Variable | Coal Flow | BFY20FF001 | BFY20FF001 | 12HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
5 | Disturbance Variable | Load | BC02FE001 | BC02FE001 | 12BAB02FE001 | Generator Active Power | AI | 0 | 45.5 | MW
6 | Disturbance Variable | Primary Air Flow | BLA15CF1_1 | BLA15CF1_1 | 12HLA15CF101 | Sponge Coal Feeder Air Flow | AI | 0 | 5500 | Nm3/h
7 | Disturbance Variable | Primary Air Flow | BLA50CF1_1 | BLA50CF1_1 | 12HLA50CF101 | Feeder Air Flow | AI | 0 | 9000 | NmJ/h
8 | Disturbance Variable | Primary Air Flow | BLA31CF1_1 | BLA31CF1_1 | 12HLA31CF101 | Duct Ignition Burner 1 Air Flow | AI | 0 | 40000 | Nm3/h
9 | Disturbance Variable | Primary Air Flow | BLA32CF1_1 | BLA32CF1_1 | 12HLA32CF101 | Duct Ignition Burner 2 Air Flow | AI | 0 | 40000 | Nm3/h
10 | Constrain Variable | Oxygen Sensor | BNA20CQ101 | BNA20CQ101 | 12HNA20CQ101 | Primary superheater outlet Oxygen(left) | AI | 0 | 25 | %
11 | Constrain Variable | Oxygen Sensor | BNA20CQ102 | BNA20CQ102 | 12HNA20CQ102 | Primary superheater outlet Oxygen(right) | AI | 0 | 25 | %
12 | Constrain Variable | Furnace Pressure | BBK10CP107 | BBK10CP107 | 12HBK10CP107 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
13 | Constrain Variable | Furnace Pressure | BBK10CP108 | BBK10CP108 | 12HBK10CP108 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
14 | Constrain Variable | Furnace Pressure | BBK10CP109 | BBK10CP109 | 12HBK10CP109 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
15 | Constrain Variable | Furnace Pressure | BBK10CP110 | BBK10CP110 | 12HBK10CP110 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
16 | Constrain Variable | Furnace Pressure | BBK10CP111 | BBK10CP111 | 12HBK10CP111 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
17 | Constrain Variable | Furnace Pressure | BBK10CP112 | BBK10CP112 | 12HBK10CP112 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
18 | Constrain Variable | Bed Differential Pressure | BBK10DP105 | BBK10DP105 | 12HBK10DP105 | Furnace DP.(left) | AI | -5 | 5 | KPa
19 | Constrain Variable | Bed Differential Pressure | BBK10DP106 | BBK10DP106 | 12HBK10DP106 | Furnace D.P.(right) | AI | -5 | 5 | KPa
20 | Constrain Variable | Bed Temperature | BBK10T621A | BBK10T621A | 12HBK10CT621A | Furnace bed temperature 1a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
21 | Constrain Variable | Bed Temperature | BBK10T621B | BBK10T621B | 12HBK10CT621B | Furnace bed temperature 1b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
22 | Constrain Variable | Bed Temperature | BBK10T622A | BBK10T622A | 12HBK10CT622A | Furnace bed temperature 2a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
23 | Constrain Variable | Bed Temperature | BBK10T622B | BBK10T622B | 12HBK10CT622B | Furnace bed temperature 2b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
24 | Constrain Variable | Bed Temperature | BBK10T623A | BBK10T623A | 12HBK10CT623A | Furnace bed temperature 3a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
25 | Constrain Variable | Bed Temperature | BBK10T623B | BBK10T623B | 12HBK10CT623B | Furnace bed temperature 3b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
26 | Constrain Variable | Bed Temperature | BBK10T624A | BBK10T624A | 12HBK10CT624A | Furnace bed temperature 4a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
27 | Constrain Variable | Bed Temperature | BBK10T624B | BBK10T624B | 12HBK10CT624B | Furnace bed temperature 4b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
28 | Constrain Variable | Bed Temperature | BBK10T625A | BBK10T625A | 12HBK10CT625A | Furnace bed temperature 5a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
29 | Constrain Variable | Bed Temperature | BBK10T625B | BBK10T625B | 12HBK10CT625B | Furnace bed temperature 5b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
30 | Constrain Variable | Bed Temperature | BBK10T626A | BBK10T626A | 12HBK10CT626A | Furnace bed temperature 6a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
31 | Constrain Variable | Bed Temperature | BBK10T626B | BBK10T626B | 12HBK10CT626B | Furnace bed temperature 6b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
32 | Constrain Variable | Bed Temperature | BBK10T627A | BBK10T627A | 12HBK10CT627A | Furnace bed temperature 7a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
33 | Constrain Variable | Bed Temperature | BBK10T627B | BBK10T627B | 12HBK10CT627B | Furnace bed temperature 7b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
34 | Constrain Variable | Bed Temperature | BBK10T628A | BBK10T628A | 12HBK10CT628A | Furnace bed temperature 8a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
35 | Constrain Variable | Bed Temperature | BBK10T628B | BBK10T628B | 12HBK10CT628B | Furnace bed temperature 8b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
36 | Constrain Variable | Bed Temperature | BBK10T629A | BBK10T629A | 12HBK10CT629A | Furnace bed temperature 9a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
37 | Constrain Variable | Bed Temperature | BBK10T629B | BBK10T629B | 12HBK10CT629B | Furnace bed temperature 9b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
38 | Constrain Variable | Bed Temperature | BBK10T630A | BBK10T630A | 12HBK10CT630A | Furnace bed temperature 10a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
39 | Constrain Variable | Bed Temperature | BBK10T630B | BBK10T630B | 12HBK10CT630B | Furnace bed temperature 10b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
40 | Constrain Variable | Bed Temperature | BBK10T631A | BBK10T631A | 12HBK10CT631A | Furnace bed temperature 11a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
41 | Constrain Variable | Bed Temperature | BBK10T631B | BBK10T631B | 12HBK10CT631B | Furnace bed temperature 11b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
42 | Constrain Variable | Bed Temperature | BBK10T632A | BBK10T632A | 12HBK10CT632A | Furnace bed temperature 12a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
43 | Constrain Variable | Bed Temperature | BBK10T632B | BBK10T632B | 12HBK10CT632B | Furnace bed temperature 12b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
44 | Constrain Variable | Furnace Temperature | BBK10CT611 | BBK10CT611 | 12HBK10CT611 | Furnace outlet temperature(left) | AI | 0 | 1200 | °C
45 | Constrain Variable | Furnace Temperature | BBK10CT612 | BBK10CT612 | 12HBK10CT612 | Furnace outlet temperature(right) | AI | 0 | 1200 | °C
46 | Constrain Variable | Stack NOx | BNE31CQ103 | BNE31CQ103 | 12HNE31CQ103 | Stack flue gas NOx | AI | 0 | 1200 | mg/Nm
47 | Constrain Variable | Stack CO | BNE31CQ102 | BNE31CQ102 | 12HNE31CQ102 | Stack flue gas CO | AI | 0 | 1400 | mg/Nm
48 | Efficiency Variable | Coal Flow | BFY10FF001 | BFY10FF001 | 12HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
49 | Efficiency Variable | Coal Flow | BFY20FF001 | BFY20FF001 | 12HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
50 | Efficiency Variable | Main Steam Pressure | BBA10CP101 | BBA10CP101 | 12LBA10CP101 | Boiler outlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
51 | Efficiency Variable | Main Steam Pressure | BBA10CP113 | BBA10CP113 | 12LBA10CP113 | Turbine inlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
52 | Efficiency Variable | Feed Water Pressure | BAB10CP121 | BAB10CP121 | 12LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
53 | Efficiency Variable | Feed Water Pressure | BAB10CP122 | BAB10CP122 | 12LAB10CP122 | Economizer inlet water pressure | AI | 0 | 20 | MPa
54 | Efficiency Variable | SH Spray Water Pressure | BAB10CP121 | BAB10CP121 | 12LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
55 | Efficiency Variable | Main Steam Temperature | BBA10CT601 | BBA10CT601 | 12LBA10CT601 | Boiler outlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
56 | Efficiency Variable | Main Steam Temperature | BBA10CT611 | BBA10CT611 | 12LBA10CT611 | Turbine inlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
57 | Efficiency Variable | Feed Water Temperature | BAB10T621 | BAB10T621 | 12LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
58 | Efficiency Variable | Feed Water Temperature | BAB10T622 | BAB10T622 | 12LAB10CT622 | Economizer inlet water temperature | AI | 0 | 600 | °C
59 | Efficiency Variable | SH Spray Temperature | BAB10T621 | BAB10T621 | 12LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
60 | Efficiency Variable | Main Steam Flow | BBA10CF101 | BBA10CF101 | 12LBA10CF101 | Main steam flow | AI | 0 | 150 | t/h
61 | Efficiency Variable | Feed Water Flow | BAB10CF1_1 | BAB10CF1_1 | 12LAB10CF121 | Main feedwater flow | AI | 0 | 150 | t/h
62 | Efficiency Variable | SH Spray Water Flow | B_B10CF131 | B_B10CF131 | 12LAB10CF131 | First stage desuperheater spray water flow | AI | 0 | 8 | t/h
63 | Efficiency Variable | SH Spray Water Flow | B_B10CF141 | B_B10CF141 | 12LAB10CF141 | Second stage desuperheater spray water flow | AI | 0 | 8 | t/h
64 | Control Variable | FD Fan Air Flow | BL81A101MV | BL81A101MV | 12HLA81AA101AO | Second air fan inlet control damp control | AO | 0 | 100 | %

## Master TAG (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARK
1 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1A | WIKA-07NP08-ABD-305-20-014-01 | AAB01CL103 | AAB01CL103 | 11PAB01CL103 | NO.1 Circulating water pump inlet suction well level | AI | 0 | 8 | m |  | 1.68 | 1.78
2 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1A | WIKA-07NP08-ABD-305-20-014-01 | AAB01CE010 | AAB01CE010 | 11PAB01CE010 | No.1 circulating water pump motor current | AI | 0 | 200 | A
3 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1A | WIKA-07NP08-ABD-305-20-014-01 | APAC1CT01 | APAC1CT01 | 11PAB01CT010 | No.1 circulating water pump motor temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
4 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1B | WIKA-07NP08-ABD-305-20-014-01 | AAB02CL103 | AAB02CL103 | 11PAB02CL103 | NO.2 Circulating water pump inlet suction well level | AI | 0 | 8 | m |  | 1.68 | 1.78
5 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1B | WIKA-07NP08-ABD-305-20-014-01 | AAB02CE010 | AAB02CE010 | 11PAB02CE010 | No.2 circulating water pump motor current | AI | 0 | 200 | A
6 | 1 | UJLJ AMG #1 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #1B | WIKA-07NP08-ABD-305-20-014-01 | APAC2CT01 | APAC2CT01 | 11PAB02CT010 | No.2 circulating water pump motor temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
7 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 3 | CLARIFIER | WIKA-07NP08-ABD-305-20-016-P001 | PH_01 | PH_01 | 10GCB01CQ001 | Chemical Tank PH Transmitter PH Measuring | AI | 0 | 14 | pH
8 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 4 | CLEAR WATER POND | WIKA-07NP08-ABD-305-20-016-P001 | PT_17 | PT_17 | 10GCL01CP001A | Clear Water Pond Level Transmitter Level of Tank | AI | 0 | 100 | %
9 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 5 | FILTER FEED (MULTIMEDIA FILTER) | WIKA-07NP08-ABD-305-20-002-P001 | PH_02 | PH_02 | 10GCB10CQ001 | Multimedia PH Transmitter PH Measuring | AI | 0 | 14 | pH
10 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 5 | FILTER FEED (MULTIMEDIA FILTER) | WIKA-07NP08-ABD-305-20-002-P001 | ORP_01 | ORP_01 | 10GCB10CQ002 | Multimedia Filter Oxidation Recduction Potential measuring | AI | -2000 | 2000 | mV
11 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 5 | FILTER FEED (MULTIMEDIA FILTER) | WIKA-07NP08-ABD-305-20-002-P001 | CE_01 | CE_01 | 10GCB10CQ003 | Multimedia Filter Conductivity measuring | AI | 0 | 100 | uS
12 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | PT_04 | PT_04 | 10GCF01CP004A | SWRO 1 HPP Pressure Transmitter Pressure Measuring | AI | 0 | 60 | Bar
13 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | PT_02 | PT_02 | 10GCF01CP005A | SWRO 1 Recycle Pressure Transmitter Pressure Measuring | AI | 0 | 60 | Bar
14 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | PT_06 | PT_06 | 10GCF01CP009A | SWRO 1 Concentrate Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
15 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | CGF01CQ02A | CGF01CQ02A | 10GCF01CQ002A | SWRO 1 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
16 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | FE_02 | FE_02 | 10GCF01CP003B | Flow Inlet SWRO 1 | AI | 0 | 50 | t/h
17 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1A | WIKA-07NP08-ABD-305-20-002-P001 | FE_01 | FE_01 | 10GCF01CP008B | Flow Outlet SWRO 1 | AI | 0 | 50 | t/h
18 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | PT_05 | PT_05 | 10GCF02CP004A | SWRO 2 HPP Pressure Transmitter Pressure Measuring | AI | 0 | 60 | Bar
19 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | PT_03 | PT_03 | 10GCF02CP005A | SWRO 2 Recycle Pressure Transmitter Pressure Measuring | AI | 0 | 60 | Bar
20 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | PT_07 | PT_07 | 10GCF02CP009A | SWRO 2 Concentrate Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
21 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | CGF02CQ02A | CGF02CQ02A | 10GCF02CQ002A | SWRO 2 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
22 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | FE_04 | FE_04 | 10GCF02CP003B | Flow Inlet SWRO 2 | AI | 0 | 50 | t/h
23 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 6 | SEA WATER RO #1B | WIKA-07NP08-ABD-305-20-002-P001 | FE_03 | FE_03 | 10GCF02CP008B | Flow Outlet SWRO 2 | AI | 0 | 50 | t/h
24 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 7 | FRESH WATER TANK | WIKA-07NP08-ABD-305-20-002-P001 | PT_08 | PT_08 | 10GCL01CP002 | Fresh Water Tank Level Transmitter Level of Tank | AI | 0 | 100 | %
25 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 9 | CARTRIDGE FILTER #1A | WIKA-07NP08-ABD-305-20-002-P002 | FE_09 | FE_09 | 10GCF10CP003B | Cartridge Filter 1 Flow Inlet | AI | 0 | 50 | t/h
26 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 9 | CARTRIDGE FILTER #1B | WIKA-07NP08-ABD-305-20-002-P002 | FE_06 | FE_06 | 10GCF11CP003B | Cartridge Filter 2 Flow Inlet | AI | 0 | 50 | t/h
27 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1A | WIKA-07NP08-ABD-305-20-002-P002 | CGF10CP04A | CGF10CP04A | 10GCF10CP004A | BWRO 1 HPP Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
28 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1A | WIKA-07NP08-ABD-305-20-002-P002 | CGF10CP07A | CGF10CP07A | 10GCF10CP007A | BWRO 1 Concentrate Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
29 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1A | WIKA-07NP08-ABD-305-20-002-P002 | CGF10CQ02A | CGF10CQ02A | 10GCF10CQ002A | BWRO 1 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
30 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1A | WIKA-07NP08-ABD-305-20-002-P002 | FE_10 | FE_10 | 10GCF10CP006B | BWRO 1 Flow Outlet | AI | 0 | 50 | t/h
31 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1B | WIKA-07NP08-ABD-305-20-002-P002 | CGF11CP04A | CGF11CP04A | 10GCF11CP004A | BWRO 2 HPP Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
32 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1B | WIKA-07NP08-ABD-305-20-002-P002 | CGF11CP07A | CGF11CP07A | 10GCF11CP007A | BWRO 1 Concentrate Pressure Transmitter Pressure Measuring | AI | 0 | 6 | Bar
33 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1B | WIKA-07NP08-ABD-305-20-002-P002 | CGF11CQ02A | CGF11CQ02A | 10GCF11CQ002A | BWRO 2 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
34 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1B | WIKA-07NP08-ABD-305-20-002-P002 | FE_07 | FE_07 | 10GCF11CP006B | BWRO 2 Flow Outlet | AI | 0 | 50 | t/h
35 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 11 | BWRO #1B | WIKA-07NP08-ABD-305-20-002-P002 | CGCL01CQ01 | CGCL01CQ01 | 10GCL01CQ001 | BWRO 2 PH Transmitter PH Measuring Outlet | AI | 0 | 14 | pH
36 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Thick Water Pond) | WIKA-07NP08-ABD-305-20-002-P002 | PT_13 | PT_13 | 10GCL01CP004A | Thick Water Pond Level Transmitter Level of Tank | AI | 0 | 100 | %
37 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Industrial Water Tank 1) | WIKA-07NP08-ABD-305-20-002-P002 | PT_14 | PT_14 | 10GCL01CP005A | Industrial Water Tank 1 Level Transmitter Level of Tank | AI | 0 | 100 | %
38 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Industrial Water Tank 2) | WIKA-07NP08-ABD-305-20-002-P002 | PT_19 | PT_19 | 10GCL01CP006A | Industrial Water Tank 2 Level Transmitter Level of Tank | AI | 0 | 100 | %
39 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK | WIKA-07NP08-ABD-305-20-002-P002 | PT_15 | PT_15 | 10GCL01CP008A | Demin Tank Level Transmitter Level of Tank | AI | 0 | 100 | %
40 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK | WIKA-07NP08-ABD-305-20-002-P002 | FE_08 | FE_08 | 10GCL01CP011B | Demin Tank Flow Inlet | AI | 0 | 50 | t/h
41 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Polisher Water Tank 1) | WIKA-07NP08-ABD-305-20-003-P002 | PT_18 | PT_18 | 10GCL01CP009A | Polisher Water Tank 1 Level Transmitter Level of Tank | AI | 0 | 100 | %
42 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Polisher Water Tank 2) | WIKA-07NP08-ABD-305-20-003-P002 | PT_16 | PT_16 | 10GCL01CP010A | Polisher Water Tank 2 Level Transmitter Level of Tank | AI | 0 | 100 | %
43 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Mixed Bed 1) | WIKA-07NP08-ABD-305-20-003-P002 | CE_06 | CE_06 | 10GCF40CQ003B | Mixed Bed 1 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
44 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Mixed Bed 2) | WIKA-07NP08-ABD-305-20-003-P002 | CE_07 | CE_07 | 10GCF41CQ003B | Mixed Bed 2 Conductivity Transmitter Conductivity Measuring | AI | 0 | 200 | uS
45 | 1 | UJLJ AMG #1 | 3 | WATER TREATMENT PLANT | 12 | DEMIN TANK (Mixed Bed) | WIKA-07NP08-ABD-305-20-003-P002 | FE_11 | FE_11 | 10GCL01CP012B | Mixed Bed Flow Outlet | AI | 0 | 50 | t/h
46 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #1 | WIKA-07NP08-ABD-300-20-002 | DEAC10CS1 | DEAC10CS1 | 10EAC10CS001 | SPEED SENSOR FOR BELT CONVEYOR 1A | AI | 0 | 300 | RPM
47 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #1 | WIKA-07NP08-A8D-300-20-002 | DEAC10CS2 | DEAC10CS2 | 10EAC10CS002 | SPEED SENSOR FOR BELT CONVEYOR 1B | AI | 0 | 300 | RPM
48 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #2 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS03 | DEAC10CS03 | 10EAC10CS003 | SPEED SENSOR FOR BELT CONVEYOR 2A | AI | 0 | 300 | RPM
49 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #2 | WIKA-07NP08-A8D-300-20-003 | DEAC10CS04 | DEAC10CS04 | 10EAC10CS004 | SPEED SENSOR FOR BELT CONVEYOR 2B | AI | 0 | 300 | RPM
50 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #3 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS05 | DEAC10CS05 | 10EAC10CS005 | SPEED SENSOR FOR BELT CONVEYOR 3A | AI | 0 | 300 | RPM
51 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #3 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS06 | DEAC10CS06 | 10EAC10CS006 | SPEED SENSOR FOR BELT CONVEYOR 3B | AI | 0 | 300 | RPM
52 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #3 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS07 | DEAC10CS07 | 10EAC10CS007 | SPEED SENSOR FOR BELT CONVEYOR 3C | AI | 0 | 300 | RPM
53 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #3 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS08 | DEAC10CS08 | 10EAC10CS008 | SPEED SENSOR FOR BELT CONVEYOR 3D | AI | 0 | 300 | RPM
54 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #4 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS09 | DEAC10CS09 | 10EAC10CS009 | SPEED SENSOR FOR BELT CONVEYOR 4A | AI | 0 | 300 | RPM
55 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #4 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS10 | DEAC10CS10 | 10EAC10CS010 | SPEED SENSOR FOR BELT CONVEYOR 4B | AI | 0 | 300 | RPM
56 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #5 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS11 | DEAC10CS11 | 10EAC10CS011 | SPEED SENSOR FOR BELT CONVEYOR 5A | AI | 0 | 300 | RPM
57 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #5 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS12 | DEAC10CS12 | 10EAC10CS012 | SPEED SENSOR FOR BELT CONVEYOR 5B | AI | 0 | 300 | RPM
58 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #6 | WIKA-07NP08-A8D-300-20-003 | DEAC10CS13 | DEAC10CS13 | 10EAC10CS013 | SPEED SENSOR FOR BELT CONVEYOR 6A | AI | 0 | 300 | RPM
59 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #6 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS14 | DEAC10CS14 | 10EAC10CS014 | SPEED SENSOR FOR BELT CONVEYOR 6B | AI | 0 | 300 | RPM
60 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #7 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS15 | DEAC10CS15 | 10EAC10CS015 | SPEED SENSOR FOR BELT CONVEYOR 7A | AI | 0 | 300 | RPM
61 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #7 | WIKA-07NP08-ABD-300-20-003 | DEAC10CS16 | DEAC10CS16 | 10EAC10CS016 | SPEED SENSOR FOR BELT CONVEYOR 7B | AI | 0 | 300 | RPM
62 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04-A | WIKA-07NP08-ABD-300-20-003 | DEAC10CS17 | DEAC10CS17 | 10EAC10CS017 | SPEED SENSOR FOR RC 04A-1 | AI | 0 | 300 | RPM
63 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04-A | WIKA-07NP08-ABD-300-20-003 | DEAC10CS18 | DEAC10CS18 | 10EAC10CS018 | SPEED SENSOR FOR RC 04A-2 | AI | 0 | 300 | RPM
64 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04-A | WIKA-07NP08-ABD-300-20-003 | DEAC10CS19 | DEAC10CS19 | 10EAC10CS019 | SPEED SENSOR FOR RC 04A-3 | AI | 0 | 300 | RPM
65 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04-A | WIKA-07NP08-ABD-300-20-003 | DEAC10CS20 | DEAC10CS20 | 10EAC10CS020 | SPEED SENSOR FOR RC 04A-4 | AI | 0 | 300 | RPM
66 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04B | WIKA-07NP08-ABD-300-20-003 | DEAC10CS21 | DEAC10CS21 | 10EAC10CS021 | SPEED SENSOR FOR RC 04B-1 | AI | 0 | 300 | RPM
67 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04B | WIKA-07NP08-ABD-300-20-003 | DEAC10CS22 | DEAC10CS22 | 10EAC10CS022 | SPEED SENSOR FOR RC 04B-2 | AI | 0 | 300 | RPM
68 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04B | WIKA-07NP08-ABD-300-20-003 | DEAC10CS23 | DEAC10CS23 | 10EAC10CS023 | SPEED SENSOR FOR RC 04B-3 | AI | 0 | 300 | RPM
69 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #04B | WIKA-07NP08-ABD-300-20-003 | DEAC10CS24 | DEAC10CS24 | 10EAC10CS024 | SPEED SENSOR FOR RC 04B-4 | AI | 0 | 300 | RPM
70 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #1 | WIKA-07NP08-ABD-300-20-003 | DEAT10K1 | DEAT10K1 | 10EAT10AK001 | BELT WEIGHER FOR CONVEYOR 1A | Al | 0 | 120 | MTPH
71 | 1 | UJLJ AMG #1 | 4 | COAL HANDLING SYSTEM | 4 | VIBRATION SYSTEM #1 | WIKA-07NP08-ABD-300-20-003 | DEAT10K2 | DEAT10K2 | 10EAT10AK002 | BELT WEIGHER FOR CONVEYOR 1B | Al | 0 | 120 | MTPH
72 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT251 | ANC10CT251 | 11HNC10CT251 | I.D Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
73 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT252 | ANC10CT252 | 11HNC10CT252 | I.D Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
74 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT253 | ANC10CT253 | 11HNC10CT253 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
75 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT254 | ANC10CT254 | 11HNC10CT254 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
76 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT255 | ANC10CT255 | 11HNC10CT255 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
77 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT261 | ANC10CT261 | 11HNC10CT261 | I.D Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
78 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CT262 | ANC10CT262 | 11HNC10CT262 | I.D Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
79 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 2 | ESP #1 | WIKA-07NP08-ABD-101-20-038 | ANA30CT301 | ANA30CT301 | 11HNA30CT301 | Boiler Outlet Gas Temperature | AI | 0 | 200 | °C
80 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 2 | ESP #1 | WIKA-07NP08-ABD-101-20-038 | ANA30CP101 | ANA30CP101 | 11HNA30CP101 | Boiler Outlet Gas Pressure | AI | -10 | 0 | KPa
81 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 2 | ESP #1 | WIKA-07NP08-ABD-101-20-038 | ANA30CQ101 | ANA30CQ101 | 11HNA30CQ101 | Boiler Outlet Gas S02 | AI | 0 | 1000 | mg/Nm3
82 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 2 | ESP #1 | WIKA-07NP08-ABD-101-20-038 | ANA40CT301 | ANA40CT301 | 11HNA40CT301 | E.S.P Outlet Gas Temperature | AI | 0 | 200 | °C
83 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 2 | ESP #1 | WIKA-07NP08-ABD-101-20-038 | ANA40CP101 | ANA40CP101 | 11HNA40CP101 | E.S.P Outlet Gas Pressure | AI | -10 | 0 | KPa
84 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | A40A101AMV | A40A101AMV | 11HNA40AA101AO | I.D. fan inlet control damp position | AO | 0 | 100 | %
85 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANA40A101T | ANA40A101T | 11HNA40AA101GT | I.D. fan inlet control damp position | AI | 0 | 100 | %
86 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ANC10CE010 | ANC10CE010 | 11HNC10CE010 | LD. fan motor current | AI | 0 | 200 | A
87 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ATH0782A_1 | ATH0782A_1 | 11HLB30VX010 | I.D. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
88 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 1 | ID FAN #1 | WIKA-07NP08-ABD-101-20-038 | ATH0782A_2 | ATH0782A_2 | 11HLB30VY010 | I.D. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
89 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT601 | ANA20CT601 | 11HNA20CT601 | Primary superheater inlet temperature(Ieft) | AI | 0 | 600 | °C
90 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT602 | ANA20CT602 | 11HNA20CT602 | Primary superheater inlet temperature(right) | AI | 0 | 600 | °C
91 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT603 | ANA20CT603 | 11HNA20CT603 | Primary superheater outlet temperature(left) | AI | 0 | 600 | °C
92 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT604 | ANA20CT604 | 11HNA20CT604 | Primary superheater outlet temperature(right) | AI | 0 | 600 | °C
93 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP101 | ANA20CP101 | 11HNA20CP101 | Finishing superheater inlet pressure(left) | AI | -3 | 1 | KPa
94 | 1 | UJLJ AMG #1 | 8 | BOILER AFG | 6 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP102 | ANA20CP102 | 11HNA20CP102 | Finishing superheater inlet pressure(right) | AI | 3 | 1 | KPa
95 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP103 | ANA20CP103 | 11HNA20CP103 | Primary superheater inlet pressure(left) | AI | -3 | 1 | KPa
96 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP104 | ANA20CP104 | 11HNA20CP104 | Primary superheater inlet pressure(right) | AI | -3 | 1 | KPa
97 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP105 | ANA20CP105 | 11HNA20CP105 | Primary superheater outlet pressure(left) | AI | -5 | 1 | KPa
98 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP106 | ANA20CP106 | 11HNA20CP106 | Primary superheater outlet pressure(right) | AI | -5 | 1 | KPa
99 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CQ101 | ANA20CQ101 | 11HNA20CQ101 | Primary superheater outlet Oxygen(left) | AI | 0 | 25 | %
100 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CQ102 | ANA20CQ102 | 11HNA20CQ102 | Primary superheater outlet Oxygen(right) | AI | 0 | 25 | %
101 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ALD10CT601 | ALD10CT601 | 11HLD10CT601 | Air heater outlet temperature(left) | AI | 0 | 600 | °C
102 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ALD10CT602 | ALD10CT602 | 11HLD10CT602 | Air heater outlet temperature(right) | AI | 0 | 600 | °C
103 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ALD10CP101 | ALD10CP101 | 11HLD10CP101 | Air heater outlet pressure(left) | AI | -8 | 0 | KPa
104 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | AIR HEATER #1 | WIKA-07NP08-ABD-101-20-012 | ALD10CP102 | ALD10CP102 | 11HLD10CP102 | Air heater outlet pressure(right) | AI | -8 | 0 | KPa
105 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | AAN40CT601 | AAN40CT601 | 11HAN40CT601 | Left sootblow drain temperature | AI | 0 | 450 | °C
106 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | AAN40CT602 | AAN40CT602 | 11HAN40CT602 | Right sootblow drain temperature | AI | 0 | 450 | °C
107 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | S06_E000.MV | S06_E000.MV | 11HCB05AA101AO | Sootblow steam pressure control valve control | AO | 0 | 100 | %
108 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | ACB05A101T | ACB05A101T | 11HCB05AA101GT | Sootblow steam pressure control valve position | AI | 0 | 100 | %
109 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | ACB10CP151 | ACB10CP151 | 11HCB10CP151 | Pressure Reducing sootblow terminal | AI | 0 | 4 | MPa
110 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 3 | SOOTBLOWER #1 | WIKA-07NP08-ABD-201-20-031 | ACB10CP152 | ACB10CP152 | 11HCB10CP152 | Pressure Reducing sootblow terminal | AI | 0 | 4 | MPa
111 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT201 | ANF10CT201 | 11HNF10CT201 | Cyclone upper metal temperature 1 | AI | 0 | 1200 | °C
112 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT202 | ANF10CT202 | 11HNF10CT202 | Cyclone upper metal temperature 2 | AI | 0 | 1200 | °C
113 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT203 | ANF10CT203 | 11HNF10CT203 | Cyclone upper metal temperature 3 | AI | 0 | 1200 | °C
114 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT204 | ANF10CT204 | 11HNF10CT204 | Cyclone upper metal temperature 4 | AI | 0 | 1200 | °C
115 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT211 | ANF10CT211 | 11HNF10CT211 | Cyclone lower metal temperature 1 | AI | 0 | 1200 | °C
116 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT212 | ANF10CT212 | 11HNF10CT212 | Cyclone lower metal temperature 2 | AI | 0 | 1200 | °C
117 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT213 | ANF10CT213 | 11HNF10CT213 | Cyclone lower metal temperature 3 | AI | 0 | 1200 | °C
118 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT214 | ANF10CT214 | 11HNF10CT214 | Cyclone lower metal temperature 4 | AI | 0 | 1200 | °C
119 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT215 | ANF10CT215 | 11HNF10CT215 | Cyclone lower metal temperature 5 | AI | 0 | 1200 | °C
120 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT216 | ANF10CT216 | 11HNF10CT216 | Cyclone lower metal temperature 6 | AI | 0 | 1200 | °C
121 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT217 | ANF10CT217 | 11HNF10CT217 | Cyclone lower metal temperature 7 | AI | 0 | 1200 | °C
122 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT218 | ANF10CT218 | 11HNF10CT218 | Cyclone lower metal temperature 8 | AI | 0 | 1200 | °C
123 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT601 | ANF10CT601 | 11HNF10CT601 | Cyclone inlet temperature | AI | 0 | 1200 | °C
124 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CP101 | ANF10CP101 | 11HNF10CP101 | Cyclone inlet pressure | AI | -5 | 5 | KPa
125 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANA11CT601 | ANA11CT601 | 11HNA11CT601 | Cyclone outlet temperature | AI | 0 | 1200 | °C
126 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | CYCLONE #1 | WIKA-07NP08-ABD-101-20-012 | ANA11CP101 | ANA11CP101 | 11HNA11CP101 | Cyclone outlet pressure | AI | -7 | 1 | KPa
127 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CT602 | ANF10CT602 | 11HNF10CT602 | J valve ash temperature | AI | 0 | 1200 | °C
128 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CP102 | ANF10CP102 | 11HNF10CP102 | J valve inlet pressure | AI | -11 | 40 | KPa
129 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10CP103 | ANF10CP103 | 11HNF10CP103 | J valve outlet pressure | AI | -20 | 60 | KPa
130 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10DP101 | ANF10DP101 | 11HNF10DP101 | J valve density | AI | -10 | 30 | KPa
131 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10DP102 | ANF10DP102 | 11HNF10DP102 | J valve sealing height | AI | -10 | 30 | KPa
132 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | ( J - VALVE) #1 | WIKA-07NP08-ABD-101-20-012 | ANF10DP103 | ANF10DP103 | 11HNF10DP103 | J valve level | AI | -20 | 60 | KPa
133 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1A | WIKA-07NP08-ABD-101-20-031 | AEH10CP101 | AEH10CP101 | 11QEH10CP101 | HP Seal Blower 1 Outlet Pressure | AI | 0 | 100 | KPa
134 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1B | WIKA-07NP08-ABD-101-20-031 | AEH20CP101 | AEH20CP101 | 11QEH20CP101 | HP Seal Blower 2 Outlet Pressure | AI | 0 | 100 | KPa
135 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AEH41CF101 | AEH41CF101 | 11QEH41CF101 | Return Leg HP fluidized air Flow(Left) | AI | 0 | 700 | Nm3/h
136 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AEH42CF101 | AEH42CF101 | 11QEH42CF101 | Return Leg HP fluidized air Flow(right) | AI | 0 | 700 | Nm3/h
137 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AS04_E009.MV | AS04_E009.MV | 11QEH30AA111AO | HP seal air pressure control damp control | AO | 0 | 100 | %
138 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AEH30A111T | AEH30A111T | 11QEH30AA111GT | HP seal air pressure control damp position | AI | 0 | 100 | %
139 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AS04_E023.MV | AS04_E023.MV | 11QEH41AA111AO | Return leg left fluidized air control damp control | AO | 0 | 100 | %
140 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AEH41A111T | AEH41A111T | 11QEH41AA111GT | Return leg left fluidized air control damp position | AI | 0 | 100 | %
141 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AS04_E024.MV | AS04_E024.MV | 11QEH42AA111AO | Return leg right fluidized air control damp control | AO | 0 | 100 | %
142 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1 | WIKA-07NP08-ABD-101-20-031 | AEH42A111T | AEH42A111T | 11QEH42AA111GT | Return leg right fluidized air control damp position | AI | 0 | 100 | %
143 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1A | WIKA-07NP08-ABD-101-20-031 | AEH11CE010 | AEH11CE010 | 11QEH11CE010 | HP Seal Blower 1 Motor Current | AI | 0 | 100 | A
144 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #1B | WIKA-07NP08-ABD-101-20-031 | AEH12CE010 | AEH12CE010 | 11QEH12CE010 | HP Seal Blower 2 Motor Current | AI | 0 | 100 | A
145 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT601 | ABK10CT601 | 11HBK10CT601 | Furnace temperature(left lower 1) | AI | 0 | 1200 | °C
146 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT602 | ABK10CT602 | 11HBK10CT602 | Furnace temperature(left lower 2) | AI | 0 | 1200 | °C
147 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT603 | ABK10CT603 | 11HBK10CT603 | Furnace temperature (left upper 1) | AI | 0 | 1200 | °C
148 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT604 | ABK10CT604 | 11HBK10CT604 | Furnace temperature(left upper 2) | AI | 0 | 1200 | °C
149 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT605 | ABK10CT605 | 11HBK10CT605 | Furnace temperature(right lower 1) | AI | 0 | 1200 | °C
150 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT606 | ABK10CT606 | 11HBK10CT606 | Furnace temperature(right lower 2) | AI | 0 | 1200 | °C
151 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT607 | ABK10CT607 | 11HBK10CT607 | Furnace temperature(right upper 1) | AI | 0 | 1200 | °C
152 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT608 | ABK10CT608 | 11HBK10CT608 | Furnace temperature(right upper 2) | AI | 0 | 1200 | °C
153 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT611 | ABK10CT611 | 11HBK10CT611 | Furnace outlet temperature(left) | AI | 0 | 1200 | °C
154 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10CT612 | ABK10CT612 | 11HBK10CT612 | Furnace outlet temperature(right) | AI | 0 | 1200 | °C
155 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T621A | ABK10T621A | 11HBK10CT621A | Furnace bed temperature 1a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
156 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T621B | ABK10T621B | 11HBK10CT621B | Furnace bed temperature 1b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
157 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T622A | ABK10T622A | 11HBK10CT622A | Furnace bed temperature 2a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
158 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T622B | ABK10T622B | 11HBK10CT622B | Furnace bed temperature 2b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
159 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T623A | ABK10T623A | 11HBK10CT623A | Furnace bed temperature 3a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
160 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T623B | ABK10T623B | 11HBK10CT623B | Furnace bed temperature 3b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
161 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WlKA-07NP08-ABD-101-20-012 | ABK10T624A | ABK10T624A | 11HBK10CT624A | Furnace bed temperature 4a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
162 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T624B | ABK10T624B | 11HBK10CT624B | Furnace bed temperature 4b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
163 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T625A | ABK10T625A | 11HBK10CT625A | Furnace bed temperature 5a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
164 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T625B | ABK10T625B | 11HBK10CT625B | Furnace bed temperature 5b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
165 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T626A | ABK10T626A | 11HBK10CT626A | Furnace bed temperature 6a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
166 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T626B | ABK10T626B | 11HBK10CT626B | Furnace bed temperature 6b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
167 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T627A | ABK10T627A | 11HBK10CT627A | Furnace bed temperature 7a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
168 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T627B | ABK10T627B | 11HBK10CT627B | Furnace bed temperature 7b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
169 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T628A | ABK10T628A | 11HBK10CT628A | Furnace bed temperature 8a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
170 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T628B | ABK10T628B | 11HBK10CT628B | Furnace bed temperature 8b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
171 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T629A | ABK10T629A | 11HBK10CT629A | Furnace bed temperature 9a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
172 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T629B | ABK10T629B | 11HBK10CT629B | Furnace bed temperature 9b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
173 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T630A | ABK10T630A | 11HBK10CT630A | Furnace bed temperature 10a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
174 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T630B | ABK10T630B | 11HBK10CT630B | Furnace bed temperature 10b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
175 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T631A | ABK10T631A | 11HBK10CT631A | Furnace bed temperature 11a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
176 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T631B | ABK10T631B | 11HBK10CT631B | Furnace bed temperature 11b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
177 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T632A | ABK10T632A | 11HBK10CT632A | Furnace bed temperature 12a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
178 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10T632B | ABK10T632B | 11HBK10CT632B | Furnace bed temperature 12b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
179 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP101 | ABK10CP101 | 11HBK10CP101 | Boiler bed levels pressure | AI | 6 | 10 | KPa
180 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP102 | ABK10CP102 | 11HBK10CP102 | Boiler bed levels pressure (right) | AI | 6 | 10 | KPa
181 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP103 | ABK10CP103 | 11HBK10CP103 | Furnace lower part pressure(left) | AI | 2 | 8 | KPa
182 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP104 | ABK10CP104 | 11HBK10CP104 | Furnace lower part pressure(right) | AI | 2 | 8 | KPa
183 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP105 | ABK10CP105 | 11HBK10CP105 | Furnace middle part pressure(left) | AI | 2 | 3 | KPa
184 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP106 | ABK10CP106 | 11HBK10CP106 | Furnace middle part pressure(right | AI | 2 | 3 | KPa
185 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP107 | ABK10CP107 | 11HBK10CP107 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
186 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP108 | ABK10CP108 | 11HBK10CP108 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
187 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP109 | ABK10CP109 | 11HBK10CP109 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
188 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP110 | ABK10CP110 | 11HBK10CP110 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
189 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP111 | ABK10CP111 | 11HBK10CP111 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
190 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10CP112 | ABK10CP112 | 11HBK10CP112 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
191 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP101 | ABK10DP101 | 11HBK10DP101 | Boiler bed material density (left) | AI | 0 | 10 | KPa
192 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP102 | ABK10DP102 | 11HBK10DP102 | Boiler bed material densiy (right) | AI | 0 | 10 | KPa
193 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP103 | ABK10DP103 | 11HBK10DP103 | Boiler bed levels D.P. | AI | 0 | 10 | KPa
194 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP104 | ABK10DP104 | 11HBK10DP104 | Boiler bed levels D.P. | AI | 0 | 10 | KPa
195 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP105 | ABK10DP105 | 11HBK10DP105 | Furnace DP.(left) | AI | -5 | 5 | KPa
196 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 | WIKA-07NP08-ABD-101-20-012 | ABK10DP106 | ABK10DP106 | 11HBK10DP106 | Furnace D.P.(right) | AI | -5 | 5 | KPa
197 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | ALA40CP101 | ALA40CP101 | 11HLA40CP101 | Winbox plenum pressure(left) | AI | 0 | 20 | KPa
198 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | ALA40CP102 | ALA40CP102 | 11HLA40CP102 | Winbox plenum pressure(right) | AI | 0 | 20 | KPa
199 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | ABK10CT613 | ABK10CT613 | 11HBK10CT613 | Windbox Plenum 1A | AI | 0 | 1200 | °C
200 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE #1 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | ABK10CT614 | ABK10CT614 | 11HBK10CT614 | Windbox Plenum 1B | AI | 0 | 1200 | °C
201 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF05CP101 | AJF05CP101 | 11HJF05CP101 | Gun feed oil pressure | AI | 0 | 4 | MPa
202 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF06CP101 | AJF06CP101 | 11HJF06CP101 | Gun return oil pressure | AI | 0 | 4 | MPa
203 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF06CF101 | AJF06CF101 | 11HJF06CF101 | Gun return oil flow | AI | 0 | 8 | t/h
204 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF30CP101 | AJF30CP101 | 11HJF30CP101 | In-bed gun 1 inlet pressure | AI | 0 | 4 | MPa
205 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF30CF101 | AJF30CF101 | 11HJF30CF101 | In-bed gun 1 inlet flow | AI | 0 | 2 | t/h
206 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF40CP101 | AJF40CP101 | 11HJF40CP101 | In-bed gun 2 inlet pressure | AI | 0 | 4 | MPa
207 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF40CF101 | AJF40CF101 | 11HJF40CF101 | In-bed gun 2 inlet flow | AI | 0 | 2 | t/h
208 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF50CP101 | AJF50CP101 | 11HJF50CP101 | In-bed gun 3 inlet pressure | AI | 0 | 4 | MPa
209 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF50CF101 | AJF50CF101 | 11HJF50CF101 | In-bed gun 3 inlet flow | AI | 0 | 2 | t/h
210 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF60CP101 | AJF60CP101 | 11HJF60CP101 | In-bed gun 4 inlet pressure | AI | 0 | 4 | MPa
211 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF60CF101 | AJF60CF101 | 11HJF60CF101 | In-bed gun 4 inlet flow | AI | 0 | 2 | t/h
212 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJS03CP101 | AJS03CP101 | 11HJS03CP101 | Pressurized air pressure | AI | 0 | 1.6 | MPa
213 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AS04_E012.MV | AS04_E012.MV | 11HJF07AA101AO | Burn oil pressure control valve control | AO | 0 | 100 | %
214 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF07A101T | AJF07A101T | 11HJF07AA101GT | Burn oil pressure control valve position | AI | 0 | 100 | %
215 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AS04_E025.MV | AS04_E025.MV | 11HJF35AA101AO | NO.1 IN-Duct bum oil flow control valve control | AO | 0 | 100 | %
216 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF35A101T | AJF35A101T | 11HJF35AA101GT | NO.1 IN-Duct burn oil flow control valve position | AI | 0 | 100 | %
217 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AS04_E026.MV | AS04_E026.MV | 11HJF45AA101AO | NO.2 IN-Duct burn oil flow control valve control | AO | 0 | 100 | %
218 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF45A101T | AJF45A101T | 11HJF45AA101GT | NO.2 IN-Duct burn oil flow control valve position | AI | 0 | 100 | %
219 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AS04_E027.MV | AS04_E027.MV | 11HJF55AA101AO | In-bed oil gun 1 oil flow control valve control | AO | 0 | 100 | %
220 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF55A101T | AJF55A101T | 11HJF55AA101GT | In-bed oil gun 1 oil flow control valve position | AI | 0 | 100 | %
221 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AS04_E028.MV | AS04_E028.MV | 11HJF65AA101AO | In-bed oil gun 2 oil flow control valve control | AO | 0 | 100 | %
222 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJF65A101T | AJF65A101T | 11HJF65AA101GT | In-bed oil gun 2 oil flow control valve position | AI | 0 | 100 | %
223 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJY11F001 | AJY11F001 | 11HJY11FQ001 | NO.1 IN-Duct burn flame intensity | AI | 0 | 100 | %
224 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJY21F001 | AJY21F001 | 11HJY21FQ001 | NO.2 IN-Duct burn flame intensity | AI | 0 | 100 | %
225 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJY31F001 | AJY31F001 | 11HJY31FQ001 | NO.1 IN-Bed burn flame intensity | AI | 0 | 100 | %
226 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #1 | WIKA-07NP08-ABD-101-20-027 | AJY41F001 | AJY41F001 | 11HJY41FQ001 | NO.2 IN-Bed burn flame intensity | AI | 0 | 100 | %
227 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1A | WIKA-07NP08-ABD-201-20-012 | AS04_E013.MV | AS04_E013.MV | 11HDY11FA101 | No.1 Ash cooler frequency control | AO | 0 | 100 | %
228 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1A | WIKA-07NP08-ABD-201-20-012 | ADY11FE001 | ADY11FE001 | 11HDY11FE001 | No.1 Ash cooler frequency | Al | 0 | 100 | %
229 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1A | WIKA-07NP08-ABD-201-20-012 | ADY11FE002 | ADY11FE002 | 11HDY11FE002 | No.1 Ash cooler current | Al | 0 | 100 | A
230 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1B | WIKA-07NP08-ABD-201-20-012 | AS04_E014.MV | AS04_E014.MV | 11HDY21FA101 | No.2 Ash cooler frequency control | AO | 0 | 100 | %
231 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1B | WIKA-07NP08-ABD-201-20-012 | ADY21FE001 | ADY21FE001 | 11HDY21FE001 | No.2 Ash cooler frequency | Al | 0 | 100 | %
232 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1B | WIKA-07NP08-ABD-201-20-012 | ADY21FE002 | ADY21FE002 | 11HDY21FE002 | No.2 Ash cooler current | Al | 0 | 100 | A
233 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1A | WIKA-07NP08-ABD-201-20-037 | LCA22G301 | LCA22G301 | 11LCA22CT301 | Temperature outlet cooling water No.1 Ash cooler | Al | 0 | 200 | °C
234 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 5 | ASH COOLER #1B | WIKA-07NP08-ABD-201-20-037 | LCA42G301 | LCA42G301 | 11LCA42CT301 | Temperature outlet cooling water No.2 Ash cooler | Al | 0 | 200 | °C
235 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT251 | ALB20CT251 | 11HLB20CT251 | S.A Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
236 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT252 | ALB20CT252 | 11HLB20CT252 | S.A Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
237 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT253 | ALB20CT253 | 11HLB20CT253 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
238 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT254 | ALB20CT254 | 11HLB20CT254 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
239 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT255 | ALB20CT255 | 11HLB20CT255 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
240 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT261 | ALB20CT261 | 11HLB20CT261 | S.A Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
241 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CT262 | ALB20CT262 | 11HLB20CT262 | S.A Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
242 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALA82CT301 | ALA82CT301 | 11HLA82CT301 | S.A. Fan Outlet Temperature | AI | 0 | 200 | °C
243 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALA82CP101 | ALA82CP101 | 11HLA82CP101 | S.A. Fan Outlet Pressure | AI | 0 | 16 | KPa
244 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | AL81A101MV | AL81A101MV | 11HLA81AA101AO | Second air fan inlet control damp control | AO | 0 | 100 | %
245 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALA81A101T | ALA81A101T | 11HLA81AA101GT | Second air fan inlet control damp position | AI | 0 | 100 | %
246 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ATH0782A_5 | ATH0782A_5 | 11HLB10VX010 | S.A. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
247 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ATH0782A_6 | ATH0782A_6 | 11HLB10VY010 | S.A. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
248 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #1 | WIKA-07NP08-ABD-101-20-028 | ALB20CE010 | ALB20CE010 | 11HLB20CE010 | Second air fan motor current | AI | 0 | 200 | A
249 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA83CT301 | ALA83CT301 | 11HLA83CT301 | Second air heater outlet temperature | AI | 0 | 450 | °C
250 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA83CP101 | ALA83CP101 | 11HLA83CP101 | Second air heater outlet pressure | AI | 0 | 16 | KPa
251 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA84CF1_1 | ALA84CF1_1 | 11HLA84CF101 | Lower CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
252 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA85CF1_1 | ALA85CF1_1 | 11HLA85CF101 | Upper CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
253 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | AS04_E021.MV | AS04_E021.MV | 11HLA84AA101AO | Lower combstion chamber air flow control damp control | AO | 0 | 100 | %
254 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA84A101T | ALA84A101T | 11HLA84AA101GT | Lower combstion chamber air flow control damp position | AI | 0 | 100 | %
255 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | AS04_E022.MV | AS04_E022.MV | 11HLA85AA101AO | Upper combstion chamber airflow control damp control | AO | 0 | 100 | %
256 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 6 | SECONDARY AIR HEATER #1 | WIKA-07NP08-ABD-101-20-028 | ALA85A101T | ALA85A101T | 11HLA85AA101GT | Upper combstion chamber airflow control damp position | AI | 0 | 100 | %
257 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT251 | ALB10CT251 | 11HLB10CT251 | P.A Fan Motor Front Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 85 | 95
258 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT252 | ALB10CT252 | 11HLB10CT252 | P.A Fan Motor Rear Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 85 | 95
259 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT253 | ALB10CT253 | 11HLB10CT253 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
260 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT254 | ALB10CT254 | 11HLB10CT254 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
261 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT255 | ALB10CT255 | 11HLB10CT255 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
262 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT261 | ALB10CT261 | 11HLB10CT261 | P.A Fan Front Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
263 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CT262 | ALB10CT262 | 11HLB10CT262 | P.A Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
264 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALA12CT301 | ALA12CT301 | 11HLA12CT301 | P.A. Fan Outlet Air Temperature | AI | 0 | 150 | °C
265 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALA12CP101 | ALA12CP101 | 11HLA12CP101 | P.A. Fan Outlet Air Pressure | AI | 0 | 25 | KPa
266 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALA15CF1_1 | ALA15CF1_1 | 11HLA15CF101 | Sponge Coal Feeder Air Flow | AI | 0 | 5500 | Nm3/h
267 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB10CE010 | ALB10CE010 | 11HLB10CE010 | Primary air fan motor current | AI | 0 | 200 | A
268 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ATH0782A_3 | ATH0782A_3 | 11HLB20VX010 | P.A. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
269 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. FAN #1 | WIKA-07NP08-ABD-101-20-039 | ATH0782A_4 | ATH0782A_4 | 11HLB20VY010 | P.A. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
270 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT251 | ALB30CT251 | 11HLB30CT251 | P.A Booster Booster Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
271 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT252 | ALB30CT252 | 11HLB30CT252 | P.A Booster Booster Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
272 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT253 | ALB30CT253 | 11HLB30CT253 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
273 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT254 | ALB30CT254 | 11HLB30CT254 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
274 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT255 | ALB30CT255 | 11HLB30CT255 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
275 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT261 | ALB30CT261 | 11HLB30CT261 | P.A Booster Booster Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
276 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CT262 | ALB30CT262 | 11HLB30CT262 | P.A Booster Booster Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
277 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | AL13A101MV | AL13A101MV | 11HLA13AA101AO | PA booster fan inlet control damp control | AO | 0 | 100 | %
278 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALA13A101T | ALA13A101T | 11HLA13AA101GT | PA booster fan inlet control damp position | AI | 0 | 100 | %
279 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #1 | WIKA-07NP08-ABD-101-20-039 | ALB30CE010 | ALB30CE010 | 11HLB30CE010 | P.A. booster fan motor current | AI | 0 | 200 | A
280 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA30CT301 | ALA30CT301 | 11HLA30CT301 | Primary air heater outlet temperature | AI | 0 | 450 | °C
281 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA30CP101 | ALA30CP101 | 11HLA30CP101 | Primary air heater outlet pressure | AI | 0 | 25 | KPa
282 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA31CF1_1 | ALA31CF1_1 | 11HLA31CF101 | Duct Ignition Burner 1 Air Flow | AI | 0 | 40000 | Nm3/h
283 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA32CF1_1 | ALA32CF1_1 | 11HLA32CF101 | Duct Ignition Burner 2 Air Flow | AI | 0 | 40000 | Nm3/h
284 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA41CF1_1 | ALA41CF1_1 | 11HLA41CF101 | Oil Gun 2 Above Grid Plate Air Flow | AI | 0 | 11000 | Nm3/h
285 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA42CF1_1 | ALA42CF1_1 | 11HLA42CF101 | Oil Gun 1 Above Grid Plate Air Flow | AI | 0 | 11000 | Nm3/h
286 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALAA101AMV | ALAA101AMV | 11HLA11AA101AO | Primary air fan inlet control damp control | AO | 0 | 100 | %
287 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALAAA101T | ALAAA101T | 11HLA11AA101GT | Primary air fan inlet control damp position | AI | 0 | 100 | %
288 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | AS04_E015.MV | AS04_E015.MV | 11HLA31AA101AO | No.1 duct burn inlet control damp controj | AO | 0 | 100 | %
289 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA31A101T | ALA31A101T | 11HLA31AA101GT | No.1 duct burn inlet control damp position | AI | 0 | 100 | %
290 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | AS04_E016.MV | AS04_E016.MV | 11HLA32AA101AO | No.2 duct burn inlet control damp control | AO | 0 | 100 | %
291 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA32A101T | ALA32A101T | 11HLA32AA101GT | No.2 duct burn inlet control damp position | AI | 0 | 100 | %
292 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | AS04_E017.MV | AS04_E017.MV | 11HLA41AA101AO | No.1 bed burn inlet control damp control | AO | 0 | 100 | %
293 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA41A101T | ALA41A101T | 11HLA41AA101GT | No.1 bed burn inlet control damp position | AI | 0 | 100 | %
294 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | AS04_E019.MV | AS04_E019.MV | 11HLA42AA101AO | No.2 bed burn inlet control damp control | AO | 0 | 100 | %
295 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 7 | P.A. HEATER #1 | WIKA-07NP08-ABD-101-20-039 | ALA42A101T | ALA42A101T | 11HLA42AA101GT | No.2 bed burn inlet control damp position | AI | 0 | 100 | %
296 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 8 | SPONGE COAL SILO / COAL BUNKER #1 | WIKA-07NP08-ABD-101-20-033 | AFB10CL101 | AFB10CL101 | 11HFB10CL101 | Sponge Coal Silo Level | AI | 0 | 14.5 | m
297 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1 | WIKA-07NP08-ABD-101-20-033 | ALA50CT301 | ALA50CT301 | 11HLA50CT301 | Feeder Air Temperature | AI | 0 | 100 | °C
298 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1 | WIKA-07NP08-ABD 101-20-033 | ALA50CP101 | ALA50CP101 | 11HLA50CP101 | Feeder Air Pressure | AI | 0 | 40 | KPa
299 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1 | WIKA-07NP08-ABD-101-20-033 | ALA50CF1_1 | ALA50CF1_1 | 11HLA50CF101 | Feeder Air Flow | AI | 0 | 9000 | NmJ/h
300 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1A | WIKA-07NP08-ABD-101-20-033 | AFY10FT001 | AFY10FT001 | 11HFY10FT001 | NO.1 gravimetric belt feeder temperature | AI | 0 | 200 | °C
301 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1A | WIKA-07NP08-ABD-101-20-033 | AFY10FS101 | AFY10FS101 | 11HFY10FS101 | NO.1 gravimetric belt feeder speed | AI | 0 | 100 | RPM
302 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1A | WIKA-07NP08-ABD-101-20-033 | AFY10FA101 | AFY10FA101 | 11HFY10FA101 | NO.1 gravimetric belt feeder speed control | AO | 0 | 100 | %
303 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1A | WIKA-07NP08-ABD-101-20-033 | AFY10FF001 | AFY10FF001 | 11HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
304 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1B | WIKA-07NP08-ABD-101-20-033 | AFY20FT001 | AFY20FT001 | 11HFY20FT001 | NO.2 gravimetric belt feeder temperature | AI | 0 | 200 | °C
305 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1B | WIKA-07NP08-ABD-101-20-033 | AFY20FS101 | AFY20FS101 | 11HFY20FS101 | NO.2 gravimetric belt feeder speed | AI | 0 | 100 | RPM
306 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1B | WIKA-07NP08-ABD-101-20-033 | AFY20FA101 | AFY20FA101 | 11HFY20FA101 | NO.2 gravimetric belt feeder speed control | AO | 0 | 100 | %
307 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #1B | WIKA-07NP08-ABD-101-20-033 | AFY20FF001 | AFY20FF001 | 11HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
308 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CT301 | ANE31CT301 | 11HNE31CT301 | Stack flue gas temperature | AI | 0 | 300 | °C
309 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CP101 | ANE31CP101 | 11HNE31CP101 | Stack flue gas pressure | AI | -10 | 10 | MPa
310 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CF101 | ANE31CF101 | 11HNE31CF101 | Stack flue gas velocity | AI | 0 | 40 | m/s
311 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CQ101 | ANE31CQ101 | 11HNE31CQ101 | Stack flue gas S02 | AI | 0 | 1000 | mg/Nm3
312 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CQ102 | ANE31CQ102 | 11HNE31CQ102 | Stack flue gas CO | AI | 0 | 1400 | mg/Nm
313 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CQ103 | ANE31CQ103 | 11HNE31CQ103 | Stack flue gas NOx | AI | 0 | 1200 | mg/Nm
314 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CQ104 | ANE31CQ104 | 11HNE31CQ104 | Stack flue gas 02 | AI | 0 | 25 | %
315 | 1 | UJLJ AMG #1 | 5 | BOILER AFG | 10 | STACK #1 | WIKA-07NP08-ABD-101-20-018 | ANE31CQ105 | ANE31CQ105 | 11HNE31CQ105 | Stack flue gas dust concentration | AI | 0 | 200 | mg/Nm
316 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-027 | AAG10CL151 | AAG10CL151 | 11MAG10CL151 | Condenser hot well level | AI | 0 | 1100 | mm |  | 0 | 300 | 1000 | 1000
317 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-027 | ACA20A102T | ACA20A102T | 11LCA20AA102GT | Hot well level control valve position | AI | 0 | 100 | %
318 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-027 | S14_E004.MV | S14_E004.MV | 11LCA20AA102AO | Hot well level control valve control | AO | 0 | 100 | %
319 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-027 | A_A20CF101 | A_A20CF101 | 11LCA20CF101 | Condenser makeup water flow | AI | 0 | 4 | t/h
320 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-027 | ACA20CL151 | ACA20CL151 | 11LCA20CL151 | Condensate storge tank level | AI | 0 | 1800 | mm |  | 250 | 250 | 1700 | 1700
321 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | ABF10CT601 | ABF10CT601 | 11LBF10CT601 | HP bypass valve outlet temperature | AI | 0 | 600 | °C
322 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | ABF10CT602 | ABF10CT602 | 11LBF10CT602 | HP bypass valve outlet temperature | AI | 0 | 600 | °C
323 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | ABF10CP101 | ABF10CP101 | 11LBF10CP101 | HP bypass valve outlet pressure | AI | -0.1 | 1 | MPa
324 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | ABF10A001T | ABF10A001T | 11LBF10AA001GT | Turbine bypass pressure control valve position | AI | 0 | 100 | %
325 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | ABF10A003T | ABF10A003T | 11LBF10AA003GT | Turbine bypass 1 stage spray water control valve position | AI | 0 | 100 | %
326 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | S16_E000.MV | S16_E000.MV | 11LBF10AA001AO | Turbine bypass pressure control valve control | AO | 0 | 100 | %
327 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 | WIKA-07NP08-ABD-201-20-007 | S16_E001.MV | S16_E001.MV | 11LBF10AA003AO | Turbine bypass 1 stage spray water control valve control | AO | 0 | 100 | %
328 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CT301 | AAB10CT301 | 11PAB10CT301 | Condenser left inlet cooling water temperature | AI | 0 | 100 | °C
329 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CT302 | AAB10CT302 | 11PAB10CT302 | Condenser left outlet cooling water temperature | AI | 0 | 100 | °C
330 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CT311 | AAB10CT311 | 11PAB10CT311 | Condenser right inlet cooling water temperature | AI | 0 | 100 | °C
331 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CT312 | AAB10CT312 | 11PAB10CT312 | Condenser right outlet cooling water temperature | AI | 0 | 100 | °C
332 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CP101 | AAB10CP101 | 11PAB10CP101 | Condenser left inlet cooling water pressure | AI | 0.1 | 0.5 | MPa
333 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CP102 | AAB10CP102 | 11PAB10CP102 | Condenser left outlet cooling water pressure | AI | 0.1 | 0.5 | MPa
334 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AAB10CP111 | AAB10CP111 | 11PAB10CP111 | Condenser right inlet cooling water pressure | AI | 0.1 | 0.5 | MPa
335 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (OCCW) | WIKA-07NP08-ABD-201-20-029 | AOB10CP112 | AOB10CP112 | 11PAB10CP112 | Condenser right outlet cooling water pressure | AI | 0.1 | 0.5 | MPa
336 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (VACUUM EJECTOR) | WIKA-07NP08-ABD-201-20-020 | AAG10CP103 | AAG10CP103 | 11MAG10CP103 | Condenser pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
337 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CONDENSER #1 (VACUUM EJECTOR) | WIKA-07NP08-ABD-201-20-020 | AAJ10CP101 | AAJ10CP101 | 11MAJ10CP101 | Vaccuum pump group inlet pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
338 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB20P111 | CPGB20P111 | 10PGB20CP111 | Closed cooling exchanger outlet water pressure | Al | 0 | 1 | MPa |  | 0.1 | 0.3 | 0.7 | 0.9
339 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB20Q101 | CPGB20Q101 | 10PGB20CQ101 | Closed cooling exchanger outlet water PH | Al | 0 | 14
340 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB20L101 | CPGB20L101 | 10PGB20CL101 | Expansion tank level | Al | 0 | 800 | mm |  | 0 | 300 | 700 | 800
341 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB21C301 | CPGB21C301 | 10PGB20CT301 | NO.1 Closed cooling exchanger inlet water temperature | Al | 0 | 150 | °C
342 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB21C302 | CPGB21C302 | 10PGB20CT311 | NO.1 Closed cooling exchanger outlet water temperature | Al | 0 | 150 | °C
343 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB20P101 | CPGB20P101 | 10PGB20CP101 | NO.1 Closed cooling water pump outlet header pressure | Al | 0 | 1 | MPa |  | 0.2 | 0.3 | 0.6 | 0.65
344 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB21C010 | CPGB21C010 | 10PGB21CE010 | NO.1 closed cooling water pump motor current | Al | 0 | 200 | A
345 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPGB22C010 | CPGB22C010 | 10PGB22CE010 | NO.2 closed cooling water pump motor current | Al | 0 | 200 | A
346 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPAB20P101 | CPAB20P101 | 10PAB20CP101 | Closed cooling exchanger inlet sea water pressure | Al | 0 | 0.4 | MPa
347 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPB21CT301 | CPB21CT301 | 10PAB20CT311 | NO.1 Closed cooling exchanger inlet sea water temperature | Al | 0 | 150 | °C
348 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPAB30P101 | CPAB30P101 | 10PAB20CP111 | Closed cooling exchanger inlet sea water pressure | Al | 0 | 0.4 | MPa
349 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 1 | CLOSED COOLING SYSTEM #1 | WIKA-07NP08-ABD-201-20-032-01 | CPB31CT301 | CPB31CT301 | 10PAB31CT301 | N0.1 Closed cooling exchanger outlet sea water temperature | Al | 0 | 150 | °C
350 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CT301 | ACA10CT301 | 11LCA10CT301 | Condensate water temperature | AI | 0 | 150 | °C
351 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CT302 | ACA10CT302 | 11LCA10CT302 | Condensate pump outlet header temperature | AI | 0 | 200 | °C
352 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CP101 | ACA10CP101 | 11LCA10CP101 | Condensate pump outlet header pressure | AI | 0 | 2 | MPa
353 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CP102 | ACA10CP102 | 11LCA10CP102 | Condensate pump outlet header pressure | AI | 0 | 2 | MPa
354 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1A | WIKA-07NP08-ABD-201-20-018 | AC10CE001 | AC10CE001 | 11LCB10CE001 | NO.1 condensate pump motor current | AI | 0 | 200 | A
355 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CP111 | ACA10CP111 | 11LCA10CP111 | HP heater by-pass valve control water pressure | AI | 0 | 2 | MPa
356 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1B | WIKA-07NP08-ABD-201-20-018 | AOC20CE001 | AOC20CE001 | 11LCB20CE001 | NO.2 condensate pump motor current | AI | 0 | 200 | A
357 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CP111 | ACA10CP111 | 11LCA10CP111 | HP heater by-pass valve control water pressure | AI | 0 | 2 | MPa
358 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #1 | WIKA-07NP08-ABD-201-20-018 | ACA10A101T | ACA10A101T | 11LCA10AA101GT | Condensate recycling control valve position | AI | 0 | 100 | %
359 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #1 | WIKA-07NP08-ABD-201-20-018 | S14_E003.MV | S14_E003.MV | 11LCA10AA101AO | Condensate recycling control valve control | AO | 0 | 100 | %
360 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #1 | WIKA-07NP08-ABD-201-20-018 | ACA10CT303 | ACA10CT303 | 11LCA10CT303 | Gland cooler outlet condensate temperature | AI | 0 | 200 | °C
361 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #1 | WIKA-07NP08-ABD-201-20-018 | A_A10CF101 | A_A10CF101 | 11LCA10CF101 | Condensate Flow | AI | 0 | 130 | t/h
362 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 4 | LP HEATER #1C | WIKA-07NP08-ABD-201-20-018 | ACA10CT304 | ACA10CT304 | 11LCA10CT304 | NO.3 LP heater outlet condensate temperature | AI | 0 | 150 | °C
363 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 4 | LP HEATER #1C | WIKA-07NP08-ABD-201-20-018 | ACA10CP103 | ACA10CP103 | 11LCA10CP103 | LP heater inlet pressure | AI | 0 | 2 | MPa
364 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 4 | LP HEATER #1C | WIKA-07NP08-ABD-201-20-014 | ABS30CP101 | ABS30CP101 | 11LBS30CP101 | NO.3 LP heater inlet steam pressure | AI | -0.1 | 0.15 | MPa
365 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 4 | LP HEATER #1C | WIKA-07NP08-ABD-201-20-019 | ACC30CL151 | ACC30CL151 | 11LCC30CL151 | NO.3 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
366 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 5 | LP HEATER #1B | WIKA-07NP08-ABD-201-20-018 | ACA10CT305 | ACA10CT305 | 11LCA10CT305 | NO.2 LP heater outlet condensate temperature | AI | 0 | 150 | °C
367 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 5 | LP HEATER #1B | WIKA-07NP08-ABD-201-20-013 | ABS20CP101 | ABS20CP101 | 11LBS20CP101 | NO.2 LP heater inlet steam pressure | AI | 0 | 0.25 | MPa
368 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 5 | LP HEATER #1B | WIKA-07NP08-ABD-201-20-019 | ACC20CL151 | ACC20CL151 | 11LCC20CL151 | NO.2 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
369 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 6 | LP HEATER #1A | WIKA-07NP08-ABD-201-20-018 | ACA10CT306 | ACA10CT306 | 11LCA10CT306 | NO.1 LP heater outlet condensate temperature | AI | 0 | 200 | °C
370 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 6 | LP HEATER #1A | WIKA-07NP08-ABD-201-20-012 | ABS10CP101 | ABS10CP101 | 11LBS10CP101 | NO.1 LP heater inlet steam pressure | AI | 0 | 0.6 | MPa
371 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 6 | LP HEATER #1A | WIKA-07NP08-ABD-201-20-019 | ACC10CL151 | ACC10CL151 | 11LCC10CL151 | NO.1 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
372 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-018 | AA10CT651 | AA10CT651 | 11LAA10CT651 | Dearator tank temperature | AI | 0 | 500 | °C
373 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-018 | AA10CL101 | AA10CL101 | 11LAA10CL101 | Dearator tank level | AI | 0 | 1800 | mm |  |  | 1240 | 1655 | 1740
374 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-018 | AA10CL102 | AA10CL102 | 11LAA10CL102 | Dearator tank level | AI | 0 | 1800 | mm |  |  | 1200 | 1650 | 1740
375 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-018 | ACA10A102T | ACA10A102T | 11LCA10AA102GT | Deaerator tank level control valve position | AI | 0 | 100 | %
376 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-018 | S14_E002.MV | S14_E002.MV | 11LCA10AA102AO | Deaerator tank level control valve control | AO | 0 | 100 | %
377 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | AA10CP101 | AA10CP101 | 11LAA10CP101 | Deaerator pressure | AI | 0 | 1 | MPa
378 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | AA10CP102 | AA10CP102 | 11LAA10CP102 | Deaerator pressure | AI | 0 | 1 | MPa
379 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | ABS40CT601 | ABS40CT601 | 11LBS40CT601 | Deaerator pressure control valve inlet temperature | AI | 0 | 600 | °C
380 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | ABS40CP101 | ABS40CP101 | 11LBS40CP101 | Deaerator pressure control valve inlet pressure | AI | 0 | 1 | MPa
381 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | ABS40A101T | ABS40A101T | 11LBS40AA101GT | Deaerator pressure control valve position | AI | 0 | 100 | %
382 | 1 | UJLJ AMG #1 | 6 | CDS SYSTEM | 7 | DEAERATOR #1 | WIKA-07NP08-ABD-201-20-011 | S14_E005.MV | S14_E005.MV | 11LBS40AA101AO | Deaerator pressure control valve control | AO | 0 | 100 | %
383 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT251 | AC10CT251 | 11LAC10CT251 | NO.1 Feedwater pump motor front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
384 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT252 | AC10CT252 | 11LAC10CT252 | NO.1 Feedwater pump motor rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
385 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT253 | AC10CT253 | 11LAC10CT253 | NO.1 Feedwater pump hydraulic coupler front bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
386 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT254 | AC10CT254 | 11LAC10CT254 | NO.1 Feedwater pump hydraulic coupler rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
387 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT255 | AC10CT255 | 11LAC10CT255 | NO.1 Feedwater pump front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
388 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT256 | AC10CT256 | 11LAC10CT256 | NO.1 Feedwater pump rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
389 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT257 | AC10CT257 | 11LAC10CT257 | NO.1 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
390 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT258 | AC10CT258 | 11LAC10CT258 | NO.1 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
391 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT261 | AC10CT261 | 11LAC10CT261 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
392 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT262 | AC10CT262 | 11LAC10CT262 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
393 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT263 | AC10CT263 | 11LAC10CT263 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
394 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT264 | AC10CT264 | 11LAC10CT264 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
395 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT265 | AC10CT265 | 11LAC10CT265 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
396 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT266 | AC10CT266 | 11LAC10CT266 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
397 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT351 | AC10CT351 | 11LAC10CT351 | NO.1 Feedwater pump hydraulic coupler outlet oil temperature | AI | 0 | 150 | °C |  |  |  | 88
398 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CT352 | AC10CT352 | 11LAC10CT352 | NO.1 Feedwater pump hydraulic coupler inlet oil temperature | AI | 0 | 150 | °C |  |  |  | 65
399 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CP151 | AC10CP151 | 11LAC10CP151 | NO.1 Feedwater pump hydraulic coupler outlet oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.2
400 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CP152 | AC10CP152 | 11LAC10CP152 | NO.1 Feedwater pump lube oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.8
401 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10CS101 | AC10CS101 | 11LAC10CS101 | NO.1 Feedwater pump speed | AI | 0 | 3000 | rpm
402 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10A051T | AC10A051T | 11LAC10AA051GT | No.1 feedwater pump hydraulic coupler actuator position | AI | 0 | 100 | %
403 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AOC10CE001 | AOC10CE001 | 11LAC10CE001 | NO.1 feedwater pump motor current | AI | 0 | 400 | A
404 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-008 | AC10A051MV | AC10A051MV | 11LAC10AA051AO | No.1 feedwater pump hydraulic coupler actuator control | AO | 0 | 100 | %
405 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1A | WIKA-07NP08-ABD-201-20-006 | ABB10CP111 | ABB10CP111 | 11LAB10CP111 | NO.1 HP Feedwater pump outlet pressure | AI | 0 | 20 | MPa
406 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT251 | AC20CT251 | 11LAC20CT251 | NO.2 Feedwater pump motor front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
407 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT252 | AC20CT252 | 11LAC20CT252 | NO.2 Feedwater pump motor rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
408 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT253 | AC20CT253 | 11LAC20CT253 | NO.2 Feedwater pump hydraulic coupler front bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
409 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT254 | AC20CT254 | 11LAC20CT254 | NO.2 Feedwater pump hydraulic coupler rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
410 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT255 | AC20CT255 | 11LAC20CT255 | NO.2 Feedwater pump front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
411 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT256 | AC20CT256 | 11LAC20CT256 | NO.2 Feedwater pump rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
412 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT257 | AC20CT257 | 11LAC20CT257 | NO.2 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
413 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT258 | AC20CT258 | 11LAC20CT258 | NO.2 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
414 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT261 | AC20CT261 | 11LAC20CT261 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
415 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT262 | AC20CT262 | 11LAC20CT262 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
416 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT263 | AC20CT263 | 11LAC20CT263 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
417 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT264 | AC20CT264 | 11LAC20CT264 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
418 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT265 | AC20CT265 | 11LAC20CT265 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
419 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT266 | AC20CT266 | 11LAC20CT266 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
420 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT351 | AC20CT351 | 11LAC20CT351 | NO.2 Feedwater pump hydraulic coupler outlet oil temperature | AI | 0 | 150 | °C |  |  |  | 88
421 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CT352 | AC20CT352 | 11LAC20CT352 | NO.2 Feedwater pump hydraulic coupler inlet oil temperature | AI | 0 | 150 | °C |  |  |  | 65
422 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CP151 | AC20CP151 | 11LAC20CP151 | NO.2 Feedwater pump hydraulic coupler outlet oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.2
423 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CP152 | AC20CP152 | 11LAC20CP152 | NO.2 Feedwater pump lube oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.8
424 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CS101 | AC20CS101 | 11LAC20CS101 | NO.2 Feedwater pump speed | AI | 0 | 3000 | rpm
425 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20A051T | AC20A051T | 11LAC20AA051GT | No.2 feedwater pump hydraulic coupler actuator position | AI | 0 | 100 | %
426 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20CE001 | AC20CE001 | 11LAC20CE001 | NO.2 feedwater pump motor current | AI | 0 | 400 | A
427 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-008 | AC20A051MV | AC20A051MV | 11LAC20AA051AO | No.2 feedwater pump hydraulic coupler actuator control | AO | 0 | 100 | %
428 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #1B | WIKA-07NP08-ABD-201-20-006 | AAB10CP112 | AAB10CP112 | 11LAB10CP112 | NO.2 HP Feedwater pump outlet pressure | AI | 0 | 20 | MPa
429 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 3 | HPH FEEDWATER #1B | WIKA-07NP08-ABD-201-20-006 | AAB10CT611 | AAB10CT611 | 11LAB10CT611 | Feedwater pump header temperature | AI | 0 | 300 | °C
430 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 3 | HPH FEEDWATER #1B | WIKA-07NP08-ABD-201-20-006 | AAB10CT612 | AAB10CT612 | 11LAB10CT612 | NO.2 High pressure heater outlet water temperature | AI | 0 | 300 | °C
431 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 3 | HPH FEEDWATER #1B | WIKA-07NP08-ABD-201-20-010 | ABQ20CP101 | ABQ20CP101 | 11LBQ20CP101 | NO.2 HP heater inlet steam pressure | AI | 0 | 2.5 | MPa
432 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 3 | HPH FEEDWATER #1B | WIKA-07NP08-ABD-201-20-005 | AAD20CL101 | AAD20CL101 | 11LAD20CL101 | NO.2 HP heater level | AI | 0 | 800 | mm |  | 150 | 200 | 650
433 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 3 | HPH FEEDWATER #1B | WIKA-07NP08-ABD-201-20-017 | ACH10CT302 | ACH10CT302 | 11LCH10CT302 | NO.2 HP heater drain temperature | AI | 0 | 300 | °C
434 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 4 | HPH FEEDWATER #1A | WIKA-07NP08-ABD-201-20-006 | AAB10CT613 | AAB10CT613 | 11LAB10CT613 | NO.1 High pressure heater outlet water temperature | AI | 0 | 300 | °C
435 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 4 | HPH FEEDWATER #1A | WIKA-07NP08-ABD-201-20-009 | ABQ10CP101 | ABQ10CP101 | 11LBQ10CP101 | NO.1 HP heater inlet steam pressure | AI | 0 | 4 | MPa
436 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 4 | HPH FEEDWATER #1A | WIKA-07NP08-ABD-201-20-005 | AOD10CL101 | AOD10CL101 | 11LAD10CL101 | NO.1 HP heater level | AI | 0 | 800 | mm |  | 150 | 200 | 650
437 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 4 | HPH FEEDWATER #1A | WIKA-07NP08-ABD-201-20-017 | ACH10CT301 | ACH10CT301 | 11LCH10CT301 | NO.1 HP heater drain temperature | AI | 0 | 500 | °C
438 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-201-20-006 | AAB10T622 | AAB10T622 | 11LAB10CT622 | Economizer inlet water temperature | AI | 0 | 600 | °C
439 | 1 | UJLJ AMG #1 | 7 | FEED WATER | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-201-20-006 | AAB10CP122 | AAB10CP122 | 11LAB10CP122 | Economizer inlet water pressure | AI | 0 | 20 | MPa
440 | 1 | UJLJ AMG #1 | 7 | BOILER AFG | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT605 | ANA20CT605 | 11HNA20CT605 | Economizer outlet temperature(left) | AI | 0 | 600 | °C
441 | 1 | UJLJ AMG #1 | 7 | BOILER AFG | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CT606 | ANA20CT606 | 11HNA20CT606 | Economizer outlet temperature(right) | AI | 0 | 600 | °C
442 | 1 | UJLJ AMG #1 | 7 | BOILER AFG | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP107 | ANA20CP107 | 11HNA20CP107 | Economizer outlet pressure(left) | AI | -5 | 1 | KPa
443 | 1 | UJLJ AMG #1 | 7 | BOILER AFG | 5 | ECONOMIZER #1 | WIKA-07NP08-ABD-101-20-012 | ANA20CP108 | ANA20CP108 | 11HNA20CP108 | Economizer outlet pressure(right) | AI | -5 | 1 | KPa
444 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10T621 | AAB10T621 | 11LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
445 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10CP121 | AAB10CP121 | 11LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
446 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10CF1_1 | AAB10CF1_1 | 11LAB10CF121 | Main feedwater flow | AI | 0 | 150 | t/h
447 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | A_B10CF131 | A_B10CF131 | 11LAB10CF131 | First stage desuperheater spray water flow | AI | 0 | 8 | t/h
448 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | A_B10CF141 | A_B10CF141 | 11LAB10CF141 | Second stage desuperheater spray water flow | AI | 0 | 8 | t/h
449 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AB10A141MV | AB10A141MV | 11LAB10AA141AO | Feedwater main control valve control | AO | 0 | 100 | %
450 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10A141T | AAB10A141T | 11LAB10AA141GT | Feedwater main control valve position | AI | 0 | 100 | %
451 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AS04_E018.MV | AS04_E018.MV | 11LAB10AA131AO | Feedwater vice control valve control | AO | 0 | 100 | %
452 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10A131T | AAB10A131T | 11LAB10AA131GT | Feedwater vice control valve position | AI | 0 | 100 | %
453 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AS04_E003.MV | AS04_E003.MV | 11LAB10AA111AO | First stage attemperator left spray water control valve control | AO | 0 | 100 | %
454 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10A111T | AAB10A111T | 11LAB10AA111GT | First stage attemperator left spray water control valve position | AI | 0 | 100 | %
455 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AS04_E032.MV | AS04_E032.MV | 11LAB10AA121AO | Second stage attemperator left spray water control valve control | AO | 0 | 100 | %
456 | 1 | UJLJ AMG #1 | 7 | FEED WATER #1 | 5 | FEEDWATER PIPING #1 | WIKA-07NP08-ABD-201-20-006 | AAB10A121T | AAB10A121T | 11LAB10AA121GT | Second stage attemperator left spray water control valve position | AI | 0 | 100 | %
457 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CT201 | AAD10CT201 | 11HAD10CT201 | Drum Upper Metal Temperature 1 | AI | 0 | 600 | °C
458 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CT202 | AAD10CT202 | 11HAD10CT202 | Drum Upper Metal Temperature 2 | AI | 0 | 600 | °C
459 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CT203 | AAD10CT203 | 11HAD10CT203 | Drum Lower Metal Temperature 1 | AI | 0 | 600 | °C
460 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CT204 | AAD10CT204 | 11HAD10CT204 | Drum Lower Metal Temperature 2 | AI | 0 | 600 | °C
461 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CP101 | AAD10CP101 | 11HAD10CP101 | Drum Pressure | AI | 0 | 16 | MPa
462 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CP102 | AAD10CP102 | 11HAD10CP102 | Drum Pressure | AI | 0 | 16 | MPa
463 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CL1_1 | AAD10CL1_1 | 11HAD10CL101 | Drum Level | AI | -533 | 533 | mm |  | -280 | -200 | 125 | 200
464 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | AAD10CL1_2 | AAD10CL1_2 | 11HAD10CL102 | Drum Level | AI | -533 | 533 | mm |  | -280 | -200 | 125 | 200
465 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | STEAM DRUM #1 | WIKA-07NP08-ABD-101-20-35-01 | A_DRUM_LV | A_DRUM_LV |  | Drum Level Rate | AI | -533 | 533 | mm
466 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #1 | WIKA-07NP08-ABD-101-20-35 | ACQ10CL151 | ACQ10CL151 | 11LCQ10CL151 | Continuous blowdown tank level | AI | 0 | 500 | mm |  |  | 100 | 450
467 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #1 | WIKA-07NP08-ABD-101-20-35 | AS04_E020.MV | AS04_E020.MV | 11LCQ10AA101AO | Continuous blowdown control valve control | AO | 0 | 100 | %
468 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #1 | WIKA-07NP08-ABD-101-20-35 | ACQ10A101T | ACQ10A101T | 11LCQ10AA101GT | Continuous blowdown control valve position | AI | 0 | 100 | %
469 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT201 | AAH10CT201 | 11HAH10CT201 | Primary superheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 480
470 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT202 | AAH10CT202 | 11HAH10CT202 | Primary superheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 480
471 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT203 | AAH10CT203 | 11HAH10CT203 | Primary superheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 480
472 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT204 | AAH10CT204 | 11HAH10CT204 | Primary superheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 480
473 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT205 | AAH10CT205 | 11HAH10CT205 | Primary superheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 480
474 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT206 | AAH10CT206 | 11HAH10CT206 | Primary superheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 480
475 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT601 | AAH10CT601 | 11HAH10CT601 | Upper separator header outlet tube steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
476 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT602 | AAH10CT602 | 11HAH10CT602 | Upper separator header outlet tube steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
477 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT603 | AAH10CT603 | 11HAH10CT603 | Upper separator header outlet tube steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
478 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT604 | AAH10CT604 | 11HAH10CT604 | Upper separator header outlet tube steam temperature 4 | AI | 0 | 600 | °C |  |  |  | 455
479 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT211 | AAH10CT211 | 11HAH10CT211 | Platen superheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 500
480 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT212 | AAH10CT212 | 11HAH10CT212 | Platen superheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 500
481 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT213 | AAH10CT213 | 11HAH10CT213 | Platen superheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 500
482 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT214 | AAH10CT214 | 11HAH10CT214 | Platen superheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 500
483 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT215 | AAH10CT215 | 11HAH10CT215 | Platen superheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 500
484 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT216 | AAH10CT216 | 11HAH10CT216 | Platen superheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 500
485 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT217 | AAH10CT217 | 11HAH10CT217 | Platen superheater outlet tube metal temperature 7 | AI | 0 | 600 | °C |  |  |  | 500
486 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT218 | AAH10CT218 | 11HAH10CT218 | Platen superheater outlet tube metal temperature 8 | AI | 0 | 600 | °C |  |  |  | 500
487 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT611 | AAH10CT611 | 11HAH10CT611 | First stage desuperheater inlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
488 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT612 | AAH10CT612 | 11HAH10CT612 | First stage desuperheater inlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
489 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT613 | AAH10CT613 | 11HAH10CT613 | First stage desuperheater inlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
490 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT614 | AAH10CT614 | 11HAH10CT614 | First stage desuperheater outlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
491 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT615 | AAH10CT615 | 11HAH10CT615 | First stage desuperheater outlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
492 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT616 | AAH10CT616 | 11HAH10CT616 | First stage desuperheater outlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
493 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T621 | AAH10T621 | 11HAH10CT621 | Second stage desuperheater inlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
494 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T622 | AAH10T622 | 11HAH10CT622 | Second stage desuperheater inlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
495 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T623 | AAH10T623 | 11HAH10CT623 | Second stage desuperheater inlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
496 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T624 | AAH10T624 | 11HAH10CT624 | Second stage desuperheater outlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
497 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T625 | AAH10T625 | 11HAH10CT625 | Second stage desuperheater outlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
498 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T626 | AAH10T626 | 11HAH10CT626 | Second stage desuperheater outlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
499 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT231 | AAH10CT231 | 11HAH10CT231 | Finishing supperheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 565
500 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT232 | AAH10CT232 | 11HAH10CT232 | Finishing supperheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 565
501 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT233 | AAH10CT233 | 11HAH10CT233 | Finishing supperheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 565
502 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT234 | AAH10CT234 | 11HAH10CT234 | Finishing supperheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 565
503 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT235 | AAH10CT235 | 11HAH10CT235 | Finishing supperheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 565
504 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT236 | AAH10CT236 | 11HAH10CT236 | Finishing supperheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 565
505 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT237 | AAH10CT237 | 11HAH10CT237 | Finishing supperheater outlet tube metal temperature 7 | AI | 0 | 600 | °C |  |  |  | 565
506 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT238 | AAH10CT238 | 11HAH10CT238 | Finishing supperheater outlet tube metal temperature 8 | AI | 0 | 600 | °C |  |  |  | 565
507 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CT239 | AAH10CT239 | 11HAH10CT239 | Finishing supperheater outlet tube metal temperature 9 | AI | 0 | 600 | °C |  |  |  | 565
508 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10T631 | AAH10T631 | 11HAH10CT631 | Finishing supperheater outlet temperature | AI | 0 | 600 | °C |  |  | 520 | 545 | 600
509 | 1 | UJLJ AMG #1 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #1 | WIKA-07NP08-ABD-101-20-35 | AAH10CP101 | AAH10CP101 | 11HAH10CP101 | Finishing supperheater outlet pressure | AI | 0 | 16 | MPa |  |  | 8 | 9.5
510 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CT381 | AAV10CT381 | 11MAV10CT381 | Turbine thrust bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
511 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CT382 | AAV10CT382 | 11MAV10CT382 | Turbine front bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
512 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CT383 | AAV10CT383 | 11MAV10CT383 | Turbine rear bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
513 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CT384 | AAV10CT384 | 11MAV10CT384 | Generator front bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
514 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CT385 | AAV10CT385 | 11MAV10CT385 | Generator rear bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
515 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CP101 | AAV10CP101 | 11MAV10CP101 | Main oil pump outlet pressure | AI | 0 | 2.5 | MPa |  | 17 | 1.8
516 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV10CP111 | AAV10CP111 | 11MAV10CP111 | Lube oil pressure | AI | 0 | 0.25 | MPa |  | 0.04 | 0.055 | 0.25 | 0.25
517 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV72CT361 | AAV72CT361 | 11MAV72CT361 | Oil cooler inlet temperature | AI | 0 | 100 | °C
518 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV72CT362 | AAV72CT362 | 11MAV72CT362 | Oil cooler inlet temperature | AI | 0 | 100 | °C
519 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV72CT363 | AAV72CT363 | 11MAV72CT363 | Oil cooler outlet temperature | AI | 0 | 100 | °C
520 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV72CT364 | AAV72CT364 | 11MAV72CT364 | Oil cooler outlet temperature | AI | 0 | 100 | °C
521 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV73CL151 | AAV73CL151 | 11MAV73CL151 | Oil tank level | AI | -200 | 200 | mm |  | -160 | -80 | 80 | 160
522 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 | WIKA-07NP08-ABD-201-20-023 | AAV72CE011 | AAV72CE011 | 11MAV72CE011 | Auxiliary oil pump motor current | AI | 0 | 400 | A
523 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AAV72CT351 | AAV72CT351 | 11MAV72CT351 | NO.1 Oil cooler inlet water temperature | AI | 0 | 100 | °C
524 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AAV72CT352 | AAV72CT352 | 11MAV72CT352 | NO.1 Oil cooler outlet water temperature | AI | 0 | 100 | °C
525 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AAV72CT353 | AAV72CT353 | 11MAV72CT353 | NO.2 Oil cooler inlet water temperature | AI | 0 | 100 | °C
526 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AAV72CT354 | AAV72CT354 | 11MAV72CT354 | NO.2 Oil cooler outlet water temperature | AI | 0 | 100 | °C
527 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AGB10CT301 | AGB10CT301 | 11PGB10CT301 | Cooling water inlet temperature | AI | 0 | 100 | °C
528 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AGB10CT302 | AGB10CT302 | 11PGB10CT302 | Cooling water outlet temperature | AI | 0 | 100 | °C
529 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AGB10CT311 | AGB10CT311 | 11PGB10CT311 | Air cooler inlet water temperature | AI | 0 | 100 | °C
530 | 1 | UJLJ AMG #1 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #1 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | AGB10CT312 | AGB10CT312 | 11PGB10CT312 | Air cooler outlet water temperature | AI | 0 | 100 | °C
531 | 1 | UJLJ AMG #1 | 9 | TURBINE | 2 | TURNING GEAR #1 | WIKA-07NP08-ABD-201-20-023 | AAY41FE001 | AAY41FE001 | 11MAY41FE001 | Turning gear motor current | AI | 0 | 50 | A
532 | 1 | UJLJ AMG #1 | 9 | TURBINE | 3 | DEH #1 |  | AC02FE001 | AC02FE001 | 11MKY01FE001 | Generator power | Al | 0 | 75 | MW
533 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAW10CT601 | AAW10CT601 | 11MAW10CT601 | Gland steam pressure reducer and attemperator outlet temperature | AI | 0 | 600 | °C
534 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAW10CT602 | AAW10CT602 | 11MAW10CT602 | Gland steam pressure reducer and attemperator outlet temperature | AI | 0 | 600 | °C
535 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAW10CP101 | AAW10CP101 | 11MAW10CP101 | Gland steam pressure reducer and attemperator outlet pressure | AI | -0.1 | 1.5 | MPa |  |  | 0 | 0.9
536 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAW10CP103 | AAW10CP103 | 11MAW10CP103 | Surge tank pressure | AI | -0.1 | 1.5 | MPa
537 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAW10A001T | AAW10A001T | 11MAW10AA001GT | Gland steam pressure control valve position | AI | 0 | 100 | %
538 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | AAB20A101T | AAB20A101T | 11LAB20AA101GT | Gland steam temperature control valve position | AI | 0 | 100 | %
539 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | S16_E002.MV | S16_E002.MV | 11MAW10AA001AO | Gland steam pressure control valve control | AO | 0 | 100 | %
540 | 1 | UJLJ AMG #1 | 9 | TURBINE | 4 | GLAND STEAM #1 | WIKA-07NP08-ABD-201-20-026 | S16_E003.MV | S16_E003.MV | 11LAB20AA101AO | Gland steam temperature control valve control | AO | 0 | 100 | %
541 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | ABA10CT601 | ABA10CT601 | 11LBA10CT601 | Boiler outlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
542 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | ABA10CT611 | ABA10CT611 | 11LBA10CT611 | Turbine inlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
543 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | ABA10CP101 | ABA10CP101 | 11LBA10CP101 | Boiler outlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
544 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | ABA10CP113 | ABA10CP113 | 11LBA10CP113 | Turbine inlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
545 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | ABA10CF101 | ABA10CF101 | 11LBA10CF101 | Main steam flow | AI | 0 | 150 | t/h
546 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CT651 | AAA01CT651 | 11MAA01CT651 | Behind governing stage steam temperature | AI | 0 | 500 | °C
547 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CT652 | AAA01CT652 | 11MAA01CT652 | Behind governing stage steam temperature | AI | 0 | 500 | °C
548 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CT653 | AAA01CT653 | 11MAA01CT653 | Behind governing stage casing flange temperature | AI | 0 | 500 | °C
549 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CT654 | AAA01CT654 | 11MAA01CT654 | Behind governing stage casing flange temperature | AI | 0 | 500 | °C
550 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CT657 | AAA01CT657 | 11MAA01CT657 | Inside exhaust chamber temperature | AI | 0 | 200 | °C |  | 0 | 0 | 80 | 80
551 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CP101 | AAA01CP101 | 11MAA01CP101 | Behind governing stage steam pressure | AI | 0 | 10 | MPa
552 | 1 | UJLJ AMG #1 | 9 | TURBINE | 5 | MAIN STEAM #1 | WIKA-07NP08-ABD-201-20-005 | AAA01CP102 | AAA01CP102 | 11MAA01CP102 | Inside exhaust chamber pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
553 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT351 | AAA01CT351 | 11MAA01CT351 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
554 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT352 | AAA01CT352 | 11MAA01CT352 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
555 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT353 | AAA01CT353 | 11MAA01CT353 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
556 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT354 | AAA01CT354 | 11MAA01CT354 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
557 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT355 | AAA01CT355 | 11MAA01CT355 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
558 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT356 | AAA01CT356 | 11MAA01CT356 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
559 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT357 | AAA01CT357 | 11MAA01CT357 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
560 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 THRUST | WIKA-07NP08-ABD-201-20-023 | AAA01CT358 | AAA01CT358 | 11MAA01CT358 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
561 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CT365 | AAA01CT365 | 11MAA01CT365 | Turbine front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
562 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CT366 | AAA01CT366 | 11MAA01CT366 | Turbine front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
563 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CT367 | AAA01CT367 | 11MAA01CT367 | Turbine rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
564 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CT368 | AAA01CT368 | 11MAA01CT368 | Turbine rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
565 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CG151 | AAA01CG151 | 11MAA01CG151 | Turbine axial displacement | AI | -2 | -2 | mm |  | -1.5 | -1 | 1 | 1.5
566 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CG152 | AAA01CG152 | 11MAA01CG152 | Turbine axial displacement | AI | -2 | -2 | mm |  | -1.5 | -1 | 1 | 1.5
567 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CG153 | AAA01CG153 | 11MAA01CG153 | Turbine differential expension | AI | -5 | 7 | mm |  | -3 | -2
568 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CG154 | AAA01CG154 | 11MAA01CG154 | Turbine differential expension | AI | -5 | 7 | mm |  | -3 | -2
569 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CG161 | AAA01CG161 | 11MAA01CG161 | Turbine absolute expansion | AI | 0 | 25 | mm
570 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CG162 | AAA01CG162 | 11MAA01CG162 | Turbine absolute expansion | AI | 0 | 25 | mm
571 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CS154 | AAA01CS154 | 11MAA01CS154 | Turbine speed | AI | 0 | 3000 | rpm |  |  |  | 3210 | 3390
572 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CS155 | AAA01CS155 | 11MAA01CS155 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
573 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CS156 | AAA01CS156 | 11MAA01CS156 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
574 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CS157 | AAA01CS157 | 11MAA01CS157 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
575 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CS161 | AAA01CS161 | 11MAA01CS161 | Turbine speed | AI | 0 | 4000 | rpm |  |  |  | 3210 | 3390
576 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CY151 | AAA01CY151 | 11MAA01CY151 | Turbine front shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
577 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS1 | WIKA-07NP08-ABD-201-20-023 | AAA01CY152 | AAA01CY152 | 11MAA01CY152 | Turbine front shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
578 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CY153 | AAA01CY153 | 11MAA01CY153 | Turbine rear shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
579 | 1 | UJLJ AMG #1 | 9 | TURBINE | 6 | TURBINE #1 TS2 | WIKA-07NP08-ABD-201-20-023 | AAA01CY154 | AAA01CY154 | 11MAA01CY154 | Turbine rear shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
580 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT351 | AKA01CT351 | 11MKA01CT351 | Generator front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
581 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT352 | AKA01CT352 | 11MKA01CT352 | Generator front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
582 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT354 | AKA01CT354 | 11MKA01CT354 | Generator rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
583 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT355 | AKA01CT355 | 11MKA01CT355 | Generator outlet air temperature | AI | 0 | 150 | °C
584 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT356 | AKA01CT356 | 11MKA01CT356 | Generator outlet air temperature | AI | 0 | 150 | °C
585 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT361 | AKA01CT361 | 11MKA01CT361 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
586 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT362 | AKA01CT362 | 11MKA01CT362 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
587 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT363 | AKA01CT363 | 11MKA01CT363 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
588 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT364 | AKA01CT364 | 11MKA01CT364 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
589 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT365 | AKA01CT365 | 11MKA01CT365 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
590 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT366 | AKA01CT366 | 11MKA01CT366 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
591 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT367 | AKA01CT367 | 11MKA01CT367 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
592 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT368 | AKA01CT368 | 11MKA01CT368 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
593 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT369 | AKA01CT369 | 11MKA01CT369 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
594 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT370 | AKA01CT370 | 11MKA01CT370 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
595 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT371 | AKA01CT371 | 11MKA01CT371 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
596 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CT372 | AKA01CT372 | 11MKA01CT372 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
597 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CY151 | AKA01CY151 | 11MKA01CY151 | Generator front shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
598 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CY152 | AKA01CY152 | 11MKA01CY152 | Generator front shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
599 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CY153 | AKA01CY153 | 11MKA01CY153 | Generator rear shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
600 | 1 | UJLJ AMG #1 | 9 | TURBINE | 8 | GENERATOR #1 | WIKA-07NP08-ABD-201-20-023 | AKA01CY154 | AKA01CY154 | 11MKA01CY154 | Generator rear shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
601 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AC02FE001 | AC02FE001 | 11BAB02FE001 | Generator Active Power | AI | 0 | 45.5 | MW
602 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AC02FE004 | AC02FE004 | 11BAB02FE004 | Generator Frequency | AI | 0 | 50 | Hz
603 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AC01FE001 | AC01FE001 | 11BAB01FE001 | Excitation Current | AI | 0 | 100 | A
604 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AC01FE002 | AC01FE002 | 11BAB01FE002 | Excitation Voltage | AI | 0 | 100 | V
605 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ01YA05 | AJ01YA05 | 11BBA01YA05 | Ampere analog Signal from Multi Power Meter #1 | AI | 0 | 1000 | A
606 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ01YA06 | AJ01YA06 | 11BBA01YA06 | Watt analog Signal from Multi Power Meter #1 | AI | 0 | 25 | W
607 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ01YA07 | AJ01YA07 | 11BBA01YA07 | VAR analog Signal from Multi Power Meter #1 | AI | -25 | 25 | VAR
608 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ03YA01 | AJ03YA01 | 11BBA03YA01 | Watt analog Signal from Multi Power Meter Primary Air Fan #1 | AI | 0 | 100 | MW
609 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ03YA02 | AJ03YA02 | 11BBA03YA02 | VAR analog Signal from Multi Power Meter Primary Air Fan #1 | AI | 0 | 100 | VAR
610 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ04YA01 | AJ04YA01 | 11BBA04YA01 | Watt analog Signal from Multi Power Meter Secondary Air Fan #1 | AI | 0 | 100 | MW
611 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ04YA02 | AJ04YA02 | 11BBA04YA02 | VAR analog Signal from Multi Power Meter Secondary Air Fan #1 | AI | 0 | 100 | VAR
612 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ05YA01 | AJ05YA01 | 11BBA05YA01 | Watt analog Signal from Multi Power Meter ID Fan #1 | AI | 0 | 100 | MW
613 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ05YA02 | AJ05YA02 | 11BBA05YA02 | VAR analog Signal from Multi Power Meter ID Fan #1 | AI | 0 | 100 | VAR
614 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ06YA01 | AJ06YA01 | 11BBA06YA01 | Watt analog Signal from Multi Power Meter Boiler Feed Pump #1 | AI | 0 | 100 | MW
615 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ06YA02 | AJ06YA02 | 11BBA06YA02 | VAR analog Signal from Multi Power Meter Boiler Feed Pump #1 | AI | 0 | 100 | VAR
616 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ07YA01 | AJ07YA01 | 11BBA07YA01 | Watt analog Signal from Multi Power Meter Boiler Feed Pump #2 | AI | 0 | 100 | MW
617 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ07YA02 | AJ07YA02 | 11BBA07YA02 | VAR analog Signal from Multi Power Meter Boiler Feed Pump #2 | AI | 0 | 100 | VAR
618 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ08YA01 | AJ08YA01 | 11BBA08YA01 | Watt analog Signal from Multi Power Meter Circulating Water Pump #1 | AI | 0 | 100 | MW
619 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ08YA02 | AJ08YA02 | 11BBA08YA02 | VAR analog Signal from Multi Power Meter Circulating WaterPump #1 | AI | 0 | 100 | VAR
620 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ09YA01 | AJ09YA01 | 11BBA09YA01 | Watt analog Signal from Multi Power Meter Circulating Water Pump #2 | AI | 0 | 100 | MW
621 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ09YA02 | AJ09YA02 | 11BBA09YA02 | VAR analog Signal from Multi Power Meter Circulating WaterPump #2 | AI | 0 | 100 | VAR
622 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ10XA01 | AJ10XA01 | 11BBA10XA01 | Watt analog Signal from Multi Power Meter Closed Cooling Water Pump #1 | AI | 0 | 100 | MW
623 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ10XA02 | AJ10XA02 | 11BBA10XA02 | VAR analog Signal from Multi Power Meter Closed Cooling WaterPump #1 | AI | 0 | 100 | VAR
624 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ11YA05 | AJ11YA05 | 11BBA11YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #1 | AI | 0 | 100 | %
625 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ11YA06 | AJ11YA06 | 11BBA11YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #1 | AI | 0 | 100 | %
626 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ11YA07 | AJ11YA07 | 11BBA11YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #1 | AI | 0 | 100 | %
627 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ12YA05 | AJ12YA05 | 11BBA12YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #1 | AI | 0 | 100 | %
628 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ12YA06 | AJ12YA06 | 11BBA12YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #1 | AI | 0 | 100 | %
629 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ12YA07 | AJ12YA07 | 11BBA12YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #1 | AI | 0 | 100 | %
630 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ13YA05 | AJ13YA05 | 11BBA13YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #1 | AI | 0 | 100 | %
631 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ13YA06 | AJ13YA06 | 11BBA13YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #1 | AI | 0 | 100 | %
632 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ13YA07 | AJ13YA07 | 11BBA13YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #1 | AI | 0 | 100 | %
633 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ14YA05 | AJ14YA05 | 11BBA14YA05 | Ampere analog signal from Multi Power Meter Bus Coupler | AI | 0 | 100 | %
634 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ14YA06 | AJ14YA06 | 11BBA14YA06 | Watt analog signal from Multi Power Meter Bus Coupler | AI | 0 | 100 | %
635 | 1 | UJLJ AMG #1 | 11 | MAIN TRAFO #1 | 2 | ELECTRICAL #1 | WIKA-07NP08-ABD-201-30-001 | AJ14YA07 | AJ14YA07 | 11BBA14YA07 | VAR analog signal from Multi Power Meter Bus Coupler | AI | 0 | 100 | %
636 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQC30AP01C | DQC30AP01C | QCA30AP001FC | NO.1 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
637 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUG20Q101 | DQUG20Q101 | 10QUG20CQ101 | CATION CONDUCTIVITY FOR MAKE UP WATER | Al | 0 | 100 | uS/cm
638 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQC30AP01F | DQC30AP01F | 10QCA30AP001FQ | NO.1 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
639 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUC20Q101 | DQUC20Q101 | 10QUC20CQ101 | CATION CONDUCTIVITY FOR 1# CONDENSATE WATER PUMP OUTLET | Al | 0 | 100 | uS/cm
640 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUC20Q102 | DQUC20Q102 | 10QUC20CQ102 | DISSOLVE OXYGEN FOR 1# CONDENSATE WATER PUMP OUTLET | Al | 0 | 20 | ppb
641 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUA20Q101 | DQUA20Q101 | 10QUA20CQ101 | DISSOLVED OXYGEN FOR 1# DEAERATOR OUTLET | Al | 0 | 20 | ppb
642 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUA22Q101 | DQUA22Q101 | 10QUA22CQ101 | CATION CONDUCTIVITY FOR 1# FEED WATER AT ECONOMIZER INLET | Al | 0 | 100 | uS/cm
643 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | MVC31AP01C | MVC31AP01C | 10QCA31AP001FC | NO.2 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
644 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUA22Q102 | DQUA22Q102 | 10QUA22CQ102 | pH FOR 1# FEED WATER AT ECONOMIZER INLET | Al | 0 | 14 | pH
645 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQC31AP01F | DQC31AP01F | 10QCA31AP001FQ | NO.2 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
646 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUA22Q103 | DQUA22Q103 | 10QUA22CQ103 | HYDRAZINE FOR 1# FEED WATER AT ECONOMIZER INLET | Al | 0 | 999 | ppb
647 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUH20Q101 | DQUH20Q101 | 10QUH20CQ101 | SPECIFIC CONDUCTIVITY FOR 1# BOILER DRUM WATER | Al | 0 | 100 | uS/cm
648 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0104 | DQUH20Q102 | DQUH20Q102 | 10QUH20CQ102 | pH FOR 1# BOILER DRUM WATER | Al | 0 | 14 | pH
649 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUH20Q103 | DQUH20Q103 | 10QUH20CQ103 | SILICA FOR 1# BOILER DRUM WATER | Al | 0 | 20 | ppb
650 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | MVC32AP01C | MVC32AP01C | 10QCA32AP001FC | NO.3 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
651 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUB20Q101 | DQUB20Q101 | 10QUB20CQ101 | CATION CONDUCTIVITY FOR 1# SATURATED STEAM | Al | 0 | 100 | uS/cm
652 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQC32AP01F | DQC32AP01F | 10QCA32AP001FQ | NO.3 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
653 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUB20Q102 | DQUB20Q102 | 10QUB20CQ102 | SILICA FOR 1# SATURATED STEAM | Al | 0 | 20 | ppb
654 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUB21Q101 | DQUB21Q101 | 10QUB21CQ101 | CATION CONDUCTIVITY FOR 1# SUPERHEATED STEAM | Al | 0 | 100 | uS/cm
655 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUC21Q101 | DQUC21Q101 | 10QUC21CQ101 | CATION CONDUCTIVITY FOR 2# CONDENSATE WATER PUMP OUTLET | Al | 0 | 100 | uS/cm
656 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUC21Q102 | DQUC21Q102 | 10QUC21CQ102 | DISSOLVE OXYGEN FOR 2# CONDENSATE WATER PUMP OUTLET | Al | 0 | 20 | ppb
657 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | MVC40AP01C | MVC40AP01C | 10QCA40AP001FC | NO.4 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
658 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0102 | DQUA21Q101 | DQUA21Q101 | 10QUA21CQ101 | DISSOLVE OXYGEN FOR 2# DEAERATOR OUTLET | Al | 0 | 20 | ppb
659 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DOC40AP01F | DOC40AP01F | 10QCA40AP001FQ | NO.4 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
660 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUA23Q101 | DQUA23Q101 | 10QUA23CQ101 | CATION CONDUCTIVITY FOR 2# FEED WATER AT ECONOMIZER INLET | Al | 0 | 100 | uS/cm
661 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUA23Q102 | DQUA23Q102 | 10QUA23CQ102 | pH FOR 2# FEED WATER AT ECONOMIZER INLET | Al | 0 | 14 | pH
662 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUA23Q103 | DQUA23Q103 | 10QUA23CQ103 | HYDRAZINE FOR 2# FEED WATER AT ECONOMIZER INLET | Al | 0 | 999 | ug/l
663 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUH21Q101 | DQUH21Q101 | 10QUH21CQ101 | SPECIFIC CONDUCTIVITY FOR 2# BOILER DRUM WATER | Al | 0 | 100 | uS/cm
664 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | MVC41AP01C | MVC41AP01C | 10QCA41AP001FC | NO.5 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
665 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUH21Q102 | DQUH21Q102 | 10QUH21CQ102 | pH FOR 2# BOILER DRUM WATER | Al | 0 | 14 | pH
666 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DOC41AP01F | DOC41AP01F | 10QCA41AP001FQ | NO.5 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
667 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUH21Q103 | DQUH21Q103 | 10QUH21CQ103 | SILICA FOR 2# BOILER DRUM WATER | Al | 0 | 20 | ppb
668 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUB22Q101 | DQUB22Q101 | 10QUB22CQ101 | CATION CONDUCTIVITY FOR 2# SATURATED STEAM | Al | 0 | 100 | uS/cm
669 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUB22Q102 | DQUB22Q102 | 10QUB22CQ102 | SILICA FOR 2# SATURATED STEAM | Al | 0 | 20 | ppb
670 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DQUB23Q101 | DQUB23Q101 | 10QUB23CQ101 | CATION CONDUCTIVITY FOR 2# SUPERHEATED STEAM | Al | 0 | 100 | uS/cm
671 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | MVC42AP01C | MVC42AP01C | 10QCA42AP001FC | NO.6 HYDRAZINE DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
672 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0103 | DOC42AP01F | DOC42AP01F | 10QCA42AP001FQ | NO.6 HYDRAZINE DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
673 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | MVD30AP01C | MVD30AP01C | 10QCD30AP001FC | NO.1 AMMONIUM DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
674 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | DOD30AP01F | DOD30AP01F | 10QCD30AP001FQ | NO.1 AMMONIUM DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
675 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | MVD31AP01C | MVD31AP01C | 10QCD31AP001FC | NO.2 AMMONIUM DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
676 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | DOD31AP01F | DOD31AP01F | 10QCD31AP001FQ | NO.2 AMMONIUM DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
677 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | MVD32AP01C | MVD32AP01C | 10QCD32AP001FC | NO.3 AMMONIUM DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
678 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | DOD32AP01F | DOD32AP01F | 10QCD32AP001FQ | NO.3 AMMONIUM DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
679 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | MVD40AP01C | MVD40AP01C | 10QCD40AP001FC | NO.4 AMMONIUM DOSING PUMP FREQUENCY CONTROL | AO | 0 | 100 | %
680 | 1 | UJLJ AMG #1 | 12 | GENERAL | 1 | CHEMICAL DOSING #1 | WIKA-07NP08-ABD-101-20-005-0101 | DOD40AP01F | DOD40AP01F | 10QCD40AP001FQ | NO.4 AMMONIUM DOSING PUMP FREQUENCY | Al | 0 | 100 | Hz
681 | 1 | UJLJ AMG #1 | 12 | GENERAL | 2 | FUEL OIL TANK #1 | WIKA-07NP08-ABD-000-30-018-02 | DEB01CL101 | DEB01CL101 | 10EGB01CL101 | NO 1 OIL STORAGE TANK LEVEL TRANSMITTER 1 | Al | 0 | 5.75 | m |  |  | 0.26 | 5.25
682 | 1 | UJLJ AMG #1 | 12 | GENERAL | 2 | FUEL OIL TANK #1 | WIKA-07NP08-ABD-000-30-018-02 | DEB01CL102 | DEB01CL102 | 10EGB01CL102 | NO 2 OIL STORAGE TANK LEVEL TRANSMITTER 2 | Al | 0 | 5.75 | m |  |  | 0.26 | 5.25
683 | 1 | UJLJ AMG #1 | 12 | GENERAL | 3 | INSTRUMENT AIR #1 | WIKA-07NP08-ABD-300-20-002B | DQF1CT101 | DQF1CT101 | 10QFA10CT101 | HEADER INSTRUMENT AIR TEMPERATURE TRANSMITTER | AI | 0 | 200 | °C
684 | 1 | UJLJ AMG #1 | 12 | GENERAL | 3 | INSTRUMENT AIR #1 | WIKA-07NP08-ABD-300-20-002B | DQF1CP102 | DQF1CP102 | 10QFA10CP102 | OUTPUT INSTRUMENT AIR RECEIVER PRESSURE TRANSMITTER | AI | 0 | 12 | KG/CM2
685 | 1 | UJLJ AMG #1 | 12 | GENERAL | 4 | SERVICE AIR #1 | WIKA-07NP08-300-20-002A | DQE1CP102 | DQE1CP102 | 10QEA10CP102 | HEADER SERVICE AIR PRESSURE TRANSMITTER | AI | 0 | 12 | KG/CM2
686 | 1 | UJLJ AMG #1 | 12 | GENERAL | 5 | Bottom Ash Handling System #1 | WIKA-07NP08-ABD-100-20-005 | DTD01CS01 | DTD01CS01 | 10ETD01CS001 | SPEED SENSOR BOTTOM ASH BELT CONVEYOR | Al | 0 | 50 | METER/SEC |  | 0 | 0 | 50 | 50
687 | 1 | UJLJ AMG #1 | 12 | GENERAL | 5 | Bottom Ash Handling System #1 | WIKA-07NP08-ABD-100-20-005 | DTD02CS01 | DTD02CS01 | 10ETD02CS001 | SPEED SENSOR BUCKET ELEVATOR | Al | 0 | 1 | METER/SEC |  | 0 | 0 | 1 | 1
688 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2A | WIKA-07NP08-ABD-305-20-014-01 | BAB01CL103 | BAB01CL103 | 12PAB01CL103 | NO.3 Circulating water pump inlet suction well level | AI | 0 | 8 | m |  | 1.68 | 1.78
689 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2A | WIKA-07NP08-ABD-305-20-014-01 | BAB01CE010 | BAB01CE010 | 12PAB01CE010 | No.3 circulating water pump motor current | AI | 0 | 200 | A
690 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2A | WIKA-07NP08-ABD-305-20-014-01 | BPAC1CT01 | BPAC1CT01 | 12PAB01CT010 | No.3 circulating water pump motor temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
691 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2B | WIKA-07NP08-ABD-305-20-014-01 | BAB02CL103 | BAB02CL103 | 12PAB02CL103 | NO.4 Circulating water pump inlet suction well level | AI | 0 | 8 | m |  | 1.68 | 1.78
692 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2B | WIKA-07NP08-ABD-305-20-014-01 | BAB02CE010 | BAB02CE010 | 12PAB02CE010 | No.4 circulating water pump motor current | AI | 0 | 200 | A
693 | 2 | UJLJ AMG #2 | 2 | CIRCULATING WATER SYSTEM | 2 | CIRCULATING WATER PUMP #2B | WIKA-07NP08-ABD-305-20-014-01 | BPAC2CT01 | BPAC2CT01 | 12PAB02CT010 | No.4 circulating water pump motor temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
694 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT251 | BNC10CT251 | 12HNC10CT251 | I.D Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
695 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT252 | BNC10CT252 | 12HNC10CT252 | I.D Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
696 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT253 | BNC10CT253 | 12HNC10CT253 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
697 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT254 | BNC10CT254 | 12HNC10CT254 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
698 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT255 | BNC10CT255 | 12HNC10CT255 | I.D Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
699 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT261 | BNC10CT261 | 12HNC10CT261 | I.D Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
700 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CT262 | BNC10CT262 | 12HNC10CT262 | I.D Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
701 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 2 | ESP #2 | WIKA-07NP08-ABD-101-20-038 | BNA30CT301 | BNA30CT301 | 12HNA30CT301 | Boiler Outlet Gas Temperature | AI | 0 | 200 | °C
702 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 2 | ESP #2 | WIKA-07NP08-ABD-101-20-038 | BNA30CP101 | BNA30CP101 | 12HNA30CP101 | Boiler Outlet Gas Pressure | AI | -10 | 0 | KPa
703 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 2 | ESP #2 | WIKA-07NP08-ABD-101-20-038 | BNA30CQ101 | BNA30CQ101 | 12HNA30CQ101 | Boiler Outlet Gas S02 | AI | 0 | 1000 | mg/Nm3
704 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 2 | ESP #2 | WIKA-07NP08-ABD-101-20-038 | BNA40CT301 | BNA40CT301 | 12HNA40CT301 | E.S.P Outlet Gas Temperature | AI | 0 | 200 | °C
705 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 2 | ESP #2 | WIKA-07NP08-ABD-101-20-038 | BNA40CP101 | BNA40CP101 | 12HNA40CP101 | E.S.P Outlet Gas Pressure | AI | -10 | 0 | KPa
706 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | B40A101AMV | B40A101AMV | 12HNA40AA101AO | I.D. fan inlet control damp position | AO | 0 | 100 | %
707 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNA40A101T | BNA40A101T | 12HNA40AA101GT | I.D. fan inlet control damp position | AI | 0 | 100 | %
708 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BNC10CE010 | BNC10CE010 | 12HNC10CE010 | LD. fan motor current | AI | 0 | 200 | A
709 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BTH0782A_1 | BTH0782A_1 | 12HLB30VX010 | I.D. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
710 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 1 | ID FAN #2 | WIKA-07NP08-ABD-101-20-038 | BTH0782A_2 | BTH0782A_2 | 12HLB30VY010 | I.D. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
711 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT601 | BNA20CT601 | 12HNA20CT601 | Primary superheater inlet temperature(Ieft) | AI | 0 | 600 | °C
712 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT602 | BNA20CT602 | 12HNA20CT602 | Primary superheater inlet temperature(right) | AI | 0 | 600 | °C
713 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT603 | BNA20CT603 | 12HNA20CT603 | Primary superheater outlet temperature(left) | AI | 0 | 600 | °C
714 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT604 | BNA20CT604 | 12HNA20CT604 | Primary superheater outlet temperature(right) | AI | 0 | 600 | °C
715 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP101 | BNA20CP101 | 12HNA20CP101 | Finishing superheater inlet pressure(left) | AI | -3 | 1 | KPa
716 | 2 | UJLJ AMG #2 | 8 | BOILER AFG | 6 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP102 | BNA20CP102 | 12HNA20CP102 | Finishing superheater inlet pressure(right) | AI | 3 | 1 | KPa
717 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP103 | BNA20CP103 | 12HNA20CP103 | Primary superheater inlet pressure(left) | AI | -3 | 1 | KPa
718 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP104 | BNA20CP104 | 12HNA20CP104 | Primary superheater inlet pressure(right) | AI | -3 | 1 | KPa
719 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP105 | BNA20CP105 | 12HNA20CP105 | Primary superheater outlet pressure(left) | AI | -5 | 1 | KPa
720 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP106 | BNA20CP106 | 12HNA20CP106 | Primary superheater outlet pressure(right) | AI | -5 | 1 | KPa
721 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CQ101 | BNA20CQ101 | 12HNA20CQ101 | Primary superheater outlet Oxygen(left) | AI | 0 | 25 | %
722 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CQ102 | BNA20CQ102 | 12HNA20CQ102 | Primary superheater outlet Oxygen(right) | AI | 0 | 25 | %
723 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BLD10CT601 | BLD10CT601 | 12HLD10CT601 | Air heater outlet temperature(left) | AI | 0 | 600 | °C
724 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BLD10CT602 | BLD10CT602 | 12HLD10CT602 | Air heater outlet temperature(right) | AI | 0 | 600 | °C
725 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BLD10CP101 | BLD10CP101 | 12HLD10CP101 | Air heater outlet pressure(left) | AI | -8 | 0 | KPa
726 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | AIR HEATER #2 | WIKA-07NP08-ABD-101-20-012 | BLD10CP102 | BLD10CP102 | 12HLD10CP102 | Air heater outlet pressure(right) | AI | -8 | 0 | KPa
727 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | BAN40CT601 | BAN40CT601 | 12HAN40CT601 | Left sootblow drain temperature | AI | 0 | 450 | °C
728 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | BAN40CT602 | BAN40CT602 | 12HAN40CT602 | Right sootblow drain temperature | AI | 0 | 450 | °C
729 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | AS12_E001.MV | AS12_E001.MV | 12HCB05AA101AO | Sootblow steam pressure control valve control | AO | 0 | 100 | %
730 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | BCB05A101T | BCB05A101T | 12HCB05AA101GT | Sootblow steam pressure control valve position | AI | 0 | 100 | %
731 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | BCB10CP151 | BCB10CP151 | 12HCB10CP151 | Pressure Reducing sootblow terminal | AI | 0 | 4 | MPa
732 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 3 | SOOTBLOWER #2 | WIKA-07NP08-ABD-201-20-031 | BCB10CP152 | BCB10CP152 | 12HCB10CP152 | Pressure Reducing sootblow terminal | AI | 0 | 4 | MPa
733 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT201 | BNF10CT201 | 12HNF10CT201 | Cyclone upper metal temperature 1 | AI | 0 | 1200 | °C
734 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT202 | BNF10CT202 | 12HNF10CT202 | Cyclone upper metal temperature 2 | AI | 0 | 1200 | °C
735 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT203 | BNF10CT203 | 12HNF10CT203 | Cyclone upper metal temperature 3 | AI | 0 | 1200 | °C
736 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT204 | BNF10CT204 | 12HNF10CT204 | Cyclone upper metal temperature 4 | AI | 0 | 1200 | °C
737 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT211 | BNF10CT211 | 12HNF10CT211 | Cyclone lower metal temperature 1 | AI | 0 | 1200 | °C
738 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT212 | BNF10CT212 | 12HNF10CT212 | Cyclone lower metal temperature 2 | AI | 0 | 1200 | °C
739 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT213 | BNF10CT213 | 12HNF10CT213 | Cyclone lower metal temperature 3 | AI | 0 | 1200 | °C
740 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT214 | BNF10CT214 | 12HNF10CT214 | Cyclone lower metal temperature 4 | AI | 0 | 1200 | °C
741 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT215 | BNF10CT215 | 12HNF10CT215 | Cyclone lower metal temperature 5 | AI | 0 | 1200 | °C
742 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT216 | BNF10CT216 | 12HNF10CT216 | Cyclone lower metal temperature 6 | AI | 0 | 1200 | °C
743 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT217 | BNF10CT217 | 12HNF10CT217 | Cyclone lower metal temperature 7 | AI | 0 | 1200 | °C
744 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT218 | BNF10CT218 | 12HNF10CT218 | Cyclone lower metal temperature 8 | AI | 0 | 1200 | °C
745 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT601 | BNF10CT601 | 12HNF10CT601 | Cyclone inlet temperature | AI | 0 | 1200 | °C
746 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CP101 | BNF10CP101 | 12HNF10CP101 | Cyclone inlet pressure | AI | -5 | 5 | KPa
747 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNA11CT601 | BNA11CT601 | 11HNA11CT601 | Cyclone outlet temperature | AI | 0 | 1200 | °C
748 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | CYCLONE #2 | WIKA-07NP08-ABD-101-20-012 | BNA11CP101 | BNA11CP101 | 11HNA11CP101 | Cyclone outlet pressure | AI | -7 | 1 | KPa
749 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CT602 | BNF10CT602 | 12HNF10CT602 | J valve ash temperature | AI | 0 | 1200 | °C
750 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CP102 | BNF10CP102 | 12HNF10CP102 | J valve inlet pressure | AI | -11 | 40 | KPa
751 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10CP103 | BNF10CP103 | 12HNF10CP103 | J valve outlet pressure | AI | -20 | 60 | KPa
752 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10DP101 | BNF10DP101 | 12HNF10DP101 | J valve density | AI | -10 | 30 | KPa
753 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10DP102 | BNF10DP102 | 12HNF10DP102 | J valve sealing height | AI | -10 | 30 | KPa
754 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | ( J - VALVE) #2 | WIKA-07NP08-ABD-101-20-012 | BNF10DP103 | BNF10DP103 | 12HNF10DP103 | J valve level | AI | -20 | 60 | KPa
755 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2A | WIKA-07NP08-ABD-101-20-031 | BEH10CP101 | BEH10CP101 | 12QEH10CP101 | HP Seal Blower 1 Outlet Pressure | AI | 0 | 100 | KPa
756 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2B | WIKA-07NP08-ABD-101-20-031 | BEH20CP101 | BEH20CP101 | 12QEH20CP101 | HP Seal Blower 2 Outlet Pressure | AI | 0 | 100 | KPa
757 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | BEH41CF101 | BEH41CF101 | 12QEH41CF101 | Return Leg HP fluidized air Flow(Left) | AI | 0 | 700 | Nm3/h
758 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | BEH42CF101 | BEH42CF101 | 12QEH42CF101 | Return Leg HP fluidized air Flow(right) | AI | 0 | 700 | Nm3/h
759 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | AS10_E010.MV | AS10_E010.MV | 12QEH30AA111AO | HP seal air pressure control damp control | AO | 0 | 100 | %
760 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | BEH30A111T | BEH30A111T | 12QEH30AA111GT | HP seal air pressure control damp position | AI | 0 | 100 | %
761 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | AS10_E023.MV | AS10_E023.MV | 12QEH41AA111AO | Return leg left fluidized air control damp control | AO | 0 | 100 | %
762 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | BEH41A111T | BEH41A111T | 12QEH41AA111GT | Return leg left fluidized air control damp position | AI | 0 | 100 | %
763 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | AS10_E024.MV | AS10_E024.MV | 12QEH42AA111AO | Return leg right fluidized air control damp control | AO | 0 | 100 | %
764 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2 | WIKA-07NP08-ABD-101-20-031 | BEH42A111T | BEH42A111T | 12QEH42AA111GT | Return leg right fluidized air control damp position | AI | 0 | 100 | %
765 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2A | WIKA-07NP08-ABD-101-20-031 | BEH11CE010 | BEH11CE010 | 12QEH11CE010 | HP Seal Blower 1 Motor Current | AI | 0 | 100 | A
766 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 4 | HP SEAL BLOWER #2B | WIKA-07NP08-ABD-101-20-031 | BEH12CE010 | BEH12CE010 | 12QEH12CE010 | HP Seal Blower 2 Motor Current | AI | 0 | 100 | A
767 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT601 | BBK10CT601 | 12HBK10CT601 | Furnace temperature(left lower 1) | AI | 0 | 1200 | °C
768 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT602 | BBK10CT602 | 12HBK10CT602 | Furnace temperature(left lower 2) | AI | 0 | 1200 | °C
769 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT603 | BBK10CT603 | 12HBK10CT603 | Furnace temperature (left upper 1) | AI | 0 | 1200 | °C
770 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT604 | BBK10CT604 | 12HBK10CT604 | Furnace temperature(left upper 2) | AI | 0 | 1200 | °C
771 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT605 | BBK10CT605 | 12HBK10CT605 | Furnace temperature(right lower 1) | AI | 0 | 1200 | °C
772 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT606 | BBK10CT606 | 12HBK10CT606 | Furnace temperature(right lower 2) | AI | 0 | 1200 | °C
773 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT607 | BBK10CT607 | 12HBK10CT607 | Furnace temperature(right upper 1) | AI | 0 | 1200 | °C
774 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT608 | BBK10CT608 | 12HBK10CT608 | Furnace temperature(right upper 2) | AI | 0 | 1200 | °C
775 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT611 | BBK10CT611 | 12HBK10CT611 | Furnace outlet temperature(left) | AI | 0 | 1200 | °C
776 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10CT612 | BBK10CT612 | 12HBK10CT612 | Furnace outlet temperature(right) | AI | 0 | 1200 | °C
777 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T621A | BBK10T621A | 12HBK10CT621A | Furnace bed temperature 1a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
778 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T621B | BBK10T621B | 12HBK10CT621B | Furnace bed temperature 1b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
779 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T622A | BBK10T622A | 12HBK10CT622A | Furnace bed temperature 2a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
780 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T622B | BBK10T622B | 12HBK10CT622B | Furnace bed temperature 2b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
781 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T623A | BBK10T623A | 12HBK10CT623A | Furnace bed temperature 3a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
782 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T623B | BBK10T623B | 12HBK10CT623B | Furnace bed temperature 3b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
783 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WlKA-07NP08-ABD-101-20-012 | BBK10T624A | BBK10T624A | 12HBK10CT624A | Furnace bed temperature 4a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
784 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T624B | BBK10T624B | 12HBK10CT624B | Furnace bed temperature 4b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
785 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T625A | BBK10T625A | 12HBK10CT625A | Furnace bed temperature 5a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
786 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T625B | BBK10T625B | 12HBK10CT625B | Furnace bed temperature 5b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
787 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T626A | BBK10T626A | 12HBK10CT626A | Furnace bed temperature 6a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
788 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T626B | BBK10T626B | 12HBK10CT626B | Furnace bed temperature 6b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
789 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T627A | BBK10T627A | 12HBK10CT627A | Furnace bed temperature 7a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
790 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T627B | BBK10T627B | 12HBK10CT627B | Furnace bed temperature 7b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
791 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T628A | BBK10T628A | 12HBK10CT628A | Furnace bed temperature 8a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
792 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T628B | BBK10T628B | 12HBK10CT628B | Furnace bed temperature 8b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
793 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T629A | BBK10T629A | 12HBK10CT629A | Furnace bed temperature 9a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
794 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T629B | BBK10T629B | 12HBK10CT629B | Furnace bed temperature 9b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
795 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T630A | BBK10T630A | 12HBK10CT630A | Furnace bed temperature 10a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
796 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T630B | BBK10T630B | 12HBK10CT630B | Furnace bed temperature 10b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
797 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T631A | BBK10T631A | 12HBK10CT631A | Furnace bed temperature 11a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
798 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T631B | BBK10T631B | 12HBK10CT631B | Furnace bed temperature 11b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
799 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T632A | BBK10T632A | 12HBK10CT632A | Furnace bed temperature 12a | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
800 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10T632B | BBK10T632B | 12HBK10CT632B | Furnace bed temperature 12b | AI | 0 | 1200 | °C |  |  |  | 990 | 1050
801 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP101 | BBK10CP101 | 12HBK10CP101 | Boiler bed levels pressure | AI | 6 | 10 | KPa
802 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP102 | BBK10CP102 | 12HBK10CP102 | Boiler bed levels pressure (right) | AI | 6 | 10 | KPa
803 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP103 | BBK10CP103 | 12HBK10CP103 | Furnace lower part pressure(left) | AI | 2 | 8 | KPa
804 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP104 | BBK10CP104 | 12HBK10CP104 | Furnace lower part pressure(right | AI | 2 | 8 | KPa
805 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP105 | BBK10CP105 | 12HBK10CP105 | Furnace middle part pressure(left) | AI | 2 | 3 | KPa
806 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP106 | BBK10CP106 | 12HBK10CP106 | Furnace middle part pressure(right | AI | 2 | 3 | KPa
807 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP107 | BBK10CP107 | 12HBK10CP107 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
808 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP108 | BBK10CP108 | 12HBK10CP108 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
809 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP109 | BBK10CP109 | 12HBK10CP109 | Furnace upper part pressure(left) | AI | -4 | 4 | KPa
810 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP110 | BBK10CP110 | 12HBK10CP110 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
811 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP111 | BBK10CP111 | 12HBK10CP111 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
812 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10CP112 | BBK10CP112 | 12HBK10CP112 | Furnace upper part pressure(right) | AI | -4 | 4 | KPa
813 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP101 | BBK10DP101 | 12HBK10DP101 | Boiler bed material density (left) | AI | 0 | 10 | KPa
814 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP102 | BBK10DP102 | 12HBK10DP102 | Boiler bed material densiy (right) | AI | 0 | 10 | KPa
815 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP103 | BBK10DP103 | 12HBK10DP103 | Boiler bed levels D.P. | AI | 0 | 10 | KPa
816 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP104 | BBK10DP104 | 12HBK10DP104 | Boiler bed levels D.P. | AI | 0 | 10 | KPa
817 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP105 | BBK10DP105 | 12HBK10DP105 | Furnace DP.(left) | AI | -5 | 5 | KPa
818 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 | WIKA-07NP08-ABD-101-20-012 | BBK10DP106 | BBK10DP106 | 12HBK10DP106 | Furnace D.P.(right) | AI | -5 | 5 | KPa
819 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | BLA40CP101 | BLA40CP101 | 12HLA40CP101 | Winbox plenum pressure(left) | AI | 0 | 20 | KPa
820 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | BLA40CP102 | BLA40CP102 | 12HLA40CP102 | Winbox plenum pressure(right) | AI | 0 | 20 | KPa
821 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | BBK10CT613 | BBK10CT613 | 12HBK10CT613 | Windbox Plenum 1A | AI | 0 | 1200 | °C
822 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE #2 (WINBOX PLENUM) | WIKA-07NP08-ABD-101-20-012 | BBK10CT614 | BBK10CT614 | 12HBK10CT614 | Windbox Plenum 1B | AI | 0 | 1200 | °C
823 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF05CP101 | BJF05CP101 | 12HJF05CP101 | Gun feed oil pressure | AI | 0 | 4 | MPa
824 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF06CP101 | BJF06CP101 | 12HJF06CP101 | Gun return oil pressure | AI | 0 | 4 | MPa
825 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF06CF101 | BJF06CF101 | 12HJF06CF101 | Gun return oil flow | AI | 0 | 8 | t/h
826 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF30CP101 | BJF30CP101 | 12HJF30CP101 | In-bed gun 1 inlet pressure | AI | 0 | 4 | MPa
827 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF30CF101 | BJF30CF101 | 12HJF30CF101 | In-bed gun 1 inlet flow | AI | 0 | 2 | t/h
828 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF40CP101 | BJF40CP101 | 12HJF40CP101 | In-bed gun 2 inlet pressure | AI | 0 | 4 | MPa
829 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF40CF101 | BJF40CF101 | 12HJF40CF101 | In-bed gun 2 inlet flow | AI | 0 | 2 | t/h
830 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF50CP101 | BJF50CP101 | 12HJF50CP101 | In-bed gun 3 inlet pressure | AI | 0 | 4 | MPa
831 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF50CF101 | BJF50CF101 | 12HJF50CF101 | In-bed gun 3 inlet flow | AI | 0 | 2 | t/h
832 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF60CP101 | BJF60CP101 | 12HJF60CP101 | In-bed gun 4 inlet pressure | AI | 0 | 4 | MPa
833 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF60CF101 | BJF60CF101 | 12HJF60CF101 | In-bed gun 4 inlet flow | AI | 0 | 2 | t/h
834 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJS03CP101 | BJS03CP101 | 12HJS03CP101 | Pressurized air pressure | AI | 0 | 1.6 | MPa
835 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | AS10_E013.MV | AS10_E013.MV | 12HJF07AA101AO | Burn oil pressure control valve control | AO | 0 | 100 | %
836 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF07A101T | BJF07A101T | 12HJF07AA101GT | Burn oil pressure control valve position | AI | 0 | 100 | %
837 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | AS10_E025.MV | AS10_E025.MV | 12HJF35AA101AO | NO.1 IN-Duct bum oil flow control valve control | AO | 0 | 100 | %
838 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF35A101T | BJF35A101T | 12HJF35AA101GT | NO.1 IN-Duct burn oil flow control valve position | AI | 0 | 100 | %
839 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | AS10_E026.MV | AS10_E026.MV | 12HJF45AA101AO | NO.2 IN-Duct burn oil flow control valve control | AO | 0 | 100 | %
840 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF45A101T | BJF45A101T | 12HJF45AA101GT | NO.2 IN-Duct burn oil flow control valve position | AI | 0 | 100 | %
841 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | AS10_E027.MV | AS10_E027.MV | 12HJF55AA101AO | In-bed oil gun 1 oil flow control valve control | AO | 0 | 100 | %
842 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF55A101T | BJF55A101T | 12HJF55AA101GT | In-bed oil gun 1 oil flow control valve position | AI | 0 | 100 | %
843 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | AS10_E028.MV | AS10_E028.MV | 12HJF65AA101AO | In-bed oil gun 2 oil flow control valve control | AO | 0 | 100 | %
844 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJF65A101T | BJF65A101T | 12HJF65AA101GT | In-bed oil gun 2 oil flow control valve position | AI | 0 | 100 | %
845 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJY11F001 | BJY11F001 | 12HJY11FQ001 | NO.1 IN-Duct burn flame intensity | AI | 0 | 100 | %
846 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJY21F001 | BJY21F001 | 12HJY21FQ001 | NO.2 IN-Duct burn flame intensity | AI | 0 | 100 | %
847 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJY31F001 | BJY31F001 | 12HJY31FQ001 | NO.1 IN-Bed burn flame intensity | AI | 0 | 100 | %
848 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | FURNACE (BOILER IGNITION SYSTEM) #2 | WIKA-07NP08-ABD-101-20-027 | BJY41F001 | BJY41F001 | 12HJY41FQ001 | NO.2 IN-Bed burn flame intensity | AI | 0 | 100 | %
849 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2A | WIKA-07NP08-ABD-201-20-012 | AS10_E014.MV | AS10_E014.MV | 12HDY11FA101 | No.1 Ash cooler frequency control | AO | 0 | 100 | %
850 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2A | WIKA-07NP08-ABD-201-20-012 | BDY11FE001 | BDY11FE001 | 12HDY11FE001 | No.1 Ash cooler frequency | Al | 0 | 100 | %
851 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2A |  | BDY11FE002 | BDY11FE002 | 12HDY11FE002 | No.1 Ash cooler current | Al | 0 | 100 | A
852 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2B | WIKA-07NP08-ABD-201-20-012 | AS10_E015.MV | AS10_E015.MV | 12HDY21FA101 | No.2 Ash cooler frequency control | AO | 0 | 100 | %
853 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2B | WIKA-07NP08-ABD-201-20-012 | BDY21FE001 | BDY21FE001 | 12HDY21FE001 | No.2 Ash cooler frequency | Al | 0 | 100 | %
854 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2B |  | BDY21FE002 | BDY21FE002 | 12HDY21FE002 | No.2 Ash cooler current | Al | 0 | 100 | A
855 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2A | WIKA-07NP08-ABD-201-20-037 | LCA22G302 | LCA22G302 | 12LCA22CT302 | Temperature outlet cooling water No.1 Ash cooler | Al | 0 | 200 | °C
856 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 5 | ASH COOLER #2B | WIKA-07NP08-ABD-201-20-037 | LCA42G302 | LCA42G302 | 12LCA42CT302 | Temperature outlet cooling water No.2 Ash cooler | Al | 0 | 200 | °C
857 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT251 | BLB20CT251 | 12HLB20CT251 | S.A Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
858 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT252 | BLB20CT252 | 12HLB20CT252 | S.A Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
859 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT253 | BLB20CT253 | 12HLB20CT253 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
860 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT254 | BLB20CT254 | 12HLB20CT254 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
861 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT255 | BLB20CT255 | 12HLB20CT255 | S.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
862 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT261 | BLB20CT261 | 12HLB20CT261 | S.A Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
863 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CT262 | BLB20CT262 | 12HLB20CT262 | S.A Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
864 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLA82CT301 | BLA82CT301 | 12HLA82CT301 | S.A. Fan Outlet Temperature | AI | 0 | 200 | °C
865 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLA82CP101 | BLA82CP101 | 12HLA82CP101 | S.A. Fan Outlet Pressure | AI | 0 | 16 | KPa
866 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BL81A101MV | BL81A101MV | 12HLA81AA101AO | Second air fan inlet control damp control | AO | 0 | 100 | %
867 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLA81A101T | BLA81A101T | 12HLA81AA101GT | Second air fan inlet control damp position | AI | 0 | 100 | %
868 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BTH0782A_5 | BTH0782A_5 | 12HLB10VX010 | S.A. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
869 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BTH0782A_6 | BTH0782A_6 | 12HLB10VY010 | S.A. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
870 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN (SA FAN) #2 | WIKA-07NP08-ABD-101-20-028 | BLB20CE010 | BLB20CE010 | 12HLB20CE010 | Second air fan motor current | AI | 0 | 200 | A
871 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA83CT301 | BLA83CT301 | 12HLA83CT301 | Second air heater outlet temperature | AI | 0 | 450 | °C
872 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA83CP101 | BLA83CP101 | 12HLA83CP101 | Second air heater outlet pressure | AI | 0 | 16 | KPa
873 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA84CF1_1 | BLA84CF1_1 | 12HLA84CF101 | Lower CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
874 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA85CF1_1 | BLA85CF1_1 | 12HLA85CF101 | Upper CombUstion Chamber Air Flow | AI | 0 | 32000 | Nm3/h
875 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | AS10_E021.MV | AS10_E021.MV | 12HLA84AA101AO | Lower combstion chamber air flow control damp control | AO | 0 | 100 | %
876 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA84A101T | BLA84A101T | 12HLA84AA101GT | Lower combstion chamber air flow control damp position | AI | 0 | 100 | %
877 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | AS10_E022.MV | AS10_E022.MV | 12HLA85AA101AO | Upper combstion chamber airflow control damp control | AO | 0 | 100 | %
878 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 6 | SECONDARY AIR FAN HEATER #2 | WIKA-07NP08-ABD-101-20-028 | BLA85A101T | BLA85A101T | 12HLA85AA101GT | Upper combstion chamber airflow control damp position | AI | 0 | 100 | %
879 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT251 | BLB10CT251 | 12HLB10CT251 | P.A Fan Motor Front Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 85 | 95
880 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT252 | BLB10CT252 | 12HLB10CT252 | P.A Fan Motor Rear Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 85 | 95
881 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT253 | BLB10CT253 | 12HLB10CT253 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
882 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT254 | BLB10CT254 | 12HLB10CT254 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
883 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT255 | BLB10CT255 | 12HLB10CT255 | P.A Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
884 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT261 | BLB10CT261 | 12HLB10CT261 | P.A Fan Front Bearing Temperature | AI | 0 | 200 | °C |  |  |  | 75 | 85
885 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CT262 | BLB10CT262 | 12HLB10CT262 | P.A Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
886 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLA12CT301 | BLA12CT301 | 12HLA12CT301 | P.A. Fan Outlet Air Temperature | AI | 0 | 150 | °C
887 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLA12CP101 | BLA12CP101 | 12HLA12CP101 | P.A. Fan Outlet Air Pressure | AI | 0 | 25 | KPa
888 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLA15CF1_1 | BLA15CF1_1 | 12HLA15CF101 | Sponge Coal Feeder Air Flow | AI | 0 | 5500 | Nm3/h
889 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB10CE010 | BLB10CE010 | 12HLB10CE010 | Primary air fan motor current | AI | 0 | 200 | A
890 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BTH0782A_3 | BTH0782A_3 | 12HLB20VX010 | P.A. Fan FV X | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
891 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. FAN #2 | WIKA-07NP08-ABD-101-20-039 | BTH0782A_4 | BTH0782A_4 | 12HLB20VY010 | P.A. Fan FV Y | AI | 0 | 50 | mm/s |  |  |  | 4.6 | 5
892 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT251 | BLB30CT251 | 12HLB30CT251 | P.A Booster Booster Fan Motor Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
893 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT252 | BLB30CT252 | 12HLB30CT252 | P.A Booster Booster Fan Motor Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 85 | 95
894 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT253 | BLB30CT253 | 12HLB30CT253 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
895 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT254 | BLB30CT254 | 12HLB30CT254 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
896 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT255 | BLB30CT255 | 12HLB30CT255 | P.A Booster Booster Fan Motor Stator Winding Temperature | AI | 0 | 200 | °C |  |  |  | 135 | 145
897 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT261 | BLB30CT261 | 12HLB30CT261 | P.A Booster Booster Fan Front Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
898 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CT262 | BLB30CT262 | 12HLB30CT262 | P.A Booster Booster Fan Rear Bearing Temperature | AI | 0 | 150 | °C |  |  |  | 75 | 85
899 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BL13A101MV | BL13A101MV | 12HLA13AA101AO | PA booster fan inlet control damp control | AO | 0 | 100 | %
900 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLA13A101T | BLA13A101T | 12HLA13AA101GT | PA booster fan inlet control damp position | AI | 0 | 100 | %
901 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. BOOSTER FAN #2 | WIKA-07NP08-ABD-101-20-039 | BLB30CE010 | BLB30CE010 | 12HLB30CE010 | P.A. booster fan motor current | AI | 0 | 200 | A
902 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA30CT301 | BLA30CT301 | 12HLA30CT301 | Primary air heater outlet temperature | AI | 0 | 450 | °C
903 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA30CP101 | BLA30CP101 | 12HLA30CP101 | Primary air heater outlet pressure | AI | 0 | 25 | KPa
904 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA31CF1_1 | BLA31CF1_1 | 12HLA31CF101 | Duct Ignition Burner 1 Air Flow | AI | 0 | 40000 | Nm3/h
905 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA32CF1_1 | BLA32CF1_1 | 12HLA32CF101 | Duct Ignition Burner 2 Air Flow | AI | 0 | 40000 | Nm3/h
906 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA41CF1_1 | BLA41CF1_1 | 12HLA41CF101 | Oil Gun 2 Above Grid Plate Air Flow | AI | 0 | 11000 | Nm3/h
907 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA42CF1_1 | BLA42CF1_1 | 12HLA42CF101 | Oil Gun 1 Above Grid Plate Air Flow | AI | 0 | 11000 | Nm3/h
908 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLAA101AMV | BLAA101AMV | 12HLA11AA101AO | Primary air fan inlet control damp control | AO | 0 | 100 | %
909 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLAAA101T | BLAAA101T | 12HLA11AA101GT | Primary air fan inlet control damp control | AI | 0 | 100 | %
910 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | AS10_E016.MV | AS10_E016.MV | 12HLA31AA101AO | No.1 duct burn inlet control damp controj | AO | 0 | 100 | %
911 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA31A101T | BLA31A101T | 12HLA31AA101GT | No.1 duct burn inlet control damp position | AI | 0 | 100 | %
912 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | AS10_E017.MV | AS10_E017.MV | 12HLA32AA101AO | No.2 duct burn inlet control damp control | AO | 0 | 100 | %
913 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA32A101T | BLA32A101T | 12HLA32AA101GT | No.2 duct burn inlet control damp position | AI | 0 | 100 | %
914 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | AS10_E018.MV | AS10_E018.MV | 12HLA41AA101AO | No.1 bed burn inlet control damp control | AO | 0 | 100 | %
915 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA41A101T | BLA41A101T | 12HLA41AA101GT | No.1 bed burn inlet control damp position | AI | 0 | 100 | %
916 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | AS10_E019.MV | AS10_E019.MV | 12HLA42AA101AO | No.2 bed burn inlet control damp control | AO | 0 | 100 | %
917 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 7 | P.A. HEATER #2 | WIKA-07NP08-ABD-101-20-039 | BLA42A101T | BLA42A101T | 12HLA42AA101GT | No.2 bed burn inlet control damp position | AI | 0 | 100 | %
918 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 8 | SPONGE COAL SILO / COAL BUNKER #2 | WIKA-07NP08-ABD-101-20-033 | BFB10CL101 | BFB10CL101 | 12HFB10CL101 | Sponge Coal Silo Level | AI | 0 | 14.5 | m
919 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2 | WIKA-07NP08-ABD-101-20-033 | BLA50CT301 | BLA50CT301 | 12HLA50CT301 | Feeder Air Temperature | AI | 0 | 100 | °C
920 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2 | WIKA-07NP08-ABD 101-20-033 | BLA50CP101 | BLA50CP101 | 12HLA50CP101 | Feeder Air Pressure | AI | 0 | 40 | KPa
921 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2 | WIKA-07NP08-ABD-101-20-033 | BLA50CF1_1 | BLA50CF1_1 | 12HLA50CF101 | Feeder Air Flow | AI | 0 | 9000 | NmJ/h
922 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2A | WIKA-07NP08-ABD-101-20-033 | BFY10FT001 | BFY10FT001 | 12HFY10FT001 | NO.1 gravimetric belt feeder temperature | AI | 0 | 200 | °C
923 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2A | WIKA-07NP08-ABD-101-20-033 | BFY10FS101 | BFY10FS101 | 12HFY10FS101 | NO.1 gravimetric belt feeder speed | AI | 0 | 100 | RPM
924 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2A | WIKA-07NP08-ABD-101-20-033 | BFY10FA101 | BFY10FA101 | 12HFY10FA101 | NO.1 gravimetric belt feeder speed control | AO | 0 | 100 | %
925 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2A | WIKA-07NP08-ABD-101-20-033 | BFY10FF001 | BFY10FF001 | 12HFY10FF001 | NO.1 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
926 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2B | WIKA-07NP08-ABD-101-20-033 | BFY20FT001 | BFY20FT001 | 12HFY20FT001 | NO.2 gravimetric belt feeder temperature | AI | 0 | 200 | °C
927 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2B | WIKA-07NP08-ABD-101-20-033 | BFY20FS101 | BFY20FS101 | 12HFY20FS101 | NO.2 gravimetric belt feeder speed | AI | 0 | 100 | RPM
928 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2B | WIKA-07NP08-ABD-101-20-033 | BFY20FA101 | BFY20FA101 | 12HFY20FA101 | NO.2 gravimetric belt feeder speed control | AO | 0 | 100 | %
929 | 2 | UJLJ AMG #2 | 5 | BOILER AFG | 9 | GRAFIMETRIC BELT /COAL FEEDER #2B | WIKA-07NP08-ABD-101-20-033 | BFY20FF001 | BFY20FF001 | 12HFY20FF001 | NO.2 gravimetric belt feeder coal weight measurement | AI | 0 | 26 | t/h
930 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-027 | BOG10CL151 | BOG10CL151 | 12MAG10CL151 | Condenser hot well level | AI | 0 | 1100 | mm |  | 0 | 300 | 1000 | 1000
931 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-027 | BCA20A102T | BCA20A102T | 12LCA20AA102GT | Hot well level control valve position | AI | 0 | 100 | %
932 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-027 | S18_E004.MV | S18_E004.MV | 12LCA20AA102AO | Hot well level control valve control | AO | 0 | 100 | %
933 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-027 | B_A20CF101 | B_A20CF101 | 12LCA20CF101 | Condenser makeup water flow | AI | 0 | 4 | t/h
934 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-027 | BCA20CL151 | BCA20CL151 | 12LCA20CL151 | Condensate storge tank level | AI | 0 | 1800 | mm |  | 250 | 250 | 1700 | 1700
935 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | BBF10CT601 | BBF10CT601 | 12LBF10CT601 | HP bypass valve outlet temperature | AI | 0 | 600 | °C
936 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | BBF10CT602 | BBF10CT602 | 12LBF10CT602 | HP bypass valve outlet temperature | AI | 0 | 600 | °C
937 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | BBF10CP101 | BBF10CP101 | 12LBF10CP101 | HP bypass valve outlet pressure | AI | -0.1 | 1 | MPa
938 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | BBF10A001T | BBF10A001T | 12LBF10AA001GT | Turbine bypass pressure control valve position | AI | 0 | 100 | %
939 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | BBF10A003T | BBF10A003T | 12LBF10AA003GT | Turbine bypass 1 stage spray water control valve position | AI | 0 | 100 | %
940 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | S20_E000.MV | S20_E000.MV | 12LBF10AA001AO | Turbine bypass pressure control valve control | AO | 0 | 100 | %
941 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 | WIKA-07NP08-ABD-201-20-007 | S20_E001.MV | S20_E001.MV | 12LBF10AA003AO | Turbine bypass 1 stage spray water control valve control | AO | 0 | 100 | %
942 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CT301 | BAB10CT301 | 12PAB10CT301 | Condenser left inlet cooling water temperature | AI | 0 | 100 | °C
943 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CT302 | BAB10CT302 | 12PAB10CT302 | Condenser left outlet cooling water temperature | AI | 0 | 100 | °C
944 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CT311 | BAB10CT311 | 12PAB10CT311 | Condenser right inlet cooling water temperature | AI | 0 | 100 | °C
945 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CT312 | BAB10CT312 | 12PAB10CT312 | Condenser right outlet cooling water temperature | AI | 0 | 100 | °C
946 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CP101 | BAB10CP101 | 12PAB10CP101 | Condenser left inlet cooling water pressure | AI | 0.1 | 0.5 | MPa
947 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CP102 | BAB10CP102 | 12PAB10CP102 | Condenser left outlet cooling water pressure | AI | 0.1 | 0.5 | MPa
948 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CP111 | BAB10CP111 | 12PAB10CP111 | Condenser right inlet cooling water pressure | AI | 0.1 | 0.5 | MPa
949 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (OCCW) | WIKA-07NP08-ABD-201-20-029 | BAB10CP112 | BAB10CP112 | 12PAB10CP112 | Condenser right outlet cooling water pressure | AI | 0.1 | 0.5 | MPa
950 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (VACUUM EJECTOR) | WIKA-07NP08-ABD-201-20-020 | BOG10CP103 | BOG10CP103 | 12MAG10CP103 | Condenser pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
951 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 1 | CONDENSER #2 (VACUUM EJECTOR) | WIKA-07NP08-ABD-201-20-020 | BOJ10CP101 | BOJ10CP101 | 12MAJ10CP101 | Vaccuum pump group inlet pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
952 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CT301 | BCA10CT301 | 12LCA10CT301 | Condensate water temperature | AI | 0 | 150 | °C
953 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CT302 | BCA10CT302 | 12LCA10CT302 | Condensate pump outlet header temperature | AI | 0 | 200 | °C
954 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CP101 | BCA10CP101 | 12LCA10CP101 | Condensate pump outlet header pressure | AI | 0 | 2 | MPa
955 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CP102 | BCA10CP102 | 12LCA10CP102 | Condensate pump outlet header pressure | AI | 0 | 2 | MPa
956 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2A | WIKA-07NP08-ABD-201-20-018 | BAC10CE001 | BAC10CE001 | 12LCB10CE001 | NO.1 condensate pump motor current | AI | 0 | 200 | A
957 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CP111 | BCA10CP111 | 12LCA10CP111 | HP heater by-pass valve control water pressure | AI | 0 | 2 | MPa
958 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2B | WIKA-07NP08-ABD-201-20-018 | BAC20CE001 | BAC20CE001 | 12LCB20CE001 | NO.2 condensate pump motor current | AI | 0 | 200 | A
959 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 2 | CONDENSATE PUMP #2 | WIKA-07NP08-ABD-201-20-018 | BCA10 CP111 | BCA10 CP111 | 12LCA10 CP111 | HP heater by-pass valve control water pressure | AI | 0 | 2 | MPa
960 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #2 | WIKA-07NP08-ABD-201-20-018 | BCA10A101T | BCA10A101T | 12LCA10AA101GT | Condensate recycling control valve position | AI | 0 | 100 | %
961 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #2 | WIKA-07NP08-ABD-201-20-018 | S18_E003.MV | S18_E003.MV | 12LCA10AA101AO | Condensate recycling control valve control | AO | 0 | 100 | %
962 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #2 | WIKA-07NP08-ABD-201-20-018 | BCA10CT303 | BCA10CT303 | 12LCA10CT303 | Gland cooler outlet condensate temperature | AI | 0 | 200 | °C
963 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 3 | GLAND STEAM COOLER #2 | WIKA-07NP08-ABD-201-20-018 | B_A10CF101 | B_A10CF101 | 12LCA10CF101 | Condensate Flow | AI | 0 | 130 | t/h
964 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 4 | LP HEATER #2C | WIKA-07NP08-ABD-201-20-018 | BCA10CT304 | BCA10CT304 | 12LCA10CT304 | NO.3 LP heater outlet condensate temperature | AI | 0 | 150 | °C
965 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 4 | LP HEATER #2C | WIKA-07NP08-ABD-201-20-018 | BCA10CP103 | BCA10CP103 | 12LCA10CP103 | LP heater inlet pressure | AI | 0 | 2 | MPa
966 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 4 | LP HEATER #2C | WIKA-07NP08-ABD-201-20-014 | BBS30CP101 | BBS30CP101 | 12LBS30CP101 | NO.3 LP heater inlet steam pressure | AI | -0.1 | 0.15 | MPa
967 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 4 | LP HEATER #2C | WIKA-07NP08-ABD-201-20-019 | BCC30CL151 | BCC30CL151 | 12LCC30CL151 | NO.3 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
968 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 5 | LP HEATER #2B | WIKA-07NP08-ABD-201-20-018 | BCA10CT305 | BCA10CT305 | 12LCA10CT305 | NO.2 LP heater outlet condensate temperature | AI | 0 | 150 | °C
969 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 5 | LP HEATER #2B | WIKA-07NP08-ABD-201-20-013 | BBS20CP101 | BBS20CP101 | 12LBS20CP101 | NO.2 LP heater inlet steam pressure | AI | 0 | 0.25 | MPa
970 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 5 | LP HEATER #2B | WIKA-07NP08-ABD-201-20-019 | BCC20CL151 | BCC20CL151 | 12LCC20CL151 | NO.2 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
971 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 6 | LP HEATER #2A | WIKA-07NP08-ABD-201-20-018 | BCA10CT306 | BCA10CT306 | 12LCA10CT306 | NO.1 LP heater outlet condensate temperature | AI | 0 | 200 | °C
972 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 6 | LP HEATER #2A | WIKA-07NP08-ABD-201-20-012 | BBS10CP101 | BBS10CP101 | 12LBS10CP101 | NO.1 LP heater inlet steam pressure | AI | 0 | 0.6 | MPa
973 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 6 | LP HEATER #2A | WIKA-07NP08-ABD-201-20-019 | BCC10CL151 | BCC10CL151 | 12LCC10CL151 | NO.1 LP heater level | AI | 0 | 700 | mm |  |  | 300 | 600
974 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-018 | BA10CT651 | BA10CT651 | 12LAA10CT651 | Dearator tank temperature | AI | 0 | 500 | °C
975 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-018 | BA10CL101 | BA10CL101 | 12LAA10CL101 | Dearator tank level | AI | 0 | 1800 | mm |  |  | 1240 | 1655 | 1740
976 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-018 | BA10CL102 | BA10CL102 | 12LAA10CL102 | Dearator tank level | AI | 0 | 1800 | mm |  |  | 1200 | 1650 | 1740
977 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-018 | BCA10A102T | BCA10A102T | 12LCA10AA102GT | Deaerator tank level control valve position | AI | 0 | 100 | %
978 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-018 | S18_E002.MV | S18_E002.MV | 12LCA10AA102AO | Deaerator tank level control valve control | AO | 0 | 100 | %
979 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | BA10CP101 | BA10CP101 | 12LAA10CP101 | Deaerator pressure | AI | 0 | 1 | MPa
980 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | BA10CP102 | BA10CP102 | 12LAA10CP102 | Deaerator pressure | AI | 0 | 1 | MPa
981 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | BBS40CT601 | BBS40CT601 | 12LBS40CT601 | Deaerator pressure control valve inlet temperature | AI | 0 | 600 | °C
982 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | BBS40CP101 | BBS40CP101 | 12LBS40CP101 | Deaerator pressure control valve inlet pressure | AI | 0 | 1 | MPa
983 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | BBS40A101T | BBS40A101T | 12LBS40AA101GT | Deaerator pressure control valve position | AI | 0 | 100 | %
984 | 2 | UJLJ AMG #2 | 6 | CDS SYSTEM | 7 | DEAERATOR #2 | WIKA-07NP08-ABD-201-20-011 | S18_E005.MV | S18_E005.MV | 12LBS40AA101AO | Deaerator pressure control valve control | AO | 0 | 100 | %
985 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT251 | BAC10CT251 | 12LAC10CT251 | NO.1 Feedwater pump motor front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
986 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT252 | BAC10CT252 | 12LAC10CT252 | NO.1 Feedwater pump motor rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
987 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT253 | BAC10CT253 | 12LAC10CT253 | NO.1 Feedwater pump hydraulic coupler front bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
988 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT254 | BAC10CT254 | 12LAC10CT254 | NO.1 Feedwater pump hydraulic coupler rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
989 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT255 | BAC10CT255 | 12LAC10CT255 | NO.1 Feedwater pump front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
990 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT256 | BAC10CT256 | 12LAC10CT256 | NO.1 Feedwater pump rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
991 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT257 | BAC10CT257 | 12LAC10CT257 | NO.1 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
992 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT258 | BAC10CT258 | 12LAC10CT258 | NO.1 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
993 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT261 | BAC10CT261 | 12LAC10CT261 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
994 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT262 | BAC10CT262 | 12LAC10CT262 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
995 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT263 | BAC10CT263 | 12LAC10CT263 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
996 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT264 | BAC10CT264 | 12LAC10CT264 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
997 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT265 | BAC10CT265 | 12LAC10CT265 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
998 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT266 | BAC10CT266 | 12LAC10CT266 | NO.1 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
999 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT351 | BAC10CT351 | 12LAC10CT351 | NO.1 Feedwater pump hydraulic coupler outlet oil temperature | AI | 0 | 150 | °C |  |  |  | 88
1000 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CT352 | BAC10CT352 | 12LAC10CT352 | NO.1 Feedwater pump hydraulic coupler inlet oil temperature | AI | 0 | 150 | °C |  |  |  | 65
1001 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CP151 | BAC10CP151 | 12LAC10CP151 | NO.1 Feedwater pump hydraulic coupler outlet oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.2
1002 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CP152 | BAC10CP152 | 12LAC10CP152 | NO.1 Feedwater pump lube oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.8
1003 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10CS101 | BAC10CS101 | 12LAC10CS101 | NO.1 Feedwater pump speed | AI | 0 | 3000 | rpm
1004 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BAC10A051T | BAC10A051T | 12LAC10AA051GT | No.1 feedwater pump hydraulic coupler actuator position | AI | 0 | 100 | %
1005 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BQC10CE001 | BQC10CE001 | 12LAC10CE001 | NO.1 feedwater pump motor current | AI | 0 | 400 | A
1006 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-008 | BC10A051MV | BC10A051MV | 12LAC10AA051AO | No.1 feedwater pump hydraulic coupler actuator control | AO | 0 | 100 | %
1007 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2A | WIKA-07NP08-ABD-201-20-006 | BQB10CP111 | BQB10CP111 | 12LAB10CP111 | NO.1 Feedwater pump outlet pressure | AI | 0 | 20 | MPa
1008 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT251 | BAC20CT251 | 12LAC20CT251 | NO.2 Feedwater pump motor front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
1009 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT252 | BAC20CT252 | 12LAC20CT252 | NO.2 Feedwater pump motor rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
1010 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT253 | BAC20CT253 | 12LAC20CT253 | NO.2 Feedwater pump hydraulic coupler front bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
1011 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT254 | BAC20CT254 | 12LAC20CT254 | NO.2 Feedwater pump hydraulic coupler rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 95
1012 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT255 | BAC20CT255 | 12LAC20CT255 | NO.2 Feedwater pump front bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
1013 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT256 | BAC20CT256 | 12LAC20CT256 | NO.2 Feedwater pump rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 70
1014 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT257 | BAC20CT257 | 12LAC20CT257 | NO.2 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
1015 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT258 | BAC20CT258 | 12LAC20CT258 | NO.2 Feedwater pump thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 75
1016 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT261 | BAC20CT261 | 12LAC20CT261 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1017 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT262 | BAC20CT262 | 12LAC20CT262 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1018 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT263 | BAC20CT263 | 12LAC20CT263 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1019 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT264 | BAC20CT264 | 12LAC20CT264 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1020 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT265 | BAC20CT265 | 12LAC20CT265 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1021 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT266 | BAC20CT266 | 12LAC20CT266 | NO.2 Feedwater pump motor stator winding temperature | AI | 0 | 200 | °C |  |  |  | 135
1022 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT351 | BAC20CT351 | 12LAC20CT351 | NO.2 Feedwater pump hydraulic coupler outlet oil temperature | AI | 0 | 150 | °C |  |  |  | 88
1023 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CT352 | BAC20CT352 | 12LAC20CT352 | NO.2 Feedwater pump hydraulic coupler inlet oil temperature | AI | 0 | 150 | °C |  |  |  | 65
1024 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CP151 | BAC20CP151 | 12LAC20CP151 | NO.2 Feedwater pump hydraulic coupler outlet oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.2
1025 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CP152 | BAC20CP152 | 12LAC20CP152 | NO.2 Feedwater pump lube oil pressure | AI | 0 | 0.4 | MPa |  | 0.1 | 0.8
1026 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20CS101 | BAC20CS101 | 12LAC20CS101 | NO.2 Feedwater pump speed | AI | 0 | 3000 | rpm
1027 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BAC20A051T | BAC20A051T | 12LAC20AA051GT | No.2 feedwater pump hydraulic coupler actuator position | AI | 0 | 100 | %
1028 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BQC20CE001 | BQC20CE001 | 12LAC20CE001 | NO.2 feedwater pump motor current | AI | 0 | 400 | A
1029 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-008 | BC20A051MV | BC20A051MV | 12LAC20AA051AO | No.2 feedwater pump hydraulic coupler actuator control | AO | 0 | 100 | %
1030 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 2 | BOILER HP FW PUMP #2B | WIKA-07NP08-ABD-201-20-006 | BQB10CP112 | BQB10CP112 | 12LAB10CP112 | NO.2 Feedwater pump outlet pressure | AI | 0 | 20 | MPa
1031 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 3 | HPH FEEDWATER #2B | WIKA-07NP08-ABD-201-20-006 | BAB10CT611 | BAB10CT611 | 12LAB10CT611 | Feedwater pump header temperature | AI | 0 | 300 | °C
1032 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 3 | HPH FEEDWATER #2B | WIKA-07NP08-ABD-201-20-006 | BAB10CT612 | BAB10CT612 | 12LAB10CT612 | NO.2 High pressure heater outlet water temperature | AI | 0 | 300 | °C
1033 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 3 | HPH FEEDWATER #2B | WIKA-07NP08-ABD-201-20-010 | BBQ20CP101 | BBQ20CP101 | 12LBQ20CP101 | NO.2 HP heater inlet steam pressure | AI | 0 | 2.5 | MPa
1034 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 3 | HPH FEEDWATER #2B | WIKA-07NP08-ABD-201-20-005 | Bad20CL101 | Bad20CL101 | 12LAD20CL101 | NO.2 HP heater level | AI | 0 | 800 | mm |  | 150 | 200 | 650
1035 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 3 | HPH FEEDWATER #2B | WIKA-07NP08-ABD-201-20-017 | BCH10CT302 | BCH10CT302 | 12LCH10CT302 | NO.2 HP heater drain temperature | AI | 0 | 300 | °C
1036 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 4 | HPH FEEDWATER #2A | WIKA-07NP08-ABD-201-20-006 | BAB10CT613 | BAB10CT613 | 12LAB10CT613 | NO.1 High pressure heater outlet water temperature | AI | 0 | 300 | °C
1037 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 4 | HPH FEEDWATER #2A | WIKA-07NP08-ABD-201-20-009 | BBQ10CP101 | BBQ10CP101 | 12LBQ10CP101 | NO.1 HP heater inlet steam pressure | AI | 0 | 4 | MPa
1038 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 4 | HPH FEEDWATER #2A | WIKA-07NP08-ABD-201-20-005 | Bad10CL101 | Bad10CL101 | 12LAD10CL101 | NO.1 HP heater level | AI | 0 | 800 | mm |  | 150 | 200 | 650
1039 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 4 | HPH FEEDWATER #2A | WIKA-07NP08-ABD-201-20-017 | BCH10CT301 | BCH10CT301 | 12LCH10CT301 | NO.1 HP heater drain temperature | AI | 0 | 500 | °C
1040 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-201-20-006 | BAB10T622 | BAB10T622 | 12LAB10CT622 | Economizer inlet water temperature | AI | 0 | 600 | °C
1041 | 2 | UJLJ AMG #2 | 7 | FEED WATER | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-201-20-006 | BAB10CP122 | BAB10CP122 | 12LAB10CP122 | Economizer inlet water pressure | AI | 0 | 20 | MPa
1042 | 2 | UJLJ AMG #2 | 7 | BOILER AFG | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT605 | BNA20CT605 | 12HNA20CT605 | Economizer outlet temperature(left) | AI | 0 | 600 | °C
1043 | 2 | UJLJ AMG #2 | 7 | BOILER AFG | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CT606 | BNA20CT606 | 12HNA20CT606 | Economizer outlet temperature(right) | AI | 0 | 600 | °C
1044 | 2 | UJLJ AMG #2 | 7 | BOILER AFG | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP107 | BNA20CP107 | 12HNA20CP107 | Economizer outlet pressure(left) | AI | -5 | 1 | KPa
1045 | 2 | UJLJ AMG #2 | 7 | BOILER AFG | 5 | ECONOMIZER #2 | WIKA-07NP08-ABD-101-20-012 | BNA20CP108 | BNA20CP108 | 12HNA20CP108 | Economizer outlet pressure(right) | AI | -5 | 1 | KPa
1046 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10T621 | BAB10T621 | 12LAB10CT621 | Main feedwater temperature | AI | 0 | 600 | °C
1047 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10CP121 | BAB10CP121 | 12LAB10CP121 | Main feedwater pressure | AI | 0 | 20 | MPa
1048 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10CF1_1 | BAB10CF1_1 | 12LAB10CF121 | Main feedwater flow | AI | 0 | 150 | t/h
1049 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | B_B10CF131 | B_B10CF131 | 12LAB10CF131 | First stage desuperheater spray water flow | AI | 0 | 8 | t/h
1050 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | B_B10CF141 | B_B10CF141 | 12LAB10CF141 | Second stage desuperheater spray water flow | AI | 0 | 8 | t/h
1051 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BB10A141MV | BB10A141MV | 12LAB10AA141AO | Feedwater main control valve control | AO | 0 | 100 | %
1052 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10A141T | BAB10A141T | 12LAB10AA141GT | Feedwater main control valve position | AI | 0 | 100 | %
1053 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | AS10_E003.MV | AS10_E003.MV | 12LAB10AA131AO | Feedwater vice control valve control | AO | 0 | 100 | %
1054 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10A131T | BAB10A131T | 12LAB10AA131GT | Feedwater vice control valve position | AI | 0 | 100 | %
1055 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | AS10_E004.MV | AS10_E004.MV | 12LAB10AA111AO | First stage attemperator left spray water control valve control | AO | 0 | 100 | %
1056 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10A111T | BAB10A111T | 12LAB10AA111GT | First stage attemperator left spray water control valve position | AI | 0 | 100 | %
1057 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | AS10_E032.MV | AS10_E032.MV | 12LAB10AA121AO | Second stage attemperator left spray water control valve control | AO | 0 | 100 | %
1058 | 2 | UJLJ AMG #2 | 7 | FEED WATER #2 | 5 | FEEDWATER PIPING #2 | WIKA-07NP08-ABD-201-20-006 | BAB10A121T | BAB10A121T | 12LAB10AA121GT | Second stage attemperator left spray water control valve position | AI | 0 | 100 | %
1059 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | Bad10CT201 | Bad10CT201 | 12HAD10 CT201 | Drum Upper Metal Temperature 1 | AI | 0 | 600 | °C
1060 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | Bad10CT202 | Bad10CT202 | 12HAD10 CT202 | Drum Upper Metal Temperature 2 | AI | 0 | 600 | °C
1061 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | Bad10CT203 | Bad10CT203 | 12HAD10 CT203 | Drum Lower Metal Temperature 1 | AI | 0 | 600 | °C
1062 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | Bad10CT204 | Bad10CT204 | 12HAD10 CT204 | Drum Lower Metal Temperature 2 | AI | 0 | 600 | °C
1063 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | BOd10CP101 | BOd10CP101 | 12HAD10 CP101 | Drum Pressure | AI | 0 | 16 | MPa
1064 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | BOd10CP102 | BOd10CP102 | 12HAD10 CP102 | Drum Pressure | AI | 0 | 16 | MPa
1065 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | BAD10CL1_1 | BAD10CL1_1 | 12HAD10 CL101 | Drum Level | AI | -533 | 533 | mm |  | -280 | -200 | 125 | 200
1066 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | BAD10CL1_2 | BAD10CL1_2 | 12HAD10 CL102 | Drum Level | AI | -533 | 533 | mm |  | -280 | -200 | 125 | 200
1067 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | STEAM DRUM #2 | WIKA-07NP08-ABD-101-20-35-01 | B_DRUM_LV | B_DRUM_LV |  | Drum Level Rate | AI | -533 | 533 | mm
1068 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #2 | WIKA-07NP08-ABD-101-20-35-01 | BCQ10CL151 | BCQ10CL151 | 12LCQ10CL151 | Continuous blowdown tank level | AI | 0 | 500 | mm |  |  | 100 | 450
1069 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #2 | WIKA-07NP08-ABD-101-20-35-01 | AS10_E020.MV | AS10_E020.MV | 12LCQ10AA101AO | Continuous blowdown control valve control | AO | 0 | 100 | %
1070 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 1 | CONTINOUS BLOWDOWN TANK #2 | WIKA-07NP08-ABD-101-20-35-01 | BCQ10A101T | BCQ10A101T | 12LCQ10AA101GT | Continuous blowdown control valve position | AI | 0 | 100 | %
1071 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT201 | BAH10CT201 | 12HAH10CT201 | Primary superheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 480
1072 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT202 | BAH10CT202 | 12HAH10CT202 | Primary superheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 480
1073 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT203 | BAH10CT203 | 12HAH10CT203 | Primary superheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 480
1074 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT204 | BAH10CT204 | 12HAH10CT204 | Primary superheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 480
1075 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT205 | BAH10CT205 | 12HAH10CT205 | Primary superheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 480
1076 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT206 | BAH10CT206 | 12HAH10CT206 | Primary superheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 480
1077 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #2 | WIKA-07NP08-ABD-101-20-35 | BAH10CT601 | BAH10CT601 | 12HAH10CT601 | Upper separator header outlet tube steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
1078 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #2 | WIKA-07NP08-ABD-101-20-35 | BAH10CT602 | BAH10CT602 | 12HAH10CT602 | Upper separator header outlet tube steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
1079 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #2 | WIKA-07NP08-ABD-101-20-35 | BAH10CT603 | BAH10CT603 | 12HAH10CT603 | Upper separator header outlet tube steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
1080 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 4 | PRIMARY SUPERHEATER (UPPER SEPARATOR HEADER) #2 | WIKA-07NP08-ABD-101-20-35 | BAH10CT604 | BAH10CT604 | 12HAH10CT604 | Upper separator header outlet tube steam temperature 4 | AI | 0 | 600 | °C |  |  |  | 455
1081 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT211 | BAH10CT211 | 12HAH10CT211 | Platen superheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 500
1082 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT212 | BAH10CT212 | 12HAH10CT212 | Platen superheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 500
1083 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT213 | BAH10CT213 | 12HAH10CT213 | Platen superheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 500
1084 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT214 | BAH10CT214 | 12HAH10CT214 | Platen superheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 500
1085 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT215 | BAH10CT215 | 12HAH10CT215 | Platen superheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 500
1086 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT216 | BAH10CT216 | 12HAH10CT216 | Platen superheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 500
1087 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT217 | BAH10CT217 | 12HAH10CT217 | Platen superheater outlet tube metal temperature 7 | AI | 0 | 600 | °C |  |  |  | 500
1088 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT218 | BAH10CT218 | 12HAH10CT218 | Platen superheater outlet tube metal temperature 8 | AI | 0 | 600 | °C |  |  |  | 500
1089 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT611 | BAH10CT611 | 12HAH10CT611 | First stage desuperheater inlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
1090 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT612 | BAH10CT612 | 12HAH10CT612 | First stage desuperheater inlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
1091 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT613 | BAH10CT613 | 12HAH10CT613 | First stage desuperheater inlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
1092 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT614 | BAH10CT614 | 12HAH10CT614 | First stage desuperheater outlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
1093 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT615 | BAH10CT615 | 12HAH10CT615 | First stage desuperheater outlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
1094 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT616 | BAH10CT616 | 12HAH10CT616 | First stage desuperheater outlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
1095 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T621 | BAH10T621 | 12HAH10CT621 | Second stage desuperheater inlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
1096 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T622 | BAH10T622 | 12HAH10CT622 | Second stage desuperheater inlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
1097 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T623 | BAH10T623 | 12HAH10CT623 | Second stage desuperheater inlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
1098 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T624 | BAH10T624 | 12HAH10CT624 | Second stage desuperheater outlet steam temperature 1 | AI | 0 | 600 | °C |  |  |  | 455
1099 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T625 | BAH10T625 | 12HAH10CT625 | Second stage desuperheater outlet steam temperature 2 | AI | 0 | 600 | °C |  |  |  | 455
1100 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 5 | PLATEN SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T626 | BAH10T626 | 12HAH10CT626 | Second stage desuperheater outlet steam temperature 3 | AI | 0 | 600 | °C |  |  |  | 455
1101 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT231 | BAH10CT231 | 12HAH10CT231 | Finishing supperheater outlet tube metal temperature 1 | AI | 0 | 600 | °C |  |  |  | 565
1102 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT232 | BAH10CT232 | 12HAH10CT232 | Finishing supperheater outlet tube metal temperature 2 | AI | 0 | 600 | °C |  |  |  | 565
1103 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT233 | BAH10CT233 | 12HAH10CT233 | Finishing supperheater outlet tube metal temperature 3 | AI | 0 | 600 | °C |  |  |  | 565
1104 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT234 | BAH10CT234 | 12HAH10CT234 | Finishing supperheater outlet tube metal temperature 4 | AI | 0 | 600 | °C |  |  |  | 565
1105 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT235 | BAH10CT235 | 12HAH10CT235 | Finishing supperheater outlet tube metal temperature 5 | AI | 0 | 600 | °C |  |  |  | 565
1106 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT236 | BAH10CT236 | 12HAH10CT236 | Finishing supperheater outlet tube metal temperature 6 | AI | 0 | 600 | °C |  |  |  | 565
1107 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT237 | BAH10CT237 | 12HAH10CT237 | Finishing supperheater outlet tube metal temperature 7 | AI | 0 | 600 | °C |  |  |  | 565
1108 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT238 | BAH10CT238 | 12HAH10CT238 | Finishing supperheater outlet tube metal temperature 8 | AI | 0 | 600 | °C |  |  |  | 565
1109 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CT239 | BAH10CT239 | 12HAH10CT239 | Finishing supperheater outlet tube metal temperature 9 | AI | 0 | 600 | °C |  |  |  | 565
1110 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10T631 | BAH10T631 | 12HAH10CT631 | Finishing supperheater outlet temperature | AI | 0 | 600 | °C |  |  | 520 | 545 | 600
1111 | 2 | UJLJ AMG #2 | 8 | BOILER STEAM | 6 | FINISHING SUPERHEATER #2 | WIKA-07NP08-ABD-101-20-35-01 | BAH10CP101 | BAH10CP101 | 12HAH10CP101 | Finishing supperheater outlet pressure | AI | 0 | 16 | MPa |  |  | 8 | 9.5
1112 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CT381 | BOV10CT381 | 12MAV10CT381 | Turbine thrust bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
1113 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CT382 | BOV10CT382 | 12MAV10CT382 | Turbine front bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
1114 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CT383 | BOV10CT383 | 12MAV10CT383 | Turbine rear bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
1115 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CT384 | BOV10CT384 | 12MAV10CT384 | Generator front bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
1116 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CT385 | BOV10CT385 | 12MAV10CT385 | Generator rear bearing return oil temperature | AI | 0 | 100 | °C |  |  |  | 65 | 70
1117 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CP101 | BOV10CP101 | 12MAV10CP101 | Main oil pump outlet pressure | AI | 0 | 2.5 | MPa |  | 17 | 1.8
1118 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV10CP111 | BOV10CP111 | 12MAV10CP111 | Lube oil pressure | AI | 0 | 0.25 | MPa |  | 0.04 | 0.055 | 0.25 | 0.25
1119 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV72CT361 | BOV72CT361 | 12MAV72CT361 | Oil cooler inlet temperature | AI | 0 | 100 | °C
1120 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV72CT362 | BOV72CT362 | 12MAV72CT362 | Oil cooler inlet temperature | AI | 0 | 100 | °C
1121 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV72CT363 | BOV72CT363 | 12MAV72CT363 | Oil cooler outlet temperature | AI | 0 | 100 | °C
1122 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV72CT364 | BOV72CT364 | 12MAV72CT364 | Oil cooler outlet temperature | AI | 0 | 100 | °C
1123 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV73CL151 | BOV73CL151 | 12MAV73CL151 | Oil tank level | AI | -200 | 200 | mm |  | -160 | -80 | 80 | 160
1124 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 | WIKA-07NP08-ABD-201-20-023 | BOV72CE011 | BOV72CE011 | 12MAV72CE011 | Auxiliary oil pump motor current | AI | 0 | 400 | A
1125 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | BOV72CT351 | BOV72CT351 | 12MAV72CT351 | NO.1 Oil cooler inlet water temperature | AI | 0 | 100 | °C
1126 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | BOV72CT352 | BOV72CT352 | 12MAV72CT352 | NO.1 Oil cooler outlet water temperature | AI | 0 | 100 | °C
1127 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | BOV72CT353 | BOV72CT353 | 12MAV72CT353 | NO.2 Oil cooler inlet water temperature | AI | 0 | 100 | °C
1128 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | BOV72CT354 | BOV72CT354 | 12MAV72CT354 | NO.2 Oil cooler outlet water temperature | AI | 0 | 100 | °C
1129 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | PGB10CT301 | PGB10CT301 | 12PGB10CT301 | Cooling water inlet temperature | AI | 0 | 100 | °C
1130 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | PGB10CT302 | PGB10CT302 | 12PGB10CT302 | Cooling water outlet temperature | AI | 0 | 100 | °C
1131 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | PGB10CT311 | PGB10CT311 | 12PGB10CT311 | Air cooler inlet water temperature | AI | 0 | 100 | °C
1132 | 2 | UJLJ AMG #2 | 9 | TURBINE | 1 | LUBE OIL SYSTEM #2 (C COOLING WATER) | WIKA-07NP08-ABD-201-20-030 | PGB10CT312 | PGB10CT312 | 12PGB10CT312 | Air cooler outlet water temperature | AI | 0 | 100 | °C
1133 | 2 | UJLJ AMG #2 | 9 | TURBINE | 2 | TURNING GEAR #2 | WIKA-07NP08-ABD-201-20-023 | BAY41FE001 | BAY41FE001 | 12MAY41FE001 | Turning gear motor current | AI | 0 | 50 | A
1134 | 2 | UJLJ AMG #2 | 9 | TURBINE | 3 | DEH #2 |  | BC02FE001 | BC02FE001 | 12MKY01FE001 | Generator power | Al | 0 | 75 | MW
1135 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BOW10CT601 | BOW10CT601 | 12MAW10CT601 | Gland steam pressure reducer and attemperator outlet temperature | AI | 0 | 600 | °C
1136 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BOW10CT602 | BOW10CT602 | 12MAW10CT602 | Gland steam pressure reducer and attemperator outlet temperature | AI | 0 | 600 | °C
1137 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BOW10CP101 | BOW10CP101 | 12MAW10CP101 | Gland steam pressure reducer and attemperator outlet pressure | AI | -0.1 | 1.5 | MPa |  |  | 0 | 0.9
1138 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BOW10CP103 | BOW10CP103 | 12MAW10CP103 | Surge tank pressure | AI | -0.1 | 1.5 | MPa
1139 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BOW10A001T | BOW10A001T | 12MAW10AA001GT | Gland steam pressure control valve position | AI | 0 | 100 | %
1140 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | BAB20A101T | BAB20A101T | 12LAB20AA101GT | Gland steam temperature control valve position | AI | 0 | 100 | %
1141 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | S20_E002.MV | S20_E002.MV | 12MAW10AA001AO | Gland steam pressure control valve control | AO | 0 | 100 | %
1142 | 2 | UJLJ AMG #2 | 9 | TURBINE | 4 | GLAND STEAM #2 | WIKA-07NP08-ABD-201-20-026 | S20_E003.MV | S20_E003.MV | 12LAB20AA101AO | Gland steam temperature control valve control | AO | 0 | 100 | %
1143 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BBA10CT601 | BBA10CT601 | 12LBA10CT601 | Boiler outlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
1144 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BBA10CT611 | BBA10CT611 | 12LBA10CT611 | Turbine inlet main steam temperature | AI | 0 | 600 | °C |  | 0 | 520 | 545 | 600
1145 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BBA10CP101 | BBA10CP101 | 12LBA10CP101 | Boiler outlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
1146 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BBA10CP113 | BBA10CP113 | 12LBA10CP113 | Turbine inlet main steam pressure | AI | 0 | 16 | MPa |  | 0 | 8.4 | 9.1 | 16
1147 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BBA10CF101 | BBA10CF101 | 12LBA10CF101 | Main steam flow | AI | 0 | 150 | t/h
1148 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CT651 | BO01CT651 | 12MAA01CT651 | Behind governing stage steam temperature | AI | 0 | 500 | °C
1149 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CT652 | BO01CT652 | 12MAA01CT652 | Behind governing stage steam temperature | AI | 0 | 500 | °C
1150 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CT653 | BO01CT653 | 12MAA01CT653 | Behind governing stage casing flange temperature | AI | 0 | 500 | °C
1151 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CT654 | BO01CT654 | 12MAA01CT654 | Behind governing stage casing flange temperature | AI | 0 | 500 | °C
1152 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CT657 | BO01CT657 | 12MAA01CT657 | Inside exhaust chamber temperature | AI | 0 | 200 | °C |  | 0 | 0 | 80 | 80
1153 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CP101 | BO01CP101 | 12MAA01CP101 | Behind governing stage steam pressure | AI | 0 | 10 | MPa
1154 | 2 | UJLJ AMG #2 | 9 | TURBINE | 5 | MAIN STEAM #2 | WIKA-07NP08-ABD-201-20-005 | BO01CP102 | BO01CP102 | 12MAA01CP102 | Inside exhaust chamber pressure | AI | -0.1 | 0.15 | MPa |  | -0.095 | -0.092 | -0.083 | -0.06
1155 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT351 | BO01CT351 | 12MAA01CT351 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1156 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT352 | BO01CT352 | 12MAA01CT352 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1157 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT353 | BO01CT353 | 12MAA01CT353 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1158 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT354 | BO01CT354 | 12MAA01CT354 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1159 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT355 | BO01CT355 | 12MAA01CT355 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1160 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT356 | BO01CT356 | 12MAA01CT356 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1161 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT357 | BO01CT357 | 12MAA01CT357 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1162 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 THRUST | WIKA-07NP08-ABD-201-20-023 | BO01CT358 | BO01CT358 | 12MAA01CT358 | Turbine thrust bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1163 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CT365 | BO01CT365 | 12MAA01CT365 | Turbine front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1164 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CT366 | BO01CT366 | 12MAA01CT366 | Turbine front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1165 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CT367 | BO01CT367 | 12MAA01CT367 | Turbine rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1166 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CT368 | BO01CT368 | 12MAA01CT368 | Turbine rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1167 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CG151 | BO01CG151 | 12MAA01CG151 | Turbine axial displacement | AI | -2 | -2 | mm |  | -1.5 | -1 | 1 | 1.5
1168 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CG152 | BO01CG152 | 12MAA01CG152 | Turbine axial displacement | AI | -2 | -2 | mm |  | -1.5 | -1 | 1 | 1.5
1169 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CG153 | BO01CG153 | 12MAA01CG153 | Turbine differential expension | AI | -5 | 7 | mm |  | -3 | -2
1170 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CG154 | BO01CG154 | 12MAA01CG154 | Turbine differential expension | AI | -5 | 7 | mm |  | -3 | -2
1171 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CG161 | BO01CG161 | 12MAA01CG161 | Turbine absolute expansion | AI | 0 | 25 | mm
1172 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CG162 | BO01CG162 | 12MAA01CG162 | Turbine absolute expansion | AI | 0 | 25 | mm
1173 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CS154 | BO01CS154 | 12MAA01CS154 | Turbine speed | AI | 0 | 3000 | rpm |  |  |  | 3210 | 3390
1174 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CS155 | BO01CS155 | 12MAA01CS155 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
1175 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CS156 | BO01CS156 | 12MAA01CS156 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
1176 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CS157 | BO01CS157 | 12MAA01CS157 | Turbine speed | AI | 0 | 5000 | rpm |  |  |  | 3210 | 3390
1177 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CS161 | BO01CS161 | 12MAA01CS161 | Turbine speed | AI | 0 | 4000 | rpm |  |  |  | 3210 | 3390
1178 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CY151 | BO01CY151 | 12MAA01CY151 | Turbine front shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1179 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS1 | WIKA-07NP08-ABD-201-20-023 | BO01CY152 | BO01CY152 | 12MAA01CY152 | Turbine front shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1180 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CY153 | BO01CY153 | 12MAA01CY153 | Turbine rear shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1181 | 2 | UJLJ AMG #2 | 9 | TURBINE | 6 | TURBINE #2 TS2 | WIKA-07NP08-ABD-201-20-023 | BO01CY154 | BO01CY154 | 12MAA01CY154 | Turbine rear shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1182 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT351 | MKA01CT351 | 12MKA01CT351 | Generator front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1183 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT352 | MKA01CT352 | 12MKA01CT352 | Generator front bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1184 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT354 | MKA01CT354 | 12MKA01CT354 | Generator rear bearing temperature | AI | 0 | 150 | °C |  |  |  | 85 | 100
1185 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT355 | MKA01CT355 | 12MKA01CT355 | Generator outlet air temperature | AI | 0 | 150 | °C
1186 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT356 | MKA01CT356 | 12MKA01CT356 | Generator outlet air temperature | AI | 0 | 150 | °C
1187 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT361 | MKA01CT361 | 12MKA01CT361 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1188 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT362 | MKA01CT362 | 12MKA01CT362 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1189 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT363 | MKA01CT363 | 12MKA01CT363 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1190 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT364 | MKA01CT364 | 12MKA01CT364 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1191 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT365 | MKA01CT365 | 12MKA01CT365 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1192 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT366 | MKA01CT366 | 12MKA01CT366 | Generator stator winding temperature | AI | 0 | 150 | °C |  |  |  | 110
1193 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT367 | MKA01CT367 | 12MKA01CT367 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1194 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT368 | MKA01CT368 | 12MKA01CT368 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1195 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT369 | MKA01CT369 | 12MKA01CT369 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1196 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT370 | MKA01CT370 | 12MKA01CT370 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1197 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT371 | MKA01CT371 | 12MKA01CT371 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1198 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CT372 | MKA01CT372 | 12MKA01CT372 | Generator stator core temperature | AI | 0 | 150 | °C |  |  |  | 105
1199 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CY151 | MKA01CY151 | 12MKA01CY151 | Generator front shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1200 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CY152 | MKA01CY152 | 12MKA01CY152 | Generator front shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1201 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CY153 | MKA01CY153 | 12MKA01CY153 | Generator rear shaft X direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1202 | 2 | UJLJ AMG #2 | 9 | TURBINE | 8 | GENERATOR #2 | WIKA-07NP08-ABD-201-20-023 | MKA01CY154 | MKA01CY154 | 12MKA01CY154 | Generator rear shaft Y direciton vibration | AI | 0 | 400 | mm |  |  |  | 160 | 250
1203 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BC02FE001 | BC02FE001 | 12BAB02FE001 | Generator Active Power | AI | 0 | 45.5 | MW
1204 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BC02FE004 | BC02FE004 | 12BAB02FE004 | Generator Frequency | AI | 0 | 50 | Hz
1205 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BC01FE001 | BC01FE001 | 12BAB01FE001 | Excitation Current | AI | 0 | 100 | A
1206 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BC01FE002 | BC01FE002 | 12BAB01FE002 | Excitation Voltage | AI | 0 | 100 | V
1207 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ01YA05 | BJ01YA05 | 12BBA01YA05 | Ampere analog Signal from Multi Power Meter | AI | 0 | 100 | %
1208 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ01YA06 | BJ01YA06 | 12BBA01YA06 | Watt analog Signal from Multi Power Meter | AI | 0 | 100 | %
1209 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ01YA07 | BJ01YA07 | 12BBA01YA07 | VAR analog Signal from Multi Power Meter | AI | 0 | 100 | %
1210 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ03YA01 | BJ03YA01 | 12BBA03YA01 | Watt analog Signal from Multi Power Meter Primary Air Fan #2 | AI | 0 | 100 | %
1211 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ03YA02 | BJ03YA02 | 12BBA03YA02 | VAR analog Signal from Multi Power Meter Primary Air Fan #2 | AI | 0 | 100 | %
1212 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ04YA01 | BJ04YA01 | 12BBA04YA01 | Watt analog Signal from Multi Power Meter Secondary Air Fan #2 | AI | 0 | 100 | %
1213 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ04YA02 | BJ04YA02 | 12BBA04YA02 | VAR analog Signal from Multi Power Meter Secondary Air Fan #2 | AI | 0 | 100 | %
1214 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ05YA01 | BJ05YA01 | 12BBA05YA01 | Watt analog Signal from Multi Power Meter ID Fan #2 | AI | 0 | 100 | %
1215 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ05YA02 | BJ05YA02 | 12BBA05YA02 | VAR analog Signal from Multi Power Meter ID Fan #2 | AI | 0 | 100 | %
1216 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ06YA01 | BJ06YA01 | 12BBA06YA01 | Watt analog Signal from Multi Power Meter Boiler Feed Pump #3 | AI | 0 | 100 | %
1217 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ06YA02 | BJ06YA02 | 12BBA06YA02 | VAR analog Signal from Multi Power Meter Boiler Feed Pump #3 | AI | 0 | 100 | %
1218 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ07YA01 | BJ07YA01 | 12BBA07YA01 | Watt analog Signal from Multi Power Meter Boiler Feed Pump #4 | AI | 0 | 100 | %
1219 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ07YA02 | BJ07YA02 | 12BBA07YA02 | VAR analog Signal from Multi Power Meter Boiler Feed Pump #4 | AI | 0 | 100 | %
1220 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ08YA01 | BJ08YA01 | 12BBA08YA01 | Watt analog Signal from Multi Power Meter Circulating Water Pump #3 | AI | 0 | 100 | %
1221 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ08YA02 | BJ08YA02 | 12BBA08YA02 | VAR analog Signal from Multi Power Meter Circulating WaterPump #3 | AI | 0 | 100 | %
1222 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ09YA01 | BJ09YA01 | 12BBA09YA01 | Watt analog Signal from Multi Power Meter Circulating Water Pump #4 | AI | 0 | 100 | %
1223 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ09YA02 | BJ09YA02 | 12BBA09YA02 | VAR analog Signal from Multi Power Meter Circulating WaterPump #4 | AI | 0 | 100 | %
1224 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ10YA01 | BJ10YA01 | 12BBA10YA01 | Watt analog Signal from Multi Power Meter Closed Cooling Water Pump #2 | AI | 0 | 100 | %
1225 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ10YA02 | BJ10YA02 | 12BBA10YA02 | VAR analog Signal from Multi Power Meter Closed Cooling WaterPump #2 | AI | 0 | 100 | %
1226 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ12YA05 | BJ12YA05 | 12BBA12YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #2 | AI | 0 | 100 | %
1227 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ12YA06 | BJ12YA06 | 12BBA12YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #2 | AI | 0 | 100 | %
1228 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ12YA07 | BJ12YA07 | 12BBA12YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 1600 kVA #2 | AI | 0 | 100 | %
1229 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ13YA05 | BJ13YA05 | 12BBA13YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #2 | AI | 0 | 100 | %
1230 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ13YA06 | BJ13YA06 | 12BBA13YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #2 | AI | 0 | 100 | %
1231 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ13YA07 | BJ13YA07 | 12BBA13YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 1000 kVA #2 | AI | 0 | 100 | %
1232 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ14YA05 | BJ14YA05 | 12BBA14YA05 | Ampere analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #2 | AI | 0 | 100 | %
1233 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ14YA06 | BJ14YA06 | 12BBA14YA06 | Watt analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #2 | AI | 0 | 100 | %
1234 | 2 | UJLJ AMG #2 | 11 | MAIN TRAFO #2 | 2 | ELECTRICAL #2 | WIKA-07NP08-ABD-201-30-001 | BJ14YA07 | BJ14YA07 | 12BBA14YA07 | VAR analog signal from Multi Power Meter Aux. Trafo of Main Building 500 kVA #2 | AI | 0 | 100 | %