## Belitung#1
No | SYSTEM NO. | SYSTEM NAME | EQUIPMENT NO. | EQUIPMENT NAME | DRAWING | TAG AT OPC | TAGATDCS | KKS | DESCRIPTION | TYPE I/O | RANGE Lo | RANGE Hi | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS | f_interlock | f_asset_health | f_value_h | f_value_l | Logic
1 | Efficiency Variable | COAL FEEDER SYSTEM #1 | 4 | COAL FEEDER A #1 | TM1608-0-E-HPB-001-00-01 | DPU_1_A:246 | 1M105AA1 | 1M105A-A1 | #1 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
2 | Efficiency Variable | COAL FEEDER SYSTEM #1 | 3 | COAL FEEDER B #1 | TM-1608-00-IC-0011-01-00 | DPU_1_A:282 | 1M105BA1 | 1M105B-A1 | #1 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
3 | Efficiency Variable | COAL FEEDER SYSTEM #1 | 4 | COAL FEEDER C #1 | TM-1608-00-IC-0011-01-00 | DPU_1_A:291 | 1M105CA1 | 1M105C-A1 | #1 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
4 | Efficiency Variable | FEED WATER SYSTEM #1 | 2 | BFP-A #1 | TM-1608-00-IC-007-01-00 | DPU_2_A:15 | 1PT303A | 1PT303A | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  | 0 | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
5 | Efficiency Variable | FEED WATER SYSTEM #1 | 3 | BFP-B #1 | TM-1608-00-IC-007-01-00 | DPU_2_A:18 | 1PT303B | 1PT303B | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
6 | Efficiency Variable | FEED WATER SYSTEM #1 | 4 | BFP-C #1 | TM-1608-00-IC-007-01-00 | DPU_2_A:483 | 1PT303C | 1PT303C | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  | 0 | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
7 | Efficiency Variable | FEED WATER SYSTEM #1 | 5 | HPH #1 | TM-1608-00-IC-0011-01-00 | DPU_3_A:273 | 1TE216 | 1TE216 | #1 TURBINE HP HEATER INLET STEAM TEMP | AI | 0 | 400 | °C | [9 empty] | 0
8 | Efficiency Variable | FEED WATER SYSTEM #2 | 6 | FEED WATER PIPING #1 | TM-1608-00-IC-007-01-00 | DPU_1_A:744 |  |  | #1 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h | [9 empty] | 0 |  |  | 1 | OR
9 | Constraint Variable | FLUE GAS SYSTEM #1 | 5 | GAS ANALYZER #1 | TM-1608-00-IC-003-05-00 | DPU_1_A:222 | 1AT102 | 1AT102 | GAS FLUE INLET O2% OF #1 BOILER | AI | 0 | 100 | % | [9 empty] | 1 | 1
10 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #1 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:417 | 1TE105 | 1TE105 | #1 BOILER BACK ATTEMPERATOR TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0
11 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #1 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:372 | 1TE104 | 1TE104 | #1 BOILER FRONT ATTEMPERATOR TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0
12 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #1 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:759 |  |  | #1 BOILER BACK BESUPERHEATER SPRAY FLOW | AI | 0 | 160000 | t/h | [9 empty] | 0 |  |  | 0.1 | AND
13 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #1 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:186 | 1FT103A | 1FT103A | #1 BOILER FRONT BESUPERHEATER SPRAY FLOW | AI | 0 | 160000 | t/h | [9 empty] | 0 |  |  | 0.1 | AND
14 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #1 | 17 | ECONOMIZER SYSTEM #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:786 | 1TE102 | 1TE102 | #1 BOILER FEEDWATER TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0 |  |  | 10 | AND
15 | Constraint Variable | FURNACE & CYCLONE SYSTEM #1 | 1 | FURNACE #1 | TM-1608-00-IC-003-04-00 | DPU_1_A:75 | 1PT119B | 1PT119B | #1 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 |  | -150 | 10 |  | 50 |  |  |  | 1 | 0 |  | -1 | OR
16 | Constraint Variable | FURNACE & CYCLONE SYSTEM #1 | 1 | FURNACE #1 | TM-1608-00-IC-003-04-00 | DPU_1_A:33 | 1PT119A | 1PT119A | #1 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 |  | -150 | 10 |  | 50 |  |  |  | 1 | 0 |  | -1 | OR
17 | Disturbance Variable | FURNACE & CYCLONE SYSTEM #1 | 10 | PRIMARY AIR FAN SYSTEM B #1 | TM-1608-00-IC-003-03-00 | DPU_1_A:711 |  |  | #2 PRIMARY AIR FLOW OF #1 BOILER | AI | 0 | 600 | t/h | [9 empty] | 0
18 | Control Variable | FURNACE & CYCLONE SYSTEM #1 | 11 | SECONDARY AIR FAN SYSTEM B #1 | TM-1608-00-IC-003-03-00 | DPU_1_A:717 |  |  | #2 SECONDARY AIR FLOW OF #1 BOILER | AI | 0 | 600000 | m3/h | [9 empty] | 0 |  |  | 1 | AND
19 | Constraint Variable | FURNACE & CYCLONE SYSTEM #1 | 2 | WINDBOX #1 | TM-1608-00-IC-003-04-00 | DPU_1_A:78 | 1PT111 | 1PT111 | #1 BOILER RIGHT WIND BOX PRESSURE | AI | 0 | 16 | KPa | [9 empty] | 0
20 | Constraint Variable | FURNACE & CYCLONE SYSTEM #1 | 2 | WINDBOX #1 | TM-1608-00-IC-003-04-00 | DPU_1_A:36 | 1PT110 | 1PT110 | #1 BOILER LEFT WIND BOX PRESSURE | AI | 0 | 16 | KPa | [9 empty] | 0
21 | Disturbance Variable | GENERATOR SYSTEM #1 | 2 | GENERATOR #1 | TM-1608-00-IC-0011-01-00 | DPU_3_A:522 | 1GT11 |  | #1 GENERATOR ACTIVE POWER | AI | [12 empty] | 0
22 | Efficiency Variable | MAIN STEAM SYSTEM #1 | 4 | BOILER MAIN STEAM PIPING SYSTEM #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:369 | 1TE101A | 1TE101A | #1 BOILER MAIN STEAM TEMPERATURE | AI | 0 | 600 | ℃ |  |  | 465 | 490 |  | 491 | 600 |  |  | 1 | 0 |  | 100 | OR
23 | Efficiency Variable | MAIN STEAM SYSTEM #1 | 4 | BOILER MAIN STEAM PIPING SYSTEM #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:750 |  |  | #1 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h | [9 empty] | 0 |  |  | 1 | OR
24 | Efficiency Variable | MAIN STEAM SYSTEM #1 | 4 | BOILER MAIN STEAM PIPING SYSTEM #1 | TM-1608-00-IC-003-02-00 | DPU_1_A:15 | 1PT105A | 1PT105A | #1 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa |  |  | 4.61 | 5.1 | [5 empty] | 1 | 0 |  | 2 | OR

## Belitung#2
No | SYSTEM NO. | SYSTEM NAME | EQUIPMENT NO. | EQUIPMENT NAME | DRAWING | TAG AT OPC | TAGATDCS | KKS | DESCRIPTION | TYPE I/O | RANGE Lo | RANGE Hi | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS | f_interlock | f_asset_health | f_value_h | f_value_l | Logic
1 | Efficiency Variable | COAL FEEDER SYSTEM #2 | 2 | COAL FEEDER A #2 | TM1608-0-E-LAC-001-00-01 | DPU_4_A:936 | 2M105AA1 | 2M105A-A1 | #2 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
2 | Efficiency Variable | COAL FEEDER SYSTEM #2 | 3 | COAL FEEDER B #2 | TM1608-0-E-LAC-001-00-01 | DPU_4_A:282 | 2M105BA1 | 2M105B-A1 | #2 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
3 | Efficiency Variable | COAL FEEDER SYSTEM #2 | 4 | COAL FEEDER C #2 | TM1608-0-E-LAC-001-00-01 | DPU_4_A:291 | 2M105CA1 | 2M105C-A1 | #2 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [9 empty] | 0
4 | Efficiency Variable | FEED WATER SYSTEM #2 | 2 | BFP-A #2 | TM-1608-00-IC-007-01-00 | DPU_5_A:15 | 2PT303A | 2PT303A | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  | 0 | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
5 | Efficiency Variable | FEED WATER SYSTEM #2 | 3 | BFP-B #2 | TM-1608-00-IC-007-01-00 | DPU_5_A:18 | 2PT303B | 2PT303B | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
6 | Efficiency Variable | FEED WATER SYSTEM #2 | 4 | BFP-C #2 | TM-1608-00-IC-007-01-00 | DPU_5_A:21 | 2PT303C | 2PT303C | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  | 0 | 7.8 | [5 empty] | 1 | 0 |  | 0.1 | OR
7 | Efficiency Variable | FEED WATER SYSTEM #2 | 2 | FEED WATER PIPING #2 | TM-1608-00-IC-007-01-00 | DPU_4_A:708 |  |  | #2 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h | [9 empty] | 0 |  |  | 1 | OR
8 | Efficiency Variable | FEED WATER SYSTEM #2 | 5 | HPH #2 | TM-1608-00-IC-003-01-00 | DPU_6_A:273 | 2TE216 | 2TE216 | #2 TURBINE HP HEATER INLET STEAM TEMP | AI | 0 | 400 | °C | [9 empty] | 0
9 | Constraint Variable | FLUE GAS SYSTEM #2 | 5 | GAS ANALYZER #2 | TM-1608-00-IC-003-05-00 | DPU_4_A:222 | 2AT102 | 2AT102 | GAS FLUE INLET O2% OF #2 BOILER | AI | 0 | 100 | % | [9 empty] | 0
10 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #2 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_4_A:720 |  |  | #2 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | 0 | 160000 | t/h | [9 empty] | 0 |  |  | 0.1 | AND
11 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #2 | 19 | ATTEMPERATOR HEATER #1 | TM-1608-00-IC-003-02-00 | DPU_4_A:186 | 2FT103A | 2FT103A | #2 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | 0 | 160000 | t/h | [9 empty] | 0 |  |  | 0.1 | AND
12 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #2 | 19 | ATTEMPERATOR HEATER #2 | TM-1608-00-IC-003-02-00 | DPU_4_A:417 | 2TE105 | 2TE105 | #2 BOILER BACK ATTEMPERATOR TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0
13 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #2 | 19 | ATTEMPERATOR HEATER #2 | TM-1608-00-IC-003-02-00 | DPU_4_A:372 | 2TE104 | 2TE104 | #2 BOILER FRONT ATTEMPERATOR TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0
14 | Efficiency Variable | FURNACE & CYCLONE SYSTEM #2 | 17 | ECONOMIZER SYSTEM #2 | TM-1608-00-IC-003-02-00 | DPU_4_A:924 | 2TE102 | 2TE102 | #2 BOILER FEEDWATER TEMPERATURE | AI | 0 | 600 | °C | [9 empty] | 0 |  |  | 10 | AND
15 | Constraint Variable | FURNACE & CYCLONE SYSTEM #2 | 1 | FURNACE #2 | TM-1608-00-IC-003-04-00 | DPU_4_A:879 | 2PT119B | 2PT119B | #2 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 |  | -150 | 10 |  | 50 |  |  |  | 1 | 0 |  | -999 | OR
16 | Constraint Variable | FURNACE & CYCLONE SYSTEM #2 | 1 | FURNACE #2 | TM-1608-00-IC-003-04-00 | DPU_4_A:876 | 2PT119A | 2PT119A | #2 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 |  | -150 | 10 |  | 50 |  |  |  | 1 | 0 |  | -999 | OR
17 | Disturbance Variable | FURNACE & CYCLONE SYSTEM #2 | 10 | PRIMARY AIR FAN SYSTEM B #1 | TM-1608-00-IC-003-03-00 | DPU_4_A:726 |  |  | #2 PRIMARY AIR FLOW OF #2 BOILER | AI | 0 | 600 | t/h | [9 empty] | 0
18 | Control Variable | FURNACE & CYCLONE SYSTEM #2 | 12 | SECONDARY AIR FAN SYSTEM B #2 | TM-1608-00-IC-003-03-00 | DPU_4_A:732 |  |  | #2 SECONDARY AIR FLOW OF #2 BOILER | AI | 0 | 600000 | m3/h | [9 empty] | 0 |  |  | 1 | AND
19 | Constraint Variable | FURNACE & CYCLONE SYSTEM #2 | 2 | WINDBOX #1 | TM-1608-00-IC-003-04-00 | DPU_4_A:78 | 2PT111 | 2PT111 | #2 BOILER RIGHT WIND BOX PRESSURE | AI | 0 | 16 | KPa | [9 empty] | 0
20 | Constraint Variable | FURNACE & CYCLONE SYSTEM #2 | 2 | WINDBOX #1 | TM-1608-00-IC-003-04-00 | DPU_4_A:36 | 2PT110 | 2PT110 | #2 BOILER LEFT WIND BOX PRESSURE | AI | 0 | 16 | KPa | [9 empty] | 0
21 | Disturbance Variable | GENERATOR SYSTEM #2 | 2 | GENERATOR #2 | TM-1608-00-IC-0011-01-00 | DPU_6_A:438 | 2FDJGL |  | #2 GENERATOR ACTIVE POWER | AI | [12 empty] | 0
22 | Efficiency Variable | MAIN STEAM SYSTEM #2 | 4 | BOILER MAIN STEAM PIPING SYSTEM #1 | TM-1608-00-IC-005-01-01 | DPU_4_A:369 | 2TE101A | 2TE101A | #2 BOILER MAIN STEAM TEMPERATURE | AI | 0 | 600 | °C |  |  | 465 | 490 |  | 491 |  |  |  | 1 | 0 |  | 100 | OR
23 | Efficiency Variable | MAIN STEAM SYSTEM #2 | 4 | BOILER MAIN STEAM PIPING SYSTEM #1 | TM-1608-00-IC-003-02-00 | DPU_4_A:714 |  |  | #2 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h | [9 empty] | 0 |  |  | 1 | OR
24 | Efficiency Variable | MAIN STEAM SYSTEM #2 | 4 | BOILER MAIN STEAM PIPING SYSTEM #2 | TM-1608-00-IC-003-02-00 | DPU_4_A:15 | 2PT105A | 2PT105A | #2 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa | 3.7 |  | 4.85 | 6.04 |  | 6.27 |  |  |  | 1 | 0 |  | 2 | OR