## Tag Mapping
No | VARIABLE | NAME EQUIPMENT | DRAWING | TAG AT DCS | TAG AT HISTORY | TAG AT OPC | TAG AT HISTORY | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | L1 | H1 | Notes | Current Value | Average | Minimum | Maximum | Std | Broken Sensor
1 | Target Variable | Oxygen Sensor | K0203-02 | 90AIR-O2-SEL.UNIT1@NET0 | 90AIR-O2-SEL | 90AIR-O2-SEL.DROP10/60.UNIT1@NET0 | 90AIR-O2-SEL | 90AIR-O2-SEL | O2 XMTR SELECTED | AI | 0.37 | 20.9 | % |  |  |  | 2.894 | 6.0018 | 1.1268 | 20.9016 | 6.2292 | FALSE
2 | Manipulated Variable | Burner Tilt Position Lower | K0202-02 | 90HHA01AA118XQ01.UNIT1@NET0 | 90HHA01AA118XQ01 | 90HHA01AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118XQ01 | 90HHA01AA118XQ01 | #1 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -30.6409 | -14.9194 | -32.6184 | 28.7952 | 12.3537 | FALSE
3 | Manipulated Variable | Burner Tilt Position Lower | K0202-02 | 90HHA02AA118XQ01.UNIT1@NET0 | 90HHA02AA118XQ01 | 90HHA02AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA118XQ01 | 90HHA02AA118XQ01 | #2 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -31.2177 | -14.7141 | -31.5015 | 30.0174 | 12.3413 | FALSE
4 | Manipulated Variable | Burner Tilt Position Lower | K0202-02 | 90HHA03AA118XQ01.UNIT1@NET0 | 90HHA03AA118XQ01 | 90HHA03AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA118XQ01 | 90HHA03AA118XQ01 | #3 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -29.0295 | -14.111 | -33.6301 | 30.75 | 12.4812 | FALSE
5 | Manipulated Variable | Burner Tilt Position Lower | K0202-02 | 90HHA04AA118XQ01.UNIT1@NET0 | 90HHA04AA118XQ01 | 90HHA04AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA118XQ01 | 90HHA04AA118XQ01 | #4 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -28.9151 | -14.877 | -30.1282 | 30.672 | 12.0771 | FALSE
6 | Manipulated Variable | Burner Tilt Position Upper | K0202-02 | 90HHA01AA118BXQ01.UNIT1@NET0 | 90HHA01AA118BXQ01 | 90HHA01AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118BXQ01 | 90HHA01AA118BXQ01 | #1 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -24.0262 | -13.4691 | -30.3891 | 30.75 | 11.7946 | FALSE
7 | Manipulated Variable | Burner Tilt Position Upper | K0202-02 | 90HHA02AA118BXQ01.UNIT1@NET0 | 90HHA02AA118BXQ01 | 90HHA02AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA118BXQ01 | 90HHA02AA118BXQ01 | #2 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -29.5697 | -14.31 | -32.2018 | 30.75 | 13.0183 | FALSE
8 | Manipulated Variable | Burner Tilt Position Upper | K0202-02 | 90HHA03AA118BXQ01.UNIT1@NET0 | 90HHA03AA118BXQ01 | 90HHA03AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA118BXQ01 | 90HHA03AA118BXQ01 | #3 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -28.288 | -14.0564 | -33.9002 | 30.75 | 12.1102 | FALSE
9 | Manipulated Variable | Burner Tilt Position Upper | K0202-02 | 90HHA04AA118BXQ01.UNIT1@NET0 | 90HHA04AA118BXQ01 | 90HHA04AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA118BXQ01 | 90HHA04AA118BXQ01 | #4 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -27.8165 | -13.7623 | -29.0158 | 30.75 | 12.4312 | FALSE
10 | Manipulated Variable | Secondary Air Flow | K0202-01 | 90HLA21CF101-FLOW.UNIT1@NET0 | 90HLA21CF101-FLOW | 90HLA21CF101-FLOW.DROP10/60.UNIT1@NET0 | 90HLA21CF101-FLOW | 90HLA21CF101 | A SIDE HOT SECOND AIR FLOW 1 | AI | 0 | 5000 | t/h |  |  |  | 861.069 | 736.8456 | 0 | 1908.25 | 288.2363 | FALSE
11 | Manipulated Variable | Secondary Air Flow | K0202-01 | 90HLA21CF102-FLOW.UNIT1@NET0 | 90HLA21CF102-FLOW | 90HLA21CF102-FLOW.DROP10/60.UNIT1@NET0 | 90HLA21CF102-FLOW | 90HLA21CF102 | A SIDE HOT SECOND AIR FLOW 2 | AI | 0 | 5000 | t/h |  |  |  | 853.706 | 737.7763 | 0 | 1769.29 | 285.7356 | FALSE
12 | Manipulated Variable | Secondary Air Flow | K0202-01 | 90HLA22CF101-FLOW.UNIT1@NET0 | 90HLA22CF101-FLOW | 90HLA22CF101-FLOW.DROP10/60.UNIT1@NET0 | 90HLA22CF101-FLOW | 90HLA22CF101 | B SIDE HOT SECOND AIR FLOW 1 | AI | 0 | 5000 | t/h |  |  |  | 1052.47 | 791.4978 | 0 | 1180.19 | 300.4589 | FALSE
13 | Manipulated Variable | Secondary Air Flow | K0202-01 | 90HLA22CF102-FLOW.UNIT1@NET0 | 90HLA22CF102-FLOW | 90HLA22CF102-FLOW.DROP10/60.UNIT1@NET0 | 90HLA22CF102-FLOW | 90HLA22CF102 | B SIDE HOT SECOND AIR FLOW 2 | AI | 0 | 5000 | t/h |  |  |  | 910.456 | 700.9568 | 0 | 1129.59 | 313.0473 | FALSE
14 | Manipulated Variable | Total Secondary Air Flow |  | 90AIR-TOTSA-FLOW.UNIT1@NET0 | 90AIR-TOTSA-FLOW | 90AIR-TOTSA-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOTSA-FLOW | 90AIR-TOTSA-FLOW | TOTAL SA FLOW | AI |  |  | t/h |  |  |  | 1909.85 | 1510.9969 | 0 | 2270.88 | 600.0271 | FALSE
15 | Efficiency Variable | Cold Reheat Steam Pressure | K0201-03 | 90LBC10CP111.UNIT1@NET0 | 90LBC10CP111 | 90LBC10CP111.DROP9/59.UNIT1@NET0 | 90LBC10CP111 | 90LBC10CP111 | BOILER SIDE COLD RH STEAM PRESS. 1 | AI |  |  | bar |  |  |  | 34.5621 | 27.5903 | -0.379 | 39.0619 | 12.9545 | FALSE
16 | Efficiency Variable | Cold Reheat Steam Temperature | K0201-03 | 90LBC10CT602.UNIT1@NET0 | 90LBC10CT602 | 90LBC10CT602.DROP9/59.UNIT1@NET0 | 90LBC10CT602 | 90LBC10CT602 | BOILER SIDE COLD RH STEAM TEMP. | TC |  |  | °C |  |  |  | 320.085 | 283.7285 | 26.2922 | 370.635 | 94.7003 | FALSE
17 | Efficiency Variable | Feed Water Flow | K0201-02 | 90LAB41CF10X-SEL.UNIT1@NET0 | 90LAB41CF10X-SEL | 90LAB41CF10X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CF10X-SEL | 90LAB41CF10X-SEL | MAIN FEED WATER FLOW SEL | AI | 0 | 2188 | t/h |  |  |  | 1967.86 | 1411.9208 | 0 | 2239.86 | 782.4567 | FALSE
18 | Efficiency Variable | Feed Water Pressure | K0201-02 | 90LAB41CP10X-SEL.UNIT1@NET0 | 90LAB41CP10X-SEL | 90LAB41CP10X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CP10X-SEL | 90LAB41CP10X-SEL | MAIN FEED WATER PRESS. SEL | AI | 0 | 250 | bar |  |  |  | 187.878 | 140.32 | -0.0629 | 249.523 | 72.4193 | FALSE
19 | Efficiency Variable | Feed Water Temperature | K0201-02 | 90LAB41CT30X-SEL.UNIT1@NET0 | 90LAB41CT30X-SEL | 90LAB41CT30X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CT30X-SEL | 90LAB41CT30X-SEL | MAIN FEED WATER TEMP. SEL | RTD | 0 | 500 | °C |  |  |  | 265.201 | 216.3496 | 25.9668 | 276.342 | 93.7301 | FALSE
20 | Efficiency Variable | Hot Reheat Steam Pressure |  | DEH1-HRHR.UNIT1@NET0 | DEH1-HRHR | DEH1-HRHR.DROP9/59.UNIT1@NET0 | DEH1-HRHR | DEH1-HRHR | HOT REHEAT STEAM PRESSURE | AI | 0 |  | bar |  |  |  | 3.2603 | 2.6142 | -0.0256 | 4.1959 | 1.1942 | FALSE
21 | Efficiency Variable | Hot Reheat Steam Temperature | K0206-01 | 90LBB20CT601.UNIT1@NET0 | 90LBB20CT601 | 90LBB20CT601.DROP9/59.UNIT1@NET0 | 90LBB20CT601 | 90LBB20CT601 | HOT REHEATED STEAM TEMP. | TC |  |  | °C |  |  |  | 538.117 | 460.9626 | 27.6811 | 557.103 | 157.2784 | FALSE
22 | Efficiency Variable | Main Steam Flow |  | 90FWS-STM-FLOW.UNIT1@NET0 | 90FWS-STM-FLOW | 90FWS-STM-FLOW.DROP10/60.UNIT1@NET0 | 90FWS-STM-FLOW | 90FWS-STM-FLOW | TOTAL STEAM FLOW | AI |  |  | t/h |  |  |  | 1942.62 | 1432.7489 | 16.3515 | 2259.62 | 772.192 | FALSE
23 | Efficiency Variable | Main Steam Pressure |  | 90LBA20CP10X-SEL.UNIT1@NET0 | 90LBA20CP10X-SEL | 90LBA20CP10X-SEL.DROP10/60.UNIT1@NET0 | 90LBA20CP10X-SEL | 90LBA20CP10X-SEL | MAIN STM PT SELECTED | AI |  |  | bar |  |  |  | 166.775 | 124.3157 | -0.4298 | 178.352 | 64.9544 | FALSE
24 | Efficiency Variable | Main Steam Temperature | K0206-03 | 90LBA20CT601.UNIT1@NET0 | 90LBA20CT601 | 90LBA20CT601.DROP9/59.UNIT1@NET0 | 90LBA20CT601 | 90LBA20CT601 | MAIN STEAM TEMP. | TC | 0 | 1000 | °C |  |  |  | 534.496 | 450.3869 | 27.8064 | 551.765 | 166.0168 | FALSE
25 | Efficiency Variable | Reheat Spray water Flow | K0201-03 | 90LAF01CF101-CMP1.UNIT1@NET0 | 90LAF01CF101-CMP1 | 90LAF01CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAF01CF101-CMP1 | 90LAF01CF101 | A SIDE RH SPRAY WATER FLOW | AI | 0 | 70 | t/h |  |  |  | 23.9997 | 13.4701 | 0 | 61.2376 | 10.8631 | FALSE
26 | Efficiency Variable | Reheat Spray water Flow | K0201-03 | 90LAF02CF101-CMP1.UNIT1@NET0 | 90LAF02CF101-CMP1 | 90LAF02CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAF02CF101-CMP1 | 90LAF02CF101 | B SIDE RH SPRAY WATER FLOW | AI | 0 | 200 | t/h |  |  |  | 28.1714 | 14.9865 | 0 | 70.9118 | 13.4267 | FALSE
27 | Efficiency Variable | Reheat Spray water Temperature | K0201-03 | 90LAF10CT301.UNIT1@NET0 | 90LAF10CT301 | 90LAF10CT301.DROP6/56.UNIT1@NET0 | 90LAF10CT301 | 90LAF10CT301 | RH SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 178.267 | 143.6199 | 26.5964 | 188.441 | 57.8928 | FALSE
28 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE01CF101-CMP1.UNIT1@NET0 | 90LAE01CF101-CMP1 | 90LAE01CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE01CF101-CMP1 | 90LAE01CF101 | A SIDE SH PRI SPRAY WATER FLOW | AI | 0 | 60 | t/h |  |  |  | 35.4878 | 29.4217 | 0 | 135.737 | 21.0896 | FALSE
29 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE02CF101-CMP1.UNIT1@NET0 | 90LAE02CF101-CMP1 | 90LAE02CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE02CF101-CMP1 | 90LAE02CF101 | B SIDE SH PRI SPRAY WATER FLOW | AI | 0 | 60 | t/h |  |  |  | 9.3818 | 12.2859 | 0 | 135.841 | 17.9048 | FALSE
30 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE03CF101-CMP1.UNIT1@NET0 | 90LAE03CF101-CMP1 | 90LAE03CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE03CF101-CMP1 | 90LAE03CF101 | A SIDE SH SECOND SPRAY WATER FLOW | AI | 0 | 120 | t/h |  |  |  | 5.516 | 4.037 | 0 | 71.0851 | 5.8231 | FALSE
31 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE04CF101-CMP1.UNIT1@NET0 | 90LAE04CF101-CMP1 | 90LAE04CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE04CF101-CMP1 | 90LAE04CF101 | B SIDE SH SECOND SPRAY WATER FLOW | AI | 0 | 120 | t/h |  |  |  | 3.4385 | 1.4886 | 0 | 71.0904 | 3.9361 | FALSE
32 | Efficiency Variable | SH Spray Water Temperture | K0201-02 | 90LAE01CT301.UNIT1@NET0 | 90LAE01CT301 | 90LAE01CT301.DROP10/60.UNIT1@NET0 | 90LAE01CT301 | 90LAE01CT301 | A SIDE SH PRI SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 179.059 | 143.9987 | 21.4368 | 407.619 | 58.8206 | FALSE
33 | Efficiency Variable | SH Spray Water Temperture | K0201-02 | 90LAE01CT302.UNIT1@NET0 | 90LAE01CT302 | 90LAE01CT302.DROP10/60.UNIT1@NET0 | 90LAE01CT302 | 90LAE01CT302 | B SIDE SH PRI SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 178.663 | 142.9501 | 26.7224 | 573.021 | 58.0877 | FALSE
34 | Efficiency Variable | SH Spray Water Temperture | K0201-02 | 90LAE03CT301.UNIT1@NET0 | 90LAE03CT301 | 90LAE03CT301.DROP10/60.UNIT1@NET0 | 90LAE03CT301 | 90LAE03CT301 | A SIDE SH SECOND SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 177.212 | 140.5694 | 26.2186 | 280.155 | 57.5021 | FALSE
35 | Efficiency Variable | SH Spray Water Temperture | K0201-02 | 90LAE04CT301.UNIT1@NET0 | 90LAE04CT301 | 90LAE04CT301.DROP10/60.UNIT1@NET0 | 90LAE04CT301 | 90LAE04CT301 | B SIDE SH SECOND SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 177.74 | 138.2428 | 26.3446 | 294.771 | 56.2302 | FALSE
36 | Disturbance Variable | Load |  | DEH1-MWGROSS.UNIT1@NET0 | DEH1-MWGROSS | DEH1-MWGROSS.DROP41/91.UNIT1@NET0 | DEH1-MWGROSS | DEH1-MWGROSS | GROSS MW | AI | 0 | 881.74 | MW |  |  |  | 630.994 | 453.7285 | 0 | 664.075 | 244.183 | FALSE
37 | Disturbance Variable | PA Flow |  | 90AIR-TOTPA-FLOW.UNIT1@NET0 | 90AIR-TOTPA-FLOW | 90AIR-TOTPA-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOTPA-FLOW | 90AIR-TOTPA-FLOW | TOTAL PA FLOW | AI |  |  | t/h |  |  |  | 824.578 | 617.048 | 0 | 991.104 | 305.0129 | FALSE
38 | Disturbance Variable | Total Coal Flow |  | 90FUE-TOT-FLOW.UNIT1@NET0 | 90FUE-TOT-FLOW | 90FUE-TOT-FLOW.DROP10/60.UNIT1@NET0 | 90FUE-TOT-FLOW | 90FUE-TOT-FLOW | FUEL TOTAL FLOW | AI |  |  | t/h |  |  |  | 386.736 | 278.1366 | 0 | 452.815 | 150.3143 | FALSE
39 | Control Variable | Burner Tilt | K0202-02 | 90HHA01AA118YQ01.UNIT1@NET0 | 90HHA01AA118YQ01 | 90HHA01AA118YQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118YQ01 | 90HHA01AA118YQ01 | #1 CORNER BURNER ADJUST ACTUATOR COMMAND LOWER | AO |  |  | ° | -35 |  |  | -28.2 | -13.6721 | -30 | 30 | 12.5061 | FALSE
40 | Control Variable | Burner Tilt | K0202-02 | 90HHA01AA118BYQ01.UNIT1@NET0 | 90HHA01AA118BYQ01 | 90HHA01AA118BYQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118BYQ01 | 90HHA01AA118BYQ01 | #1 CORNER BURNER ADJUST ACTUATOR COMMAND UPPER | AO |  |  | ° | -35 |  |  | -28.2 | -13.7244 | -30 | 20 | 12.4914 | FALSE
41 | Constraint Variable | Furnace Pressure | K0203-01 | 90HBK10CP10X-SEL.UNIT1@NET0 | 90HBK10CP10X-SEL | 90HBK10CP10X-SEL.DROP10/60.UNIT1@NET0 | 90HBK10CP10X-SEL | 90HBK10CP10X | FURNACE PRESS SELECTED | [7 empty] | -1.1185 | -0.90442 | -10.0153 | 3.0685 | 0.38081 | FALSE
42 | Constraint Variable | Mill Outlet Temperature A | K0205-01 | 90HHE11CT601.UNIT1@NET0 | 90HHE11CT601 | 90HHE11CT601.DROP3/53.UNIT1@NET0 | 90HHE11CT601 | 90HHE11CT601 | AIR POWDER PIPE METAL TEMP. FOR A LAYER A1 BURNER | TC |  |  | °C |  |  |  | 48.9695 | 44.7737 | 22.768 | 2050.86 | 10.6207 | FALSE
43 | Constraint Variable | Mill Outlet Temperature A | K0205-01 | 90HHE12CT601.UNIT1@NET0 | 90HHE12CT601 | 90HHE12CT601.DROP3/53.UNIT1@NET0 | 90HHE12CT601 | 90HHE12CT601 | AIR POWDER PIPE METAL TEMP. FOR A LAYER A2 BURNER | TC |  |  | °C |  |  |  | 50.8848 | 45.8274 | 21.8668 | 1252.72 | 9.6148 | FALSE
44 | Constraint Variable | Mill Outlet Temperature A | K0205-01 | 90HHE13CT601.UNIT1@NET0 | 90HHE13CT601 | 90HHE13CT601.DROP3/53.UNIT1@NET0 | 90HHE13CT601 | 90HHE13CT601 | AIR POWDER PIPE METAL TEMP. FOR A LAYER A3 BURNER | TC |  |  | °C |  |  |  | 48.8761 | 44.8277 | 22.5713 | 2059.84 | 10.8464 | FALSE
45 | Constraint Variable | Mill Outlet Temperature A | K0205-01 | 90HHE14CT601.UNIT1@NET0 | 90HHE14CT601 | 90HHE14CT601.DROP3/53.UNIT1@NET0 | 90HHE14CT601 | 90HHE14CT601 | AIR POWDER PIPE METAL TEMP. FOR A LAYER A4 BURNER | TC |  |  | °C |  |  |  | 53.1959 | 47.5892 | -57.2233 | 2050.86 | 12.6329 | FALSE
46 | Constraint Variable | Mill Outlet Temperature B | K0205-02 | 90HHE21CT601.UNIT1@NET0 | 90HHE21CT601 | 90HHE21CT601.DROP3/53.UNIT1@NET0 | 90HHE21CT601 | 90HHE21CT601 | AIR POWDER PIPE METAL TEMP. FOR B LAYER B1 BURNER | TC |  |  | °C |  |  |  | 51.1867 | 45.7094 | 23.6694 | 58.4351 | 9.2028 | FALSE
47 | Constraint Variable | Mill Outlet Temperature B | K0205-02 | 90HHE22CT601.UNIT1@NET0 | 90HHE22CT601 | 90HHE22CT601.DROP3/53.UNIT1@NET0 | 90HHE22CT601 | 90HHE22CT601 | AIR POWDER PIPE METAL TEMP. FOR B LAYER B2 BURNER | TC |  |  | °C |  |  |  | 50.989 | 44.6702 | 22.675 | 55.727 | 9.0848 | FALSE
48 | Constraint Variable | Mill Outlet Temperature B | K0205-02 | 90HHE23CT601.UNIT1@NET0 | 90HHE23CT601 | 90HHE23CT601.DROP3/53.UNIT1@NET0 | 90HHE23CT601 | 90HHE23CT601 | AIR POWDER PIPE METAL TEMP. FOR B LAYER B3 BURNER | TC |  |  | °C |  |  |  | 51.9881 | 46.8921 | 23.3689 | 59.4352 | 9.7439 | FALSE
49 | Constraint Variable | Mill Outlet Temperature B | K0205-02 | 90HHE24CT601.UNIT1@NET0 | 90HHE24CT601 | 90HHE24CT601.DROP3/53.UNIT1@NET0 | 90HHE24CT601 | 90HHE24CT601 | AIR POWDER PIPE METAL TEMP. FOR B LAYER B4 BURNER | TC |  |  | °C |  |  |  | 50.8848 | 45.6594 | 23.3689 | 58.7373 | 9.1608 | FALSE
50 | Constraint Variable | Mill Outlet Temperature C | K0205-03 | 90HHE31CT601.UNIT1@NET0 | 90HHE31CT601 | 90HHE31CT601.DROP3/53.UNIT1@NET0 | 90HHE31CT601 | 90HHE31CT601 | AIR POWDER PIPE METAL TEMP. FOR C LAYER C1 BURNER | TC |  |  | °C |  |  |  | 51.8947 | 42.294 | 22.3746 | 74.8895 | 10.5138 | FALSE
51 | Constraint Variable | Mill Outlet Temperature C | K0205-03 | 90HHE32CT601.UNIT1@NET0 | 90HHE32CT601 | 90HHE32CT601.DROP3/53.UNIT1@NET0 | 90HHE32CT601 | 90HHE32CT601 | AIR POWDER PIPE METAL TEMP. FOR C LAYER C2 BURNER | TC |  |  | °C |  |  |  | 52.592 | 42.9064 | 22.4676 | 65.8044 | 11.117 | FALSE
52 | Constraint Variable | Mill Outlet Temperature C | K0205-03 | 90HHE33CT601.UNIT1@NET0 | 90HHE33CT601 | 90HHE33CT601.DROP3/53.UNIT1@NET0 | 90HHE33CT601 | 90HHE33CT601 | AIR POWDER PIPE METAL TEMP. FOR C LAYER C3 BURNER | TC |  |  | °C |  |  |  | 49.9792 | 41.4764 | 22.4676 | 56.2161 | 9.9264 | FALSE
53 | Constraint Variable | Mill Outlet Temperature C | K0205-03 | 90HHE34CT601.UNIT1@NET0 | 90HHE34CT601 | 90HHE34CT601.DROP3/53.UNIT1@NET0 | 90HHE34CT601 | 90HHE34CT601 | AIR POWDER PIPE METAL TEMP. FOR C LAYER C4 BURNER | TC |  |  | °C |  |  |  | 52.1966 | 42.263 | 22.3746 | 67.0247 | 10.6997 | FALSE
54 | Constraint Variable | Mill Outlet Temperature D | K0205-04 | 90HHE41CT601.UNIT1@NET0 | 90HHE41CT601 | 90HHE41CT601.DROP8/58.UNIT1@NET0 | 90HHE41CT601 | 90HHE41CT601 | AIR POWDER PIPE METAL TEMP. FOR D LAYER D1 BURNER | TC |  |  | °C |  |  |  | 48.1684 | 45.0335 | 23.7624 | 53.9976 | 9.0573 | FALSE
55 | Constraint Variable | Mill Outlet Temperature D | K0205-04 | 90HHE42CT601.UNIT1@NET0 | 90HHE42CT601 | 90HHE42CT601.DROP8/58.UNIT1@NET0 | 90HHE42CT601 | 90HHE42CT601 | AIR POWDER PIPE METAL TEMP. FOR D LAYER D2 BURNER | TC |  |  | °C |  |  |  | 49.3755 | 46.564 | 23.9913 | 55.1014 | 9.8672 | FALSE
56 | Constraint Variable | Mill Outlet Temperature D | K0205-04 | 90HHE43CT601.UNIT1@NET0 | 90HHE43CT601 | 90HHE43CT601.DROP8/58.UNIT1@NET0 | 90HHE43CT601 | 90HHE43CT601 | AIR POWDER PIPE METAL TEMP. FOR D LAYER D3 BURNER | TC |  |  | °C |  |  |  | 51.7904 | 46.7608 | 23.7624 | 55.5077 | 9.9667 | FALSE
57 | Constraint Variable | Mill Outlet Temperature D | K0205-04 | 90HHE44CT601.UNIT1@NET0 | 90HHE44CT601 | 90HHE44CT601.DROP8/58.UNIT1@NET0 | 90HHE44CT601 | 90HHE44CT601 | AIR POWDER PIPE METAL TEMP. FOR D LAYER D4 BURNER | TC |  |  | °C |  |  |  | 52.0924 | 47.3757 | 23.7624 | 56.4139 | 10.286 | FALSE
58 | Constraint Variable | Mill Outlet Temperature E | K0205-05 | 90HHE51CT601.UNIT1@NET0 | 90HHE51CT601 | 90HHE51CT601.DROP8/58.UNIT1@NET0 | 90HHE51CT601 | 90HHE51CT601 | AIR POWDER PIPE METAL TEMP. FOR E LAYER E1 BURNER | TC |  |  | °C |  |  |  | 52.1966 | 45.5938 | 22.4676 | 74.5869 | 10.6492 | FALSE
59 | Constraint Variable | Mill Outlet Temperature E | K0205-05 | 90HHE52CT601.UNIT1@NET0 | 90HHE52CT601 | 90HHE52CT601.DROP8/58.UNIT1@NET0 | 90HHE52CT601 | 90HHE52CT601 | AIR POWDER PIPE METAL TEMP. FOR E LAYER E2 BURNER | TC |  |  | °C |  |  |  | 49.7816 | 44.1804 | 22.8717 | 70.654 | 10.0024 | FALSE
60 | Constraint Variable | Mill Outlet Temperature E | K0205-05 | 90HHE53CT601.UNIT1@NET0 | 90HHE53CT601 | 90HHE53CT601.DROP8/58.UNIT1@NET0 | 90HHE53CT601 | 90HHE53CT601 | AIR POWDER PIPE METAL TEMP. FOR E LAYER E3 BURNER | TC |  |  | °C |  |  |  | 53.1024 | 45.9575 | 22.768 | 76.0998 | 10.7656 | FALSE
61 | Constraint Variable | Mill Outlet Temperature E | K0205-05 | 90HHE54CT601.UNIT1@NET0 | 90HHE54CT601 | 90HHE54CT601.DROP8/58.UNIT1@NET0 | 90HHE54CT601 | 90HHE54CT601 | AIR POWDER PIPE METAL TEMP. FOR E LAYER E4 BURNER | TC |  |  | °C |  |  |  | 50.3852 | 44.1485 | 22.1672 | 54.9144 | 9.8614 | FALSE
62 | Constraint Variable | Mill Outlet Temperature F | K0205-07 | 90HHE61CT601.UNIT1@NET0 | 90HHE61CT601 | 90HHE61CT601.DROP8/58.UNIT1@NET0 | 90HHE61CT601 | 90HHE61CT601 | AIR POWDER PIPE METAL TEMP. FOR F LAYER F1 BURNER | TC |  |  | °C |  |  |  | 33.0972 | 38.2653 | 22.9647 | 57.3201 | 8.6646 | FALSE
63 | Constraint Variable | Mill Outlet Temperature F | K0205-07 | 90HHE62CT601.UNIT1@NET0 | 90HHE62CT601 | 90HHE62CT601.DROP8/58.UNIT1@NET0 | 90HHE62CT601 | 90HHE62CT601 | AIR POWDER PIPE METAL TEMP. FOR F LAYER F2 BURNER | TC |  |  | °C |  |  |  | 29.185 | 36.5006 | 21.4735 | 61.9788 | 8.6399 | FALSE
64 | Constraint Variable | Mill Outlet Temperature F | K0205-07 | 90HHE63CT601.UNIT1@NET0 | 90HHE63CT601 | 90HHE63CT601.DROP8/58.UNIT1@NET0 | 90HHE63CT601 | 90HHE63CT601 | AIR POWDER PIPE METAL TEMP. FOR F LAYER F3 BURNER | TC |  |  | °C |  |  |  | 32.7962 | 37.0788 | 22.9755 | 59.6438 | 7.7797 | FALSE
65 | Constraint Variable | Mill Outlet Temperature F | K0205-07 | 90HHE64CT601.UNIT1@NET0 | 90HHE64CT601 | 90HHE64CT601.DROP8/58.UNIT1@NET0 | 90HHE64CT601 | 90HHE64CT601 | AIR POWDER PIPE METAL TEMP. FOR F LAYER F4 BURNER | TC |  |  | °C |  |  |  | 31.8932 | 37.3108 | 22.675 | 56.4139 | 8.243 | FALSE
66 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA01AA115XQ01.UNIT1@NET0 | 90HHA01AA115XQ01 | 90HHA01AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA115XQ01 | 90HHA01AA115XQ01 | #1 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 20.6848 | 21.0285 | -1.25 | 108.865 | 21.0434 | FALSE
67 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA01AA116XQ01.UNIT1@NET0 | 90HHA01AA116XQ01 | 90HHA01AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA116XQ01 | 90HHA01AA116XQ01 | #1 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.0244 | 4.5141 | -1.25 | 111.52 | 17.3965 | FALSE
68 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA01AA117XQ01.UNIT1@NET0 | 90HHA01AA117XQ01 | 90HHA01AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA117XQ01 | 90HHA01AA117XQ01 | #1 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.116 | 5.258 | -1.25 | 100.16 | 12.1762 | FALSE
69 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA02AA115XQ01.UNIT1@NET0 | 90HHA02AA115XQ01 | 90HHA02AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA115XQ01 | 90HHA02AA115XQ01 | #2 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 23.0499 | 22.5896 | -1.25 | 108.079 | 20.1333 | FALSE
70 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA02AA116XQ01.UNIT1@NET0 | 90HHA02AA116XQ01 | 90HHA02AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA116XQ01 | 90HHA02AA116XQ01 | #2 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.3418 | 4.785 | -0.5402 | 110.788 | 18.8083 | FALSE
71 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA02AA117XQ01.UNIT1@NET0 | 90HHA02AA117XQ01 | 90HHA02AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA117XQ01 | 90HHA02AA117XQ01 | #2 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.444 | 6.6575 | -1.25 | 101.8 | 15.4975 | FALSE
72 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA03AA115XQ01.UNIT1@NET0 | 90HHA03AA115XQ01 | 90HHA03AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA115XQ01 | 90HHA03AA115XQ01 | #3 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 20.5551 | 21.07 | -0.1968 | 102.083 | 20.3926 | FALSE
73 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA03AA116XQ01.UNIT1@NET0 | 90HHA03AA116XQ01 | 90HHA03AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA116XQ01 | 90HHA03AA116XQ01 | #3 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.0443 | 4.9898 | -0.7385 | 110.643 | 18.7456 | FALSE
74 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA03AA117XQ01.UNIT1@NET0 | 90HHA03AA117XQ01 | 90HHA03AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA117XQ01 | 90HHA03AA117XQ01 | #3 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.2808 | 6.1851 | -1.25 | 103.273 | 16.6999 | FALSE
75 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA04AA115XQ01.UNIT1@NET0 | 90HHA04AA115XQ01 | 90HHA04AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA115XQ01 | 90HHA04AA115XQ01 | #4 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 21.1426 | 21.0535 | -1.12 | 102.762 | 20.603 | FALSE
76 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA04AA116XQ01.UNIT1@NET0 | 90HHA04AA116XQ01 | 90HHA04AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA116XQ01 | 90HHA04AA116XQ01 | #4 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.116 | 1.3657 | -0.6546 | 103.487 | 8.7711 | FALSE
77 | Constraint Variable | Over-Fire-Air Dampers | K0202-02 | 90HHA04AA117XQ01.UNIT1@NET0 | 90HHA04AA117XQ01 | 90HHA04AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA117XQ01 | 90HHA04AA117XQ01 | #4 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.0443 | 6.2294 | -1.25 | 105.47 | 17.7392 | FALSE
78 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP150.UNIT1@NET0 | 90HBK10CP150 | 90HBK10CP150.DROP10/60.UNIT1@NET0 | 90HBK10CP150 | 90HBK10CP150 | FURNACE/WINBOX DIFF. PRESS. 1 | AI | 0 | 25 | mBar |  |  |  | 10.7483 | 8.3722 | -0.156 | 25.5131 | 4.0744 | FALSE
79 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP151.UNIT1@NET0 | 90HBK10CP151 | 90HBK10CP151.DROP10/60.UNIT1@NET0 | 90HBK10CP151 | 90HBK10CP151 | FURNACE/WINBOX DIFF. PRESS. 2 | AI | 0 | 25 | mbar |  |  |  | 9.5219 | 7.0673 | -0.1598 | 24.7482 | 3.799 | FALSE
80 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP152.UNIT1@NET0 | 90HBK10CP152 | 90HBK10CP152.DROP10/60.UNIT1@NET0 | 90HBK10CP152 | 90HBK10CP152 | FURNACE/WINBOX DIFF. PRESS. 3 | AI | 0 | 25 | mBar |  |  |  | 10.7044 | 8.1541 | -0.1617 | 16.6515 | 4.0644 | FALSE
81 |  |  |  | 90AIR-TOT-FLOW.UNIT1@NET0 | 90AIR-TOT-FLOW | 90AIR-TOT-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOT-FLOW | 90AIR-TOT-FLOW | TOTAL AIR FLOW | AI |  |  | t/h |  |  |  | 2797.76 | 2137.4012 | 0 | 3038.81 | 883.8448 | FALSE
82

## Calculations
No | Variables Color | Calculations
1 |  | Average all variables
2 |  | Average all / 2
or use only this tag