## Tag Mapping
No | VARIABLE | NAME EQUIPMENT | DRAWING | TAG AT DCS | TAG AT HISTORY | TAG AT OPC | TAG AT HISTORY | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | L1 | H1 | Notes | Current Value | Average | Minimum | Maximum | Std | Broken Sensor
1 | Manipulated Variable | Oxygen Sensor | K0203-02 | 90AIR-O2-SEL.UNIT1@NET0 | 90AIR-O2-SEL | 90AIR-O2-SEL.DROP10/60.UNIT1@NET0 | 90AIR-O2-SEL | 90AIR-O2-SEL | O2 XMTR SELECTED | AI | 0.37 | 20.9 | % |  |  |  | 2.894 | 6.6959 | 1.4777 | 20.9016 | 6.6505 | FALSE
2 | Disturbance Variable | Burner Tilt Position Lower | K0202-02 | 90HHA01AA118XQ01.UNIT1@NET0 | 90HHA01AA118XQ01 | 90HHA01AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118XQ01 | 90HHA01AA118XQ01 | #1 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -30.6409 | -14.9118 | -32.7832 | 13.071 | 11.5878 | FALSE
3 | Disturbance Variable | Burner Tilt Position Lower | K0202-02 | 90HHA02AA118XQ01.UNIT1@NET0 | 90HHA02AA118XQ01 | 90HHA02AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA118XQ01 | 90HHA02AA118XQ01 | #2 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -31.2177 | -15.8116 | -31.5518 | 12.5171 | 11.5094 | FALSE
4 | Disturbance Variable | Burner Tilt Position Lower | K0202-02 | 90HHA03AA118XQ01.UNIT1@NET0 | 90HHA03AA118XQ01 | 90HHA03AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA118XQ01 | 90HHA03AA118XQ01 | #3 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -29.0295 | -14.6265 | -31.6846 | 13.5013 | 11.3806 | FALSE
5 | Disturbance Variable | Burner Tilt Position Lower | K0202-02 | 90HHA04AA118XQ01.UNIT1@NET0 | 90HHA04AA118XQ01 | 90HHA04AA118XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA118XQ01 | 90HHA04AA118XQ01 | #4 CORNER BURNER ADJUST ACTUATOR POSITION LOWER | AI |  |  | ° | -35 |  |  | -28.9151 | -14.4355 | -30.1877 | 13.3823 | 11.2678 | FALSE
6 | Disturbance Variable | Burner Tilt Position Upper | K0202-02 | 90HHA01AA118BXQ01.UNIT1@NET0 | 90HHA01AA118BXQ01 | 90HHA01AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118BXQ01 | 90HHA01AA118BXQ01 | #1 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -24.0262 | -12.815 | -30.3891 | 30.75 | 10.9301 | FALSE
7 | Disturbance Variable | Burner Tilt Position Upper | K0202-02 | 90HHA02AA118BXQ01.UNIT1@NET0 | 90HHA02AA118BXQ01 | 90HHA02AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA118BXQ01 | 90HHA02AA118BXQ01 | #2 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -29.5697 | -13.9416 | -32.0691 | 30.75 | 12.075 | FALSE
8 | Disturbance Variable | Burner Tilt Position Upper | K0202-02 | 90HHA03AA118BXQ01.UNIT1@NET0 | 90HHA03AA118BXQ01 | 90HHA03AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA118BXQ01 | 90HHA03AA118BXQ01 | #3 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -28.288 | -13.9364 | -33.9002 | 30.75 | 11.4645 | FALSE
9 | Disturbance Variable | Burner Tilt Position Upper | K0202-02 | 90HHA04AA118BXQ01.UNIT1@NET0 | 90HHA04AA118BXQ01 | 90HHA04AA118BXQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA118BXQ01 | 90HHA04AA118BXQ01 | #4 CORNER BURNER ADJUST ACTUATOR POSITION UPPER | AI |  |  | ° | -35 |  |  | -27.8165 | -13.4221 | -28.6633 | 30.75 | 11.7578 | FALSE
10 | Manipulated Variable | Total Secondary Air Flow |  | 90AIR-TOTSA-FLOW.UNIT1@NET0 | 90AIR-TOTSA-FLOW | 90AIR-TOTSA-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOTSA-FLOW | 90AIR-TOTSA-FLOW | TOTAL SA FLOW | AI |  |  | t/h |  |  |  | 1909.85 | 1487.2599 | 0 | 2261.42 | 619.5859 | FALSE
11 | Efficiency Variable | Cold Reheat Steam Pressure | K0201-03 | 90LBC10CP111.UNIT1@NET0 | 90LBC10CP111 | 90LBC10CP111.DROP9/59.UNIT1@NET0 | 90LBC10CP111 | 90LBC10CP111 | BOILER SIDE COLD RH STEAM PRESS. 1 | AI |  |  | bar |  |  |  | 34.5621 | 25.5483 | -0.379 | 40.7007 | 14.0011 | FALSE
12 | Efficiency Variable | Cold Reheat Steam Temperature | K0201-03 | 90LBC10CT602.UNIT1@NET0 | 90LBC10CT602 | 90LBC10CT602.DROP9/59.UNIT1@NET0 | 90LBC10CT602 | 90LBC10CT602 | BOILER SIDE COLD RH STEAM TEMP. | TC |  |  | °C |  |  |  | 320.085 | 271.9096 | 26.2922 | 370.635 | 103.5738 | FALSE
13 | Efficiency Variable | Feed Water Flow | K0201-02 | 90LAB41CF10X-SEL.UNIT1@NET0 | 90LAB41CF10X-SEL | 90LAB41CF10X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CF10X-SEL | 90LAB41CF10X-SEL | MAIN FEED WATER FLOW SEL | AI | 0 | 2188 | t/h |  |  |  | 1967.86 | 1411.5897 | 0 | 2239.86 | 767.7085 | FALSE
14 | Efficiency Variable | Feed Water Pressure | K0201-02 | 90LAB41CP10X-SEL.UNIT1@NET0 | 90LAB41CP10X-SEL | 90LAB41CP10X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CP10X-SEL | 90LAB41CP10X-SEL | MAIN FEED WATER PRESS. SEL | AI | 0 | 250 | bar |  |  |  | 187.878 | 139.1836 | -0.0629 | 249.523 | 71.7724 | FALSE
15 | Efficiency Variable | Feed Water Temperature | K0201-02 | 90LAB41CT30X-SEL.UNIT1@NET0 | 90LAB41CT30X-SEL | 90LAB41CT30X-SEL.DROP10/60.UNIT1@NET0 | 90LAB41CT30X-SEL | 90LAB41CT30X-SEL | MAIN FEED WATER TEMP. SEL | RTD | 0 | 500 | °C |  |  |  | 265.201 | 216.1654 | 25.9668 | 276.342 | 90.816 | FALSE
16 | Efficiency Variable | Hot Reheat Steam Pressure |  | DEH1-HRHR.UNIT1@NET0 | DEH1-HRHR | DEH1-HRHR.DROP9/59.UNIT1@NET0 | DEH1-HRHR | DEH1-HRHR | HOT REHEAT STEAM PRESSURE | AI | 0 |  | bar |  |  |  | 3.2603 | 2.4282 | -0.0256 | 4.1959 | 1.2935 | FALSE
17 | Efficiency Variable | Hot Reheat Steam Temperature | K0206-01 | 90LBB20CT601.UNIT1@NET0 | 90LBB20CT601 | 90LBB20CT601.DROP9/59.UNIT1@NET0 | 90LBB20CT601 | 90LBB20CT601 | HOT REHEATED STEAM TEMP. | TC |  |  | °C |  |  |  | 538.117 | 467.4793 | 27.6811 | 557.103 | 148.4156 | FALSE
18 | Efficiency Variable | Main Steam Flow |  | 90FWS-STM-FLOW.UNIT1@NET0 | 90FWS-STM-FLOW | 90FWS-STM-FLOW.DROP10/60.UNIT1@NET0 | 90FWS-STM-FLOW | 90FWS-STM-FLOW | TOTAL STEAM FLOW | AI |  |  | t/h |  |  |  | 1942.62 | 1422.7316 | 17.2671 | 2251.383 | 737.1176 | FALSE
19 | Efficiency Variable | Main Steam Pressure |  | 90LBA20CP10X-SEL.UNIT1@NET0 | 90LBA20CP10X-SEL | 90LBA20CP10X-SEL.DROP10/60.UNIT1@NET0 | 90LBA20CP10X-SEL | 90LBA20CP10X-SEL | MAIN STM PT SELECTED | AI |  |  | bar |  |  |  | 166.775 | 125.5458 | -0.4298 | 178.352 | 63.597 | FALSE
20 | Efficiency Variable | Main Steam Temperature | K0206-03 | 90LBA20CT601.UNIT1@NET0 | 90LBA20CT601 | 90LBA20CT601.DROP9/59.UNIT1@NET0 | 90LBA20CT601 | 90LBA20CT601 | MAIN STEAM TEMP. | TC | 0 | 1000 | °C |  |  |  | 534.496 | 453.5132 | 27.8064 | 560.537 | 164.9977 | FALSE
21 | Efficiency Variable | Reheat Spray water Flow | K0201-03 | 90LAF01CF101-CMP1.UNIT1@NET0 | 90LAF01CF101-CMP1 | 90LAF01CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAF01CF101-CMP1 | 90LAF01CF101 | A SIDE RH SPRAY WATER FLOW | AI | 0 | 70 | t/h |  |  |  | 23.9997 | 14.3592 | 0 | 61.2376 | 11.0588 | FALSE
22 | Efficiency Variable | Reheat Spray water Flow | K0201-03 | 90LAF02CF101-CMP1.UNIT1@NET0 | 90LAF02CF101-CMP1 | 90LAF02CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAF02CF101-CMP1 | 90LAF02CF101 | B SIDE RH SPRAY WATER FLOW | AI | 0 | 200 | t/h |  |  |  | 28.1714 | 14.8574 | 0 | 70.9118 | 12.4893 | FALSE
23 | Efficiency Variable | Reheat Spray water Temperature | K0201-03 | 90LAF10CT301.UNIT1@NET0 | 90LAF10CT301 | 90LAF10CT301.DROP6/56.UNIT1@NET0 | 90LAF10CT301 | 90LAF10CT301 | RH SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 178.267 | 143.1506 | 26.5964 | 188.441 | 57.532 | FALSE
24 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE01CF101-CMP1.UNIT1@NET0 | 90LAE01CF101-CMP1 | 90LAE01CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE01CF101-CMP1 | 90LAE01CF101 | A SIDE SH PRI SPRAY WATER FLOW | AI | 0 | 60 | t/h |  |  |  | 35.4878 | 31.3057 | 0 | 135.737 | 21.3228 | FALSE
25 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE02CF101-CMP1.UNIT1@NET0 | 90LAE02CF101-CMP1 | 90LAE02CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE02CF101-CMP1 | 90LAE02CF101 | B SIDE SH PRI SPRAY WATER FLOW | AI | 0 | 60 | t/h |  |  |  | 9.3818 | 12.9539 | 0 | 135.841 | 17.2418 | FALSE
26 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE03CF101-CMP1.UNIT1@NET0 | 90LAE03CF101-CMP1 | 90LAE03CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE03CF101-CMP1 | 90LAE03CF101 | A SIDE SH SECOND SPRAY WATER FLOW | AI | 0 | 120 | t/h |  |  |  | 5.516 | 4.113 | 0 | 71.0851 | 4.874 | FALSE
27 | Efficiency Variable | SH Spray Water Flow | K0201-02 | 90LAE04CF101-CMP1.UNIT1@NET0 | 90LAE04CF101-CMP1 | 90LAE04CF101-CMP1.DROP10/60.UNIT1@NET0 | 90LAE04CF101-CMP1 | 90LAE04CF101 | B SIDE SH SECOND SPRAY WATER FLOW | AI | 0 | 120 | t/h |  |  |  | 3.4385 | 1.6471 | 0 | 71.0904 | 3.861 | FALSE
28 | Efficiency Variable | SH Spray Water Temperture 1 | K0201-02 | 90LAE01CT301.UNIT1@NET0 | 90LAE01CT301 | 90LAE01CT301.DROP10/60.UNIT1@NET0 | 90LAE01CT301 | 90LAE01CT301 | A SIDE SH PRI SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 179.059 | 143.6229 | 21.4368 | 407.619 | 58.238 | FALSE
29 | Efficiency Variable | SH Spray Water Temperture 1 | K0201-02 | 90LAE01CT302.UNIT1@NET0 | 90LAE01CT302 | 90LAE01CT302.DROP10/60.UNIT1@NET0 | 90LAE01CT302 | 90LAE01CT302 | B SIDE SH PRI SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 178.663 | 142.8164 | 26.7224 | 573.021 | 57.5764 | FALSE
30 | Efficiency Variable | SH Spray Water Temperture 2 | K0201-02 | 90LAE03CT301.UNIT1@NET0 | 90LAE03CT301 | 90LAE03CT301.DROP10/60.UNIT1@NET0 | 90LAE03CT301 | 90LAE03CT301 | A SIDE SH SECOND SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 177.212 | 140.06 | 26.2186 | 280.155 | 56.9813 | FALSE
31 | Efficiency Variable | SH Spray Water Temperture 2 | K0201-02 | 90LAE04CT301.UNIT1@NET0 | 90LAE04CT301 | 90LAE04CT301.DROP10/60.UNIT1@NET0 | 90LAE04CT301 | 90LAE04CT301 | B SIDE SH SECOND SPRAY WATER TEMP. | RTD | 0 | 500 | °C |  |  |  | 177.74 | 139.0324 | 26.3446 | 294.771 | 56.1904 | FALSE
32 | Disturbance Variable | Load |  | DEH1-MWGROSS.UNIT1@NET0 | DEH1-MWGROSS | DEH1-MWGROSS.DROP41/91.UNIT1@NET0 | DEH1-MWGROSS | DEH1-MWGROSS | GROSS MW | AI | 0 | 881.74 | MW |  |  |  | 630.994 | 453.2608 | 0 | 690.3808 | 241.7205 | FALSE
33 | Disturbance Variable | PA Flow |  | 90AIR-TOTPA-FLOW.UNIT1@NET0 | 90AIR-TOTPA-FLOW | 90AIR-TOTPA-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOTPA-FLOW | 90AIR-TOTPA-FLOW | TOTAL PA FLOW | AI |  |  | t/h |  |  |  | 824.578 | 621.5444 | 0 | 1021.5338 | 302.9016 | FALSE
34 | Disturbance Variable | Total Coal Flow |  | 90FUE-TOT-FLOW.UNIT1@NET0 | 90FUE-TOT-FLOW | 90FUE-TOT-FLOW.DROP10/60.UNIT1@NET0 | 90FUE-TOT-FLOW | 90FUE-TOT-FLOW | FUEL TOTAL FLOW | AI |  |  | t/h |  |  |  | 386.736 | 280.9621 | 0 | 423.7474 | 146.1531 | FALSE
35 | Manipulated Variable | Burner Tilt Lower Command | K0202-02 | 90HHA01AA118YQ01.UNIT1@NET0 | 90HHA01AA118YQ01 | 90HHA01AA118YQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118YQ01 | 90HHA01AA118YQ01 | #1 CORNER BURNER ADJUST ACTUATOR COMMAND LOWER | AO |  |  | ° | -35 |  |  | -28.2 | -14.1558 | -30 | 13.8 | 11.2238 | FALSE
36 | Manipulated Variable | Burner Tilt Upper Command | K0202-02 | 90HHA01AA118BYQ01.UNIT1@NET0 | 90HHA01AA118BYQ01 | 90HHA01AA118BYQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA118BYQ01 | 90HHA01AA118BYQ01 | #1 CORNER BURNER ADJUST ACTUATOR COMMAND UPPER | AO |  |  | ° | -35 |  |  | -28.2 | -13.4724 | -30 | 20 | 11.7717 | FALSE
37 | Constraint Variable | Furnace Pressure | K0203-01 | 90HBK10CP10X-SEL.UNIT1@NET0 | 90HBK10CP10X-SEL | 90HBK10CP10X-SEL.DROP10/60.UNIT1@NET0 | 90HBK10CP10X-SEL | 90HBK10CP10X | FURNACE PRESS SELECTED |  |  |  |  | -100 | 0 |  | -1.1185 | -0.89387 | -10.0153 | 4.2474 | 0.37962 | FALSE
38 | Constraint Variable | Over-Fire-Air Dampers G | K0202-02 | 90HHA01AA115XQ01.UNIT1@NET0 | 90HHA01AA115XQ01 | 90HHA01AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA115XQ01 | 90HHA01AA115XQ01 | #1 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 20.6848 | 20.1448 | -1.25 | 108.865 | 18.0397 | FALSE
39 | Constraint Variable | Over-Fire-Air Dampers H | K0202-02 | 90HHA01AA116XQ01.UNIT1@NET0 | 90HHA01AA116XQ01 | 90HHA01AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA116XQ01 | 90HHA01AA116XQ01 | #1 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.0244 | 3.8406 | -1.25 | 111.52 | 14.7462 | FALSE
40 | Constraint Variable | Over-Fire-Air Dampers I | K0202-02 | 90HHA01AA117XQ01.UNIT1@NET0 | 90HHA01AA117XQ01 | 90HHA01AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA01AA117XQ01 | 90HHA01AA117XQ01 | #1 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.116 | 3.7449 | -1.25 | 100.16 | 10.4751 | FALSE
41 | Constraint Variable | Over-Fire-Air Dampers G | K0202-02 | 90HHA02AA115XQ01.UNIT1@NET0 | 90HHA02AA115XQ01 | 90HHA02AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA115XQ01 | 90HHA02AA115XQ01 | #2 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 23.0499 | 21.8216 | -1.25 | 108.079 | 17.3204 | FALSE
42 | Constraint Variable | Over-Fire-Air Dampers H | K0202-02 | 90HHA02AA116XQ01.UNIT1@NET0 | 90HHA02AA116XQ01 | 90HHA02AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA116XQ01 | 90HHA02AA116XQ01 | #2 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.3418 | 3.7798 | -0.5402 | 110.788 | 15.837 | FALSE
43 | Constraint Variable | Over-Fire-Air Dampers I | K0202-02 | 90HHA02AA117XQ01.UNIT1@NET0 | 90HHA02AA117XQ01 | 90HHA02AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA02AA117XQ01 | 90HHA02AA117XQ01 | #2 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.444 | 4.7219 | -1.25 | 101.8 | 13.1646 | FALSE
44 | Constraint Variable | Over-Fire-Air Dampers G | K0202-02 | 90HHA03AA115XQ01.UNIT1@NET0 | 90HHA03AA115XQ01 | 90HHA03AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA115XQ01 | 90HHA03AA115XQ01 | #3 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 20.5551 | 20.0638 | -0.1968 | 102.083 | 17.6169 | FALSE
45 | Constraint Variable | Over-Fire-Air Dampers H | K0202-02 | 90HHA03AA116XQ01.UNIT1@NET0 | 90HHA03AA116XQ01 | 90HHA03AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA116XQ01 | 90HHA03AA116XQ01 | #3 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.0443 | 4.1255 | -0.7385 | 110.643 | 15.8635 | FALSE
46 | Constraint Variable | Over-Fire-Air Dampers I | K0202-02 | 90HHA03AA117XQ01.UNIT1@NET0 | 90HHA03AA117XQ01 | 90HHA03AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA03AA117XQ01 | 90HHA03AA117XQ01 | #3 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.2808 | 4.2261 | -1.25 | 103.273 | 14.1176 | FALSE
47 | Constraint Variable | Over-Fire-Air Dampers G | K0202-02 | 90HHA04AA115XQ01.UNIT1@NET0 | 90HHA04AA115XQ01 | 90HHA04AA115XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA115XQ01 | 90HHA04AA115XQ01 | #4 CORNER G LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 21.1426 | 20.3474 | -1.12 | 102.762 | 17.741 | FALSE
48 | Constraint Variable | Over-Fire-Air Dampers H | K0202-02 | 90HHA04AA116XQ01.UNIT1@NET0 | 90HHA04AA116XQ01 | 90HHA04AA116XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA116XQ01 | 90HHA04AA116XQ01 | #4 CORNER H LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | 0.116 | 1.7013 | -0.6546 | 103.487 | 8.1805 | FALSE
49 | Constraint Variable | Over-Fire-Air Dampers I | K0202-02 | 90HHA04AA117XQ01.UNIT1@NET0 | 90HHA04AA117XQ01 | 90HHA04AA117XQ01.DROP10/60.UNIT1@NET0 | 90HHA04AA117XQ01 | 90HHA04AA117XQ01 | #4 CORNER I LAYER SOFA AIR DAMPER POSITION | AI | 0 | 100 | % | -5 | 105 |  | -0.0443 | 4.4023 | -1.25 | 105.47 | 14.9946 | FALSE
50 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP150.UNIT1@NET0 | 90HBK10CP150 | 90HBK10CP150.DROP10/60.UNIT1@NET0 | 90HBK10CP150 | 90HBK10CP150 | FURNACE/WINBOX DIFF. PRESS. 1 | AI | 0 | 25 | mBar |  |  |  | 10.7483 | 8.3311 | -0.15602 | 25.5131 | 4.0333 | FALSE
51 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP151.UNIT1@NET0 | 90HBK10CP151 | 90HBK10CP151.DROP10/60.UNIT1@NET0 | 90HBK10CP151 | 90HBK10CP151 | FURNACE/WINBOX DIFF. PRESS. 2 | AI | 0 | 25 | mbar |  |  |  | 9.5219 | 7.4126 | -0.15984 | 24.7482 | 3.7655 | FALSE
52 | Constraint Variable | Windbox-to-Furnace Diff. Press | K0202-02 | 90HBK10CP152.UNIT1@NET0 | 90HBK10CP152 | 90HBK10CP152.DROP10/60.UNIT1@NET0 | 90HBK10CP152 | 90HBK10CP152 | FURNACE/WINBOX DIFF. PRESS. 3 | AI | 0 | 25 | mBar |  |  |  | 10.7044 | 8.2038 | -0.16365 | 14.9254 | 4.0483 | FALSE
53 | Disturbance Variable | Total Air Flow |  | 90AIR-TOT-FLOW.UNIT1@NET0 | 90AIR-TOT-FLOW | 90AIR-TOT-FLOW.DROP10/60.UNIT1@NET0 | 90AIR-TOT-FLOW | 90AIR-TOT-FLOW | TOTAL AIR FLOW | AI |  |  | t/h |  |  |  | 2797.76 | 2108.6658 | 0 | 3038.81 | 910.5585 | FALSE
54 | Constraint Variable | Mill Outlet Temperature A |  |  |  | 90HFC10CT30X-SEL.DROP3/53.UNIT1@NET0 | 90HFC10CT30X-SEL.UNIT1@NET0 | 90HFC10CT30X-SEL | MILL A AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 59.3759 | 54.3066 | 28.0451 | 79.2135 | 10.8389 | FALSE
55 | Constraint Variable | Mill Outlet Temperature B |  |  |  | 90HFC20CT30X-SEL.DROP3/53.UNIT1@NET0 | 90HFC20CT30X-SEL.UNIT1@NET0 | 90HFC20CT30X-SEL | MILL B AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 48.3924 | 53.7051 | 28.0451 | 80.5573 | 11.0455 | FALSE
56 | Constraint Variable | Mill Outlet Temperature C |  |  |  | 90HFC30CT30X-SEL.DROP3/53.UNIT1@NET0 | 90HFC30CT30X-SEL.UNIT1@NET0 | 90HFC30CT30X-SEL | MILL C AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 58.4857 | 53.4857 | 27.9821 | 70.8427 | 11.1418 | FALSE
57 | Constraint Variable | Mill Outlet Temperature D |  |  |  | 90HFC40CT30X-SEL.DROP8/58.UNIT1@NET0 | 90HFC40CT30X-SEL.UNIT1@NET0 | 90HFC40CT30X-SEL | MILL D AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 60.2028 | 55.3386 | 28.4231 | 263.6984 | 10.2252 | FALSE
58 | Constraint Variable | Mill Outlet Temperature E |  |  |  | 90HFC50CT30X-SEL.DROP8/58.UNIT1@NET0 | 90HFC50CT30X-SEL.UNIT1@NET0 | 90HFC50CT30X-SEL | MILL E AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 59.8211 | 53.1324 | 27.7931 | 86.8356 | 11.3836 | FALSE
59 | Constraint Variable | Mill Outlet Temperature F |  |  |  | 90HFC60CT30X-SEL.DROP8/58.UNIT1@NET0 | 90HFC60CT30X-SEL.UNIT1@NET0 | 90HFC60CT30X-SEL | MILL F AIR POWDER MIX TEMP SEL | RTD |  |  | °C |  |  |  | 59.9483 | 50.0221 | 29.2423 | 85.3628 | 9.2508 | FALSE
60 | Target Variable | Efficiency |  |  |  | Efficiency | Efficiency |  | Efficiency |  | 0 | 100 | % |  |  |  |  | 80.9908 | 60 | 90 | 9.0571

## Calculations
No | Variables Color | Calculations
1 |  | Averaged by `Name Equipment`
2 |  | Sum by `Name Equipment` / 2
3 |  | Sum of all