## RBG1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG NAME | LOW LIMIT | HI LIMIT | SEQUENCE | BRACKET OPEN | BRACKET CLOSE | UNIT MEAS | NOTES
1 | Target Variable | Efficiency | Efficiency | 60 | 100 | 1 | ( | ) | %
2 | Manipulated Variable | All Wind | OPC.AIRFLOW:MATH1.RO01 |  |  | 1 | ( | ) | % | Total airflow
3 | Manipulated Variable | Total Secondary Air Flow | OPC.AIRFLOW_1:HLACFA1.PNT |  |  | 1 | (((( | ) + | T/H
4 | Manipulated Variable | Total Secondary Air Flow | OPC.AIRFLOW_1:HLACFA2.PNT |  |  | 2 | ( | )) / 2) + | T/H
5 | Manipulated Variable | Total Secondary Air Flow | OPC.AIRFLOW_2:HLACFB1.PNT |  |  | 3 | ((( | ) + | T/H
6 | Manipulated Variable | Total Secondary Air Flow | OPC.AIRFLOW_2:HLACFB2.PNT |  |  | 4 | ( | )) / 2)) | T/H
7 | Manipulated Variable | Burner Tilt Position Lower | OPC.2QDAS:ZT210705.PNT |  |  | 1 | (( | ) + | %
8 | Manipulated Variable | Burner Tilt Position Lower | OPC.2QDAS:ZT210707.PNT |  |  | 2 | ( | ) + | %
9 | Manipulated Variable | Burner Tilt Position Lower | OPC.2QDAS:ZT210801.PNT |  |  | 3 | ( | ) + | %
10 | Manipulated Variable | Burner Tilt Position Lower | OPC.2QDAS:ZT210803.PNT |  |  | 4 | ( | )) / 4 | %
11 | Manipulated Variable | Burner Tilt Position Upper | OPC.2QDAS:ZT210706.PNT |  |  | 1 | (( | ) + | %
12 | Manipulated Variable | Burner Tilt Position Upper | OPC.2QDAS:ZT210708.PNT |  |  | 2 | ( | ) + | %
13 | Manipulated Variable | Burner Tilt Position Upper | OPC.2QDAS:ZT210802.PNT |  |  | 3 | ( | ) + | %
14 | Manipulated Variable | Burner Tilt Position Upper | OPC.2QDAS:ZT210804.PNT |  |  | 4 | ( | )) / 4 | %
15 | Manipulated Variable | Excess Oxygen Sensor | OPC.OXYGEN:SIGSEL1.OUT | 1.5 | 20 | 1 | ( | ) | %
16 | Disturbance Variable | Coal Flow | OPC.FUELMASTER:AINCOAL.PNT |  |  | 1 | ( | ) | T/H
17 | Disturbance Variable | Efficiency | Efficiency | 60 | 100 | 1 | ( | ) | %
18 | Disturbance Variable | Load | OPC.2SDAS:AI174108.PNT | 200 | 330 | 1 | ( | ) | MW
19 | Disturbance Variable | Total Primary Air Flow | OPC.MILLAHCAD_2:CALCA2.RO01 |  |  | 1 | (((( | ) + | T/H
20 | Disturbance Variable | Total Primary Air Flow | OPC.MILLAHCAD_2:CALCA3.RO01 |  |  | 2 | ( | )) / 2) + | T/H
21 | Disturbance Variable | Total Primary Air Flow | OPC.MILLBHCAD_2:CALCA2.RO01 |  |  | 3 | ((( | ) + | T/H
22 | Disturbance Variable | Total Primary Air Flow | OPC.MILLBHCAD_2:CALCA3.RO01 |  |  | 4 | ( | )) / 2) + | T/H
23 | Disturbance Variable | Total Primary Air Flow | OPC.MILLCHCAD_2:CALCA2.RO01 |  |  | 5 | ((( | ) + | T/H
24 | Disturbance Variable | Total Primary Air Flow | OPC.MILLCHCAD_2:CALCA3.RO01 |  |  | 6 | ( | )) / 2) + | T/H
25 | Disturbance Variable | Total Primary Air Flow | OPC.MILLDHCAD_2:CALCA2.RO01 |  |  | 7 | ((( | ) + | T/H
26 | Disturbance Variable | Total Primary Air Flow | OPC.MILLDHCAD_2:CALCA3.RO01 |  |  | 8 | ( | )) / 2) + | T/H
27 | Disturbance Variable | Total Primary Air Flow | OPC.MILLEHCAD_2:CALCA2.RO01 |  |  | 9 | ((( | ) + | T/H
28 | Disturbance Variable | Total Primary Air Flow | OPC.MILLEHCAD_2:CALCA3.RO01 |  |  | 10 | ( | )) / 2)) | T/H
29 | Disturbance Variable | Total Secondary Air Flow | OPC.AIRFLOW_1:HLACFA1.PNT |  |  | 1 | (((( | ) + | T/H
30 | Disturbance Variable | Total Secondary Air Flow | OPC.AIRFLOW_1:HLACFA2.PNT |  |  | 2 | ( | )) / 2) + | T/H
31 | Disturbance Variable | Total Secondary Air Flow | OPC.AIRFLOW_2:HLACFB1.PNT |  |  | 3 | ((( | ) + | T/H
32 | Disturbance Variable | Total Secondary Air Flow | OPC.AIRFLOW_2:HLACFB2.PNT |  |  | 4 | ( | )) / 2)) | T/H
33 | Constrain Variable | Excess Oxygen Sensor | OPC.OXYGEN:SIGSEL1.OUT | 1.5 | 20 | 1 | ( | ) | %
34 | Constrain Variable | FD Fan A Blade Pos | OPC.2PDAS:ZT201104.PNT | 5 | 95 | 1 | ( | ) | %
35 | Constrain Variable | FD Fan A Motor Current | OPC.2MDAS:CT163205.PNT | 22 | 38 | 1 | ( | ) | A
36 | Constrain Variable | FD Fan B Blade Pos | OPC.2PDAS:ZT201204.PNT | 5 | 95 | 1 | ( | ) | %
37 | Constrain Variable | FD Fan B Motor Current | OPC.2NDAS:CT183205.PNT | 22 | 38 | 1 | ( | ) | A
38 | Constrain Variable | Furnace Pressure | OPC.FURPRESS:AINFURPRE.PNT | -2500 | 10 | 1 | ( | ) | Pa
39 | Constrain Variable | ID Fan A Blade Pos | OPC.2PDAS:ZT201107.PNT | 5 | 95 | 1 | ( | ) | %
40 | Constrain Variable | ID Fan A Motor Current | OPC.2MDAS:CT163207.PNT | 115 | 180 | 1 | ( | ) | A
41 | Constrain Variable | ID Fan B Blade Pos | OPC.2PDAS:ZT201207.PNT | 5 | 95 | 1 | ( | ) | %
42 | Constrain Variable | ID Fan B Motor Current | OPC.2NDAS:CT183207.PNT | 115 | 180 | 1 | ( | ) | A

## RBG2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG NAME | LOW LIMIT | HI LIMIT | SEQUENCE | BRACKET OPEN | BRACKET CLOSE | UNIT MEAS | NOTES
1 | Target Variable | Efficiency | Efficiency | 60 | 100 | 1 | ( | ) | %
2 | Manipulated Variable | All Wind | OPC.1AIRFLOW:MATH1.RO01 |  |  | 1 | ( | ) | % | Total airflow
3 | Manipulated Variable | Total Secondary Air Flow | OPC.1AIRFLOW_1:HLACFA1.PNT |  |  | 1 | (((( | ) + | T/H
4 | Manipulated Variable | Total Secondary Air Flow | OPC.1AIRFLOW_1:HLACFA2.PNT |  |  | 2 | ( | )) / 2) + | T/H
5 | Manipulated Variable | Total Secondary Air Flow | OPC.1AIRFLOW_2:HLACFB1.PNT |  |  | 3 | ((( | ) + | T/H
6 | Manipulated Variable | Total Secondary Air Flow | OPC.1AIRFLOW_2:HLACFB2.PNT |  |  | 4 | ( | )) / 2)) | T/H
7 | Manipulated Variable | Burner Tilt Position Lower | OPC.1QDAS:ZT210705.PNT |  |  | 1 | (( | ) + | %
8 | Manipulated Variable | Burner Tilt Position Lower | OPC.1QDAS:ZT210707.PNT |  |  | 2 | ( | ) + | %
9 | Manipulated Variable | Burner Tilt Position Lower | OPC.1QDAS:ZT210801.PNT |  |  | 3 | ( | ) + | %
10 | Manipulated Variable | Burner Tilt Position Lower | OPC.1QDAS:ZT210803.PNT |  |  | 4 | ( | )) / 4 | %
11 | Manipulated Variable | Burner Tilt Position Upper | OPC.1QDAS:ZT210706.PNT |  |  | 1 | (( | ) + | %
12 | Manipulated Variable | Burner Tilt Position Upper | OPC.1QDAS:ZT210708.PNT |  |  | 2 | ( | ) + | %
13 | Manipulated Variable | Burner Tilt Position Upper | OPC.1QDAS:ZT210802.PNT |  |  | 3 | ( | ) + | %
14 | Manipulated Variable | Burner Tilt Position Upper | OPC.1QDAS:ZT210804.PNT |  |  | 4 | ( | )) / 4 | %
15 | Manipulated Variable | Excess Oxygen Sensor | OPC.1OXYGEN:SIGSEL1.OUT | 1.5 | 20 | 1 | ( | ) | %
16 | Disturbance Variable | Coal Flow | OPC.1FUELMASTER:AINCOAL.PNT |  |  | 1 | ( | ) | T/H
17 | Disturbance Variable | Efficiency | Efficiency | 60 | 100 | 1 | ( | ) | %
18 | Disturbance Variable | Load | OPC.1SDAS:AI174108.PNT | 200 | 330 | 1 | ( | ) | MW
19 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLAHCAD_2:CALCA2.RO01 |  |  | 1 | (((( | ) + | T/H
20 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLAHCAD_2:CALCA3.RO01 |  |  | 2 | ( | )) / 2) + | T/H
21 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLBHCAD_2:CALCA2.RO01 |  |  | 3 | ((( | ) + | T/H
22 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLBHCAD_2:CALCA3.RO01 |  |  | 4 | ( | )) / 2) + | T/H
23 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLCHCAD_2:CALCA2.RO01 |  |  | 5 | ((( | ) + | T/H
24 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLCHCAD_2:CALCA3.RO01 |  |  | 6 | ( | )) / 2) + | T/H
25 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLDHCAD_2:CALCA2.RO01 |  |  | 7 | ((( | ) + | T/H
26 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLDHCAD_2:CALCA3.RO01 |  |  | 8 | ( | )) / 2) + | T/H
27 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLEHCAD_2:CALCA2.RO01 |  |  | 9 | ((( | ) + | T/H
28 | Disturbance Variable | Total Primary Air Flow | OPC.1MILLEHCAD_2:CALCA3.RO01 |  |  | 10 | ( | )) / 2)) | T/H
29 | Disturbance Variable | Total Secondary Air Flow | OPC.1AIRFLOW_1:HLACFA1.PNT |  |  | 1 | (((( | ) + | T/H
30 | Disturbance Variable | Total Secondary Air Flow | OPC.1AIRFLOW_1:HLACFA2.PNT |  |  | 2 | ( | )) / 2) + | T/H
31 | Disturbance Variable | Total Secondary Air Flow | OPC.1AIRFLOW_2:HLACFB1.PNT |  |  | 3 | ((( | ) + | T/H
32 | Disturbance Variable | Total Secondary Air Flow | OPC.1AIRFLOW_2:HLACFB2.PNT |  |  | 4 | ( | )) / 2)) | T/H
33 | Constrain Variable | Excess Oxygen Sensor | OPC.1OXYGEN:SIGSEL1.OUT | 1.5 | 20 | 1 | ( | ) | %
34 | Constrain Variable | FD Fan A Blade Pos | OPC.1PDAS:ZT201104.PNT | 5 | 95 | 1 | ( | ) | %
35 | Constrain Variable | FD Fan A Motor Current | OPC.1MDAS:CT163205.PNT | 22 | 38 | 1 | ( | ) | A
36 | Constrain Variable | FD Fan B Blade Pos | OPC.1PDAS:ZT201204.PNT | 5 | 95 | 1 | ( | ) | %
37 | Constrain Variable | FD Fan B Motor Current | OPC.1NDAS:CT183205.PNT | 22 | 38 | 1 | ( | ) | A
38 | Constrain Variable | Furnace Pressure | OPC.1FURPRESS:AINFURPRE.PNT | -2500 | 10 | 1 | ( | ) | Pa
39 | Constrain Variable | ID Fan A Blade Pos | OPC.1PDAS:ZT201107.PNT | 5 | 95 | 1 | ( | ) | %
40 | Constrain Variable | ID Fan A Motor Current | OPC.1MDAS:CT163207.PNT | 115 | 180 | 1 | ( | ) | A
41 | Constrain Variable | ID Fan B Blade Pos | OPC.1PDAS:ZT201207.PNT | 5 | 95 | 1 | ( | ) | %
42 | Constrain Variable | ID Fan B Motor Current | OPC.1NDAS:CT183207.PNT | 115 | 180 | 1 | ( | ) | A

## UJRBG10 (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS
1137 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.1IDAS:LT120103.PNT | 1IDAS:LT120103.PNT | 10MAG10CL201 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
1145 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.1IDAS:LT120203.PNT | 1IDAS:LT120203.PNT | 10MAG10CL202 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
1153 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.1IDAS:LT120303.PNT | 1IDAS:LT120303.PNT | 10MAG10CL203 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
539 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:AI113307.PNT | 1HDAS:AI113307.PNT | 10PAH11GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM A SIDE DIFF.PRESS | AI | -1 | 9
540 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:AI113308.PNT | 1HDAS:AI113308.PNT | 10PAH12GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM B SIDE DIFF.PRESS | AI | -1 | 9
533 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:PT113301.PNT | 1HDAS:PT113301.PNT | 10PAH21CP201 | CONDENSER SIDE A CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa
741 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:RT113401.PNT | 1HDAS:RT113401.PNT | 10PAH21CT001 | CONDENSER SIDE A CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | °C
535 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:PT113303.PNT | 1HDAS:PT113303.PNT | 10PAH22CP201 | CONDENSER SIDE B CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa
743 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:RT113403.PNT | 1HDAS:RT113403.PNT | 10PAH22CT001 | CONDENSER SIDE B CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | °C
537 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:ZT113305.PNT | 1HDAS:ZT113305.PNT | 10PAH31AA001XB12 | CONDENSER A SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITIO | AI | 0 | 100 | %
534 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:PT113302.PNT | 1HDAS:PT113302.PNT | 10PAH31CP201 | CONDENSER SIDE A CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa
742 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:RT113402.PNT | 1HDAS:RT113402.PNT | 10PAH31CT001 | CONDENSER SIDE A CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | °C
538 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:ZT113306.PNT | 1HDAS:ZT113306.PNT | 10PAH32AA001XB12 | CONDENSER B SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITIO | AI | 0 | 100 | %
536 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:PT113304.PNT | 1HDAS:PT113304.PNT | 10PAH32CP201 | CONDENSER SIDE B CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa
744 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.1HDAS:RT113404.PNT | 1HDAS:RT113404.PNT | 10PAH32CT001 | CONDENSER SIDE B CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | °C
744 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #10 (CONDENSING SYSTEM/CONDENSER) |  | OPC.1VALVE:1AD106AIN.PNT_3 | 1VALVE:1AD106AIN.PNT_3 | 10MAG10CP201 | #10 COND VACUUM | AI | 103 | -103 | kPa |  | -80 | -85
607 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053805.PNT | 1EDAS:RT053805.PNT | 10LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 100 | °C
358 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:PT050508.PNT | 1EDAS:PT050508.PNT | 10LCA12CP201 | CONDENSATE PUMP A OUTLET PRESS | AI | 0 | 4 | MPa
368 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:PT050702.PNT | 1EDAS:PT050702.PNT | 10LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa
375 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50- | OPC.1EDAS:ZT050801.PNT | 1EDAS:ZT050801.PNT | 10LCB12AP001XB13 | CONDENSER PUMP A CURRENT | AI | 0 | 100 | %
579 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053404.PNT | 1EDAS:RT053404.PNT | 10LCB12CT001 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
586 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053504.PNT | 1EDAS:RT053504.PNT | 10LCB12CT002 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
580 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053405.PNT | 1EDAS:RT053405.PNT | 10LCB12CT003 | CONDENSATE PUMP A MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
587 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053505.PNT | 1EDAS:RT053505.PNT | 10LCB12CT004 | CONDENSATE PUMP A MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
576 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053401.PNT | 1EDAS:RT053401.PNT | 10LCB12CT005 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
583 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053501.PNT | 1EDAS:RT053501.PNT | 10LCB12CT006 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
577 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053402.PNT | 1EDAS:RT053402.PNT | 10LCB12CT007 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
584 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053502.PNT | 1EDAS:RT053502.PNT | 10LCB12CT008 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
578 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053403.PNT | 1EDAS:RT053403.PNT | 10LCB12CT009 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
585 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053503.PNT | 1EDAS:RT053503.PNT | 10LCB12CT010 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
585 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM |  | OPC.1VMS2:AIN1.PNT | 1VMS2:AIN1.PNT | 10LCB12CY201X | #10 CEP A DRIVE END VIB X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
585 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 2 | MAIN CONDESATE A PUMP SYSTEM |  | OPC.1VMS2:AIN2.PNT | 1VMS2:AIN2.PNT | 10LCB12CY201Y | #10 CEP A DRIVE END VIB Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
366 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:PT050608.PNT | 1EDAS:PT050608.PNT | 10LCA13CP201 | CONDENSATE PUMP B OUTLET PRESS | AI | 0 | 4 | MPa
376 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50- | OPC.1EDAS:ZT050802.PNT | 1EDAS:ZT050802.PNT | 10LCB13AP001XB13 | CONDENSER PUMP B CURRENT | AI | 0 | 100 | %
593 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053604.PNT | 1EDAS:RT053604.PNT | 10LCB13CT001 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
600 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053704.PNT | 1EDAS:RT053704.PNT | 10LCB13CT002 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
594 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053605.PNT | 1EDAS:RT053605.PNT | 10LCB13CT003 | CONDENSATE PUMP B MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
601 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053705.PNT | 1EDAS:RT053705.PNT | 10LCB13CT004 | CONDENSATE PUMP B MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
590 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053601.PNT | 1EDAS:RT053601.PNT | 10LCB13CT005 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
597 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053701.PNT | 1EDAS:RT053701.PNT | 10LCB13CT006 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
591 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053602.PNT | 1EDAS:RT053602.PNT | 10LCB13CT007 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
598 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053702.PNT | 1EDAS:RT053702.PNT | 10LCB13CT008 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
592 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053603.PNT | 1EDAS:RT053603.PNT | 10LCB13CT009 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
599 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.1EDAS:RT053703.PNT | 1EDAS:RT053703.PNT | 10LCB13CT010 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
599 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM |  | OPC.1VMS2:AIN3.PNT | 1VMS2:AIN3.PNT | 10LCB13CY201X | #10 CEP B DRIVE END VIB X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
599 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 3 | MAIN CONDESATE B PUMP SYSTEM |  | OPC.1VMS2:AIN4.PNT | 1VMS2:AIN4.PNT | 10LCB13CY201Y | #10 CEP B DRIVE END VIB Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
493 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:CT092701.PNT | 1GDAS:CT092701.PNT | 10MAJ21AP001XB13 | VACUUM PUMP A CURRENT | AI | 0 | 100 | %
705 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093501.PNT | 1GDAS:RT093501.PNT | 10MAJ21CT001 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
713 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093601.PNT | 1GDAS:RT093601.PNT | 10MAJ21CT002 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
706 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093502.PNT | 1GDAS:RT093502.PNT | 10MAJ21CT003 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
714 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093602.PNT | 1GDAS:RT093602.PNT | 10MAJ21CT004 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
707 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093503.PNT | 1GDAS:RT093503.PNT | 10MAJ21CT005 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
715 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093603.PNT | 1GDAS:RT093603.PNT | 10MAJ21CT006 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
708 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093504.PNT | 1GDAS:RT093504.PNT | 10MAJ21CT007 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
716 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-15 | OPC.1GDAS:RT093604.PNT | 1GDAS:RT093604.PNT | 10MAJ21CT008 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
655 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 4 | VACUUM PUMP 10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067707.PNT | 1EDAS:RT067707.PNT | 10PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 50 | °C
709 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093505.PNT | 1GDAS:RT093505.PNT | 10MAJ21CT009 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
717 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093605.PNT | 1GDAS:RT093605.PNT | 10MAJ21CT010 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
710 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093506.PNT | 1GDAS:RT093506.PNT | 10MAJ21CT011 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
718 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093606.PNT | 1GDAS:RT093606.PNT | 10MAJ21CT012 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
711 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093507.PNT | 1GDAS:RT093507.PNT | 10MAJ21CT013 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
719 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093607.PNT | 1GDAS:RT093607.PNT | 10MAJ21CT014 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
712 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093508.PNT | 1GDAS:RT093508.PNT | 10MAJ21CT015 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
720 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:RT093608.PNT | 1GDAS:RT093608.PNT | 10MAJ21CT016 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
494 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 5 | VACUUM PUMP 10B | 50-F290S-J0201-15 | OPC.1GDAS:CT092702.PNT | 1GDAS:CT092702.PNT | 10MAJ22AP001XB13 | VACUUM PUMP B CURRENT | AI | 0 | 100 | %
410 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #10 | 50-F290S-J0201-10 | OPC.1FDAS:CT073103.PNT | 1FDAS:CT073103.PNT | 10LBW20AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN A CURRENT | AI | 0 | 100 | %
411 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #10 | 50-F290S-J0201-10 | OPC.1FDAS:CT073104.PNT | 1FDAS:CT073104.PNT | 10LBW21AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN B CURRENT | AI | 0 | 100 | %
581 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053406.PNT | 1EDAS:RT053406.PNT | 10LCA10CT001 | GLAND STEAM CONDENSER INLET TEMP | RTD | 0 | 100 | °C
582 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053407.PNT | 1EDAS:RT053407.PNT | 10LCA10CT002 | GLAND STEAM CONDENSER OUTLET MAIN PIPE TEMP | RTD | 0 | 100 | °C
462 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086504.PNT | 1FDAS:PT086504.PNT | 10LBS80CP201 | #8 EXTRACTION STEAM PRESS(LEFT) | AI | 0 | 0.1 | MPa
467 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086602.PNT | 1FDAS:PT086602.PNT | 10LBS80CP202 | #8 EXTRACTION STEAM PRESS(RIGHT) | AI | 0 | 0.1 | MPa
771 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087308.PNT | 1FDAS:TE087308.PNT | 10LBS80CT001 | #8 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 150 | °C
775 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087404.PNT | 1FDAS:TE087404.PNT | 10LBS80CT002 | #8 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 150 | °C
369 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-07 | OPC.1EDAS:PT050703.PNT | 1EDAS:PT050703.PNT | 10LCA10CP201 | #8 LP HEATER INLET PRESS | AI | 0 | 4 | MPa
588 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053506.PNT | 1EDAS:RT053506.PNT | 10LCA10CT003 | #8 LP HEATER INLET WATER TEMP | RTD | 0 | 100 | °C
1161 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120403.PNT | 1IDAS:LT120403.PNT | 10LCC80CL201 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1168 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120503.PNT | 1IDAS:LT120503.PNT | 10LCC80CL202 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1176 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120603.PNT | 1IDAS:LT120603.PNT | 10LCC80CL203 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1253 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP8LVL:AO122505.OUT | 1LP8LVL:AO122505.OUT | 10LCJ80AA101XB11 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1212 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121305.PNT | 1IDAS:ZT121305.PNT | 10LCJ80AA101XB12 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
606 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1EDAS:RT053804.PNT | 1EDAS:RT053804.PNT | 10LCJ80CT001 | #8 LP HEATER DRAIN WATER TEMP | RTD | 0 | 50 | °C
1254 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP8LVL:AO122506.OUT | 1LP8LVL:AO122506.OUT | 10LCJ81AA101XB11 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1213 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 9 | LP FEED WATER HEATER 8 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121306.PNT | 1IDAS:ZT121306.PNT | 10LCJ81AA101XB12 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
461 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086503.PNT | 1FDAS:PT086503.PNT | 10LBS70CP201 | #7 EXTRACTION STEAM PRESS(LEFT) | AI | 0 | 0.15 | MPa
466 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086601.PNT | 1FDAS:PT086601.PNT | 10LBS70CP202 | #7 EXTRACTION STEAM PRESS(RIGHT) | AI | 0 | 0.15 | MPa
770 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087307.PNT | 1FDAS:TE087307.PNT | 10LBS70CT001 | #7 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 200 | °C
774 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087403.PNT | 1FDAS:TE087403.PNT | 10LBS70CT002 | #7 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 200 | °C
589 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053507.PNT | 1EDAS:RT053507.PNT | 10LCA20CT001 | #7 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1160 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120402.PNT | 1IDAS:LT120402.PNT | 10LCC70CL201 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1167 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120502.PNT | 1IDAS:LT120502.PNT | 10LCC70CL202 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1175 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120602.PNT | 1IDAS:LT120602.PNT | 10LCC70CL203 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1251 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP7LVL:AO122503.OUT | 1LP7LVL:AO122503.OUT | 10LCJ70AA101XB11 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1210 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121303.PNT | 1IDAS:ZT121303.PNT | 10LCJ70AA101XB12 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
605 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1EDAS:RT053803.PNT | 1EDAS:RT053803.PNT | 10LCJ70CT001 | #7 LP HEATER DRAIN WATER TEMP | RTD | 0 | 100 | °C
1252 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP7LVL:AO122504.OUT | 1LP7LVL:AO122504.OUT | 10LCJ71AA101XB11 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1211 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 10 | LP FEED WATER HEATER 7 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121304.PNT | 1IDAS:ZT121304.PNT | 10LCJ71AA101XB12 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
460 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086502.PNT | 1FDAS:PT086502.PNT | 10LBS60CP201 | #6 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.4 | MPa
505 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104106.PNT | 1GDAS:PT104106.PNT | 10LBS60CP202 | #6 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.4 | MPa
767 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087304.PNT | 1FDAS:TE087304.PNT | 10LBS60CT001 | #6 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 250 | °C
768 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087305.PNT | 1FDAS:TE087305.PNT | 10LBS60CT002 | #6 EXTRACTION PIPE TOP TEMP | TC | 0 | 250 | °C
769 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087306.PNT | 1FDAS:TE087306.PNT | 10LBS60CT003 | #6 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 250 | °C
825 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107402.PNT | 1GDAS:TE107402.PNT | 10LBS60CT004 | #6 EXTRACTION STEAM TEMP (LP HEATER SIDE) | TC | 0 | 250 | °C
595 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053606.PNT | 1EDAS:RT053606.PNT | 10LCA30CT001 | #6 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1159 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120401.PNT | 1IDAS:LT120401.PNT | 10LCC60CL201 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1166 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120501.PNT | 1IDAS:LT120501.PNT | 10LCC60CL202 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1174 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120601.PNT | 1IDAS:LT120601.PNT | 10LCC60CL203 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1249 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP6LVL:AO122501.OUT | 1LP6LVL:AO122501.OUT | 10LCJ60AA101XB11 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1208 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121301.PNT | 1IDAS:ZT121301.PNT | 10LCJ60AA101XB12 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
604 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1EDAS:RT053802.PNT | 1EDAS:RT053802.PNT | 10LCJ60CT001 | #6 LP HEATER DRAIN WATER TEMP | RTD | 0 | 110 | °C
1250 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP6LVL:AO122502.OUT | 1LP6LVL:AO122502.OUT | 10LCJ61AA101XB11 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1209 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 12 | LP FEED WATER HEATER 6 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121302.PNT | 1IDAS:ZT121302.PNT | 10LCJ61AA101XB12 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
459 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086501.PNT | 1FDAS:PT086501.PNT | 10LBS50CP201 | #5 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.6 | MPa
504 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104105.PNT | 1GDAS:PT104105.PNT | 10LBS50CP202 | #5 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.6 | MPa
764 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087301.PNT | 1FDAS:TE087301.PNT | 10LBS50CT001 | #5 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 300 | °C
765 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087302.PNT | 1FDAS:TE087302.PNT | 10LBS50CT002 | #5 EXTRACTION PIPE TOP TEMP | TC | 0 | 300 | °C
766 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087303.PNT | 1FDAS:TE087303.PNT | 10LBS50CT003 | #5 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 300 | °C
824 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107401.PNT | 1GDAS:TE107401.PNT | 10LBS50CT004 | #5 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 300 | °C
596 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053607.PNT | 1EDAS:RT053607.PNT | 10LCA40CT001 | #5 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1142 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120108.PNT | 1IDAS:LT120108.PNT | 10LCC50CL201 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1150 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120208.PNT | 1IDAS:LT120208.PNT | 10LCC50CL202 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1158 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:LT120308.PNT | 1IDAS:LT120308.PNT | 10LCC50CL203 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1247 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP5LVL:AO122406.OUT | 1LP5LVL:AO122406.OUT | 10LCJ50AA101XB11 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1206 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121206.PNT | 1IDAS:ZT121206.PNT | 10LCJ50AA101XB12 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
603 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1EDAS:RT053801.PNT | 1EDAS:RT053801.PNT | 10LCJ50CT001 | #5 LP HEATER DRAIN WATER TEMP | RTD | 0 | 150 | °C
1248 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1LP5LVL:AO122407.OUT | 1LP5LVL:AO122407.OUT | 10LCJ51AA101XB11 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1207 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 14 | LP FEED WATER HEATER 5 #10 | 50-F290S-J0201-09(2/2) | OPC.1IDAS:ZT121207.PNT | 1IDAS:ZT121207.PNT | 10LCJ51AA101XB12 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
541 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50- | OPC.1GHH:AO092801.OUT | 1GHH:AO092801.OUT | 10LAA40AA501XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
491 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-09(1/2) | OPC.1GDAS:ZT092606.PNT | 1GDAS:ZT092606.PNT | 10LAA40AA501XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | %
542 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50- | OPC.1GHH:AO092802.OUT | 1GHH:AO092802.OUT | 10LAA40AA502XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
495 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50- | OPC.1GDAS:ZT092703.PNT | 1GDAS:ZT092703.PNT | 10LAA40AA502XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 101 | %
543 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50- | OPC.1GHH:AO092803.OUT | 1GHH:AO092803.OUT | 10LAA40AA503XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 3 CONTROL COMMAND | AO | 0 | 100 | %
496 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50- | OPC.1GDAS:ZT092704.PNT | 1GDAS:ZT092704.PNT | 10LAA40AA503XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 3 POSITION | AI | 0 | 102 | %
1138 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1IDAS:LT120104.PNT | 1IDAS:LT120104.PNT | 10LAA40CL201 | DEAERATOR TANK LEVEL | AI | -1950 | 550 | mm |  |  | -200 | 200
1146 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1IDAS:LT120204.PNT | 1IDAS:LT120204.PNT | 10LAA40CL202 | DEAERATOR TANK LEVEL | AI | -195 | 550 | mm |  |  | -200 | 200
1154 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1IDAS:LT120304.PNT | 1IDAS:LT120304.PNT | 10LAA40CL203 | DEAERATOR TANK LEVEL | AI | -195 | 550 | mm |  |  | -200 | 200
602 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1EDAS:RT053706.PNT | 1EDAS:RT053706.PNT | 10LAA40CT001 | DEAERATOR TANK TEMP | RTD | 0 | 200 | °C
473 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:ZT086701.PNT | 1FDAS:ZT086701.PNT | 10LBS40AA005XB12 | AUXILIARY STEAM HEADER TO DEAERATOR INCHING MOTORIZED VALVE POSITI | AI | 0 | 100 | %
455 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086404.PNT | 1FDAS:PT086404.PNT | 10LBS40CP201 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (TURBINE SIDE) | AI | 0 | 1 | MPa
463 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086505.PNT | 1FDAS:PT086505.PNT | 10LBS40CP202 | #4 EXTRACTION STEAM PIPE 1 PRESS 2 (TURBINE SIDE) | AI | 0 | 1 | MPa
1181 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1IDAS:PT120701.PNT | 1IDAS:PT120701.PNT | 10LBS40CP203 | DEAERATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa
1186 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1IDAS:PT120801.PNT | 1IDAS:PT120801.PNT | 10LBS40CP204 | DEAERATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa
503 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104104.PNT | 1GDAS:PT104104.PNT | 10LBS40CP205 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (DEAERATOR SIDE) | AI | 0 | 1 | MPa
761 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087204.PNT | 1FDAS:TE087204.PNT | 10LBS40CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 400 | °C
762 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087205.PNT | 1FDAS:TE087205.PNT | 10LBS40CT002 | #4 EXTRACTION STEAM PIPE 1 TOP TEMP | TC | 0 | 400 | °C
756 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087107.PNT | 1FDAS:TE087107.PNT | 10LBS40CT003 | #4 EXTRACTION STEAM PIPE 1 BOTTOM TEMP | TC | 0 | 400 | °C
822 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107306.PNT | 1GDAS:TE107306.PNT | 10LBS40CT004 | #4 EXTRACTION STEAM PIPE 1 TEMP (DEAERATOR SIDE) | TC | 0 | 400 | °C
474 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-05 | OPC.1FDAS:ZT086702.PNT | 1FDAS:ZT086702.PNT | 10LBS43AA001XB12 | OPEN #4 EXTRACTION STEAM PIPE TO DEAERATOR INCHING MOTORIZED VALVE | AI | 0 | 100 | %
373 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1EDAS:ZT050707.PNT | 1EDAS:ZT050707.PNT | 10LCA10AA004XB12 | DEAERATOR LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | %
1224 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1DALVL:AO122103.OUT | 1DALVL:AO122103.OUT | 10LCA10AA101XB11 | DEAERATOR WATER LEVEL CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1172 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120507.PNT | 1IDAS:ZT120507.PNT | 10LCA10AA101XB12 | DEAERATOR WATER LEVEL CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1230 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1DALVL:AO122203.OUT | 1DALVL:AO122203.OUT | 10LCA10AA102XB11 | DEAERATOR WATER LEVEL CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1173 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #10 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120508.PNT | 1IDAS:ZT120508.PNT | 10LCA10AA102XB12 | DEAERATOR WATER LEVEL CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
1182 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1IDAS:FT120702.PNT | 1IDAS:FT120702.PNT | 10LCA40CF201 | CONDENSATE WATER FLOW | AI | 0 | 1000 | T/H
1187 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1IDAS:FT120802.PNT | 1IDAS:FT120802.PNT | 10LCA40CF202 | CONDENSATE WATER FLOW | AI | 0 | 1000 | T/H
372 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1EDAS:ZT050706.PNT | 1EDAS:ZT050706.PNT | 10LCA42AA001XB12 | OPEN CONDENSATE RECIRCULATING CONTROL VALVE BYPASS MOTORIZED VALV | AI | 0 | 100 | %
1228 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1CNREC:AO122107.OUT | 1CNREC:AO122107.OUT | 10LCA42AA101XB11 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1171 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120506.PNT | 1IDAS:ZT120506.PNT | 10LCA42AA101XB12 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE POSITION | AI | 0 | 100 | %
1165 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | 50-F290S-J0201-07 | OPC.1IDAS:FT120407.PNT | 1IDAS:FT120407.PNT | 10LCA42CF201 | CONDENSATE WATER RECIRCULATING FLOW | AI | 0 | 1000 | T/H
1227 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1CNMKUP:AO122106.OUT | 1CNMKUP:AO122106.OUT | 10LCA21AA101XB91 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE CONTROL COMM | AO | 0 | 100 | %
1170 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1IDAS:ZT120505.PNT | 1IDAS:ZT120505.PNT | 10LCA21AA101XB92 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | %
1235 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1CNMKUP:AO122301.OUT | 1CNMKUP:AO122301.OUT | 10LCD10AA101XB11 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1193 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1IDAS:ZT121101.PNT | 1IDAS:ZT121101.PNT | 10LCD10AA101XB12 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1236 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1CNLVL:AO122302.OUT | 1CNLVL:AO122302.OUT | 10LCP10AA101XB11 | CONDENSER WATER LEVEL CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1194 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1IDAS:ZT121102.PNT | 1IDAS:ZT121102.PNT | 10LCP10AA101XB12 | SHUI | AI | 0 | 100 | %
367 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1EDAS:CT050701.PNT | 1EDAS:CT050701.PNT | 10LCP10AP001XB13 | CONDENSATE MAKE-UP WATER PUMP CURRENT | AI | 0 | 100 | %
371 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1EDAS:FT050705.PNT | 1EDAS:FT050705.PNT | 10LCP10CF201 | CONDENSATE MAKE-UP WATER FLOW | AI | 0 | 80 | T/H
1169 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1IDAS:LT120504.PNT | 1IDAS:LT120504.PNT | 10LCP10CL201 | CONDENSATE MAKE-UP TANK LEVEL | AI | 0 | 4500 | mm
370 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1EDAS:PT050704.PNT | 1EDAS:PT050704.PNT | 10LCP10CP201 | CONDENSATE MAKE-UP WATER PUMP OUTLET PRESS | AI | 0 | 2.5 | MPa
374 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1EDAS:ZT050708.PNT | 1EDAS:ZT050708.PNT | 10LCP11AA001XB12 | CONDENSER WATER LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITI | AI | 0 | 100 | %
365 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.1EDAS:CT050607.PNT | 1EDAS:CT050607.PNT | 10LCP20AP001XB13 | BOILER FEEDWATER PUMP CURRENT | AI | 0 | 100 | %
544 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50- | OPC.1GDAS:AO092804.OUT | 1GDAS:AO092804.OUT | 10LCE14AA001XB11 | DRAIN FLASH TANK ? DESUPERHEATING WATER VALVE CONTROL | AO | 0 | 100 | %
545 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50- | OPC.1GDAS:AO092805.OUT | 1GDAS:AO092805.OUT | 10LCE19AA001XB11 | DRAIN FLASH TANK?DESUPERHEATING WATER VALVE CONTROL | AO | 0 | 100 | %
826 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113501.PNT | 1HDAS:TE113501.PNT | 10LCT10CT001 | NO.1 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 560 | °C
827 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113502.PNT | 1HDAS:TE113502.PNT | 10LCT10CT002 | NO.2 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 560 | °C
828 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113503.PNT | 1HDAS:TE113503.PNT | 10LCT10CT003 | NO.3 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 420 | °C
829 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113504.PNT | 1HDAS:TE113504.PNT | 10LCT10CT004 | NO.4 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 550 | °C
830 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113505.PNT | 1HDAS:TE113505.PNT | 10LCT10CT005 | NO.5 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 360 | °C
831 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113506.PNT | 1HDAS:TE113506.PNT | 10LCT10CT006 | NO.6 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 100 | °C
832 | 2 | UJRBG #10 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | 50-F290S-J0201-12 | OPC.1HDAS:TE113507.PNT | 1HDAS:TE113507.PNT | 10LCT10CT007 | NO.7 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 360 | °C
400 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 1 | CIRCULATING-WATER BOOSTER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:PT066701.PNT | 1EDAS:PT066701.PNT | 10PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.25 | MPa
654 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 1 | CIRCULATING-WATER BOOSTER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067706.PNT | 1EDAS:RT067706.PNT | 10PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 50 | °C
390 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 1 | CIRCULATING-WATER BOOSTER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:CT064705.PNT | 1EDAS:CT064705.PNT | 10PCC21AP001XB13 | CIRCULATING-WATER BOOSTER PUMP A CURRENT | AI | 0 | 100 | %
397 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 2 | CIRCULATING-WATER BOOSTER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:CT064805.PNT | 1EDAS:CT064805.PNT | 10PCC22AP001XB13 | CIRCULATING-WATER BOOSTER PUMP B CURRENT | AI | 0 | 100 | %
387 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 10A | 50-F290S-J0201-14 | OPC.1EDAS:ZT064702.PNT | 1EDAS:ZT064702.PNT | 10PCB31AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A SEA WATER SIDE OUTL | AI | 0 | 100 | %
388 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 10A | 50-F290S-J0201-14 | OPC.1EDAS:ZT064703.PNT | 1EDAS:ZT064703.PNT | 10PGA21AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A COOLING WATER INLET | AI | 0 | 100 | %
386 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 10A | 50-F290S-J0201-14 | OPC.1EDAS:PT064701.PNT | 1EDAS:PT064701.PNT | 10PGA21CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET PRESS | AI | 0 | 0.8 | MPa
633 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067406.PNT | 1EDAS:RT067406.PNT | 10PGA21CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET TEMP | RTD | 0 | 50 | °C
394 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 10B | 50-F290S-J0201-14 | OPC.1EDAS:ZT064802.PNT | 1EDAS:ZT064802.PNT | 10PCB32AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B SEA WATER SIDE OUTL | AI | 0 | 100 | %
395 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 10B | 50-F290S-J0201-14 | OPC.1EDAS:ZT064803.PNT | 1EDAS:ZT064803.PNT | 10PGA22AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B COOLING WATER INLET | AI | 0 | 100 | %
393 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 10B | 50-F290S-J0201-14 | OPC.1EDAS:PT064801.PNT | 1EDAS:PT064801.PNT | 10PGA22CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET PRESS | AI | 0 | 0.8 | MPa
640 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067506.PNT | 1EDAS:RT067506.PNT | 10PGA22CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET TEMP | RTD | 0 | 50 | °C
405 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:ZT066706.PNT | 1EDAS:ZT066706.PNT | 10PGA11AA001XB12 | CLOSED CIRCULATING-WATER PUMP A OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | %
391 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:CT064706.PNT | 1EDAS:CT064706.PNT | 10PGA11AP001XB13 | CLOSED CIRCULATING-WATER PUMP A CURRENT | AI | 0 | 100 | %
631 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067404.PNT | 1EDAS:RT067404.PNT | 10PGA11CT001 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
638 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067504.PNT | 1EDAS:RT067504.PNT | 10PGA11CT002 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
632 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067405.PNT | 1EDAS:RT067405.PNT | 10PGA11CT003 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
639 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067505.PNT | 1EDAS:RT067505.PNT | 10PGA11CT004 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
628 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067401.PNT | 1EDAS:RT067401.PNT | 10PGA11CT005 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
635 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067501.PNT | 1EDAS:RT067501.PNT | 10PGA11CT006 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
629 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067402.PNT | 1EDAS:RT067402.PNT | 10PGA11CT007 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
636 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067502.PNT | 1EDAS:RT067502.PNT | 10PGA11CT008 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
630 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067403.PNT | 1EDAS:RT067403.PNT | 10PGA11CT009 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
637 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067503.PNT | 1EDAS:RT067503.PNT | 10PGA11CT010 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
401 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CLOSED CIRCULATING-WATER PUMP #10A | 50-F290S-J0201-14 | OPC.1EDAS:PT066702.PNT | 1EDAS:PT066702.PNT | 10PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 1.6 | MPa
398 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:CT064806.PNT | 1EDAS:CT064806.PNT | 10PGA12AP001XB13 | CLOSED CIRCULATING-WATER PUMP B CURRENT | AI | 0 | 100 | %
645 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067604.PNT | 1EDAS:RT067604.PNT | 10PGA12CT001 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
652 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067704.PNT | 1EDAS:RT067704.PNT | 10PGA12CT002 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
646 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067605.PNT | 1EDAS:RT067605.PNT | 10PGA12CT003 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
653 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067705.PNT | 1EDAS:RT067705.PNT | 10PGA12CT004 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
642 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067601.PNT | 1EDAS:RT067601.PNT | 10PGA12CT005 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
649 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067701.PNT | 1EDAS:RT067701.PNT | 10PGA12CT006 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
643 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067602.PNT | 1EDAS:RT067602.PNT | 10PGA12CT007 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
650 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067702.PNT | 1EDAS:RT067702.PNT | 10PGA12CT008 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
644 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067603.PNT | 1EDAS:RT067603.PNT | 10PGA12CT009 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
651 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CLOSED CIRCULATING-WATER PUMP #10B | 50-F290S-J0201-14 | OPC.1EDAS:RT067703.PNT | 1EDAS:RT067703.PNT | 10PGA12CT010 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
389 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:ZT064704.PNT | 1EDAS:ZT064704.PNT | 10PGA31AA002XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | %
403 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:PT066704.PNT | 1EDAS:PT066704.PNT | 10PGA31CP201 | BOOSTER PUMP FOR T-BFP DRIVEN BOILER FEED WATER PUMP BEARING COOL | AI | 0 | 0.8 | MPa
647 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067606.PNT | 1EDAS:RT067606.PNT | 10PGA31CT001 | TURBINE HOUSE COOLING WATER INLET TEMP | RTD | 0 | 50 | °C
634 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067407.PNT | 1EDAS:RT067407.PNT | 10PGA31CT002 | TURBINE HOUSER COOLING RETURN WATER TEMP 1 | RTD | 0 | 50 | °C
641 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067507.PNT | 1EDAS:RT067507.PNT | 10PGA31CT004 | TURBINE HOUSER COOLING RETURN WATER TEMP 2 | RTD | 0 | 50 | °C
396 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:ZT064804.PNT | 1EDAS:ZT064804.PNT | 10PGA33AA001XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | %
402 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:PT066703.PNT | 1EDAS:PT066703.PNT | 10PGA40CP201 | FUEL OIL COOLER INLET PRESS | AI | 0 | 0.8 | MPa
656 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067801.PNT | 1EDAS:RT067801.PNT | 10PGA40CT001 | BOILER HOUSE COOLING WATER MAIN PIPE INLET TEMP | RTD | 0 | 50 | °C
392 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:ZT064707.PNT | 1EDAS:ZT064707.PNT | 10PGA50AA001XB12 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE MOTORIZED VALVE POSIT | AI | 0 | 100 | %
657 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067802.PNT | 1EDAS:RT067802.PNT | 10PGA50CT001 | BOILER HOUSE COOLING RENTURN WATER TEMP | RTD | 0 | 50 | °C
658 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | 50-F290S-J0201-14 | OPC.1EDAS:RT067803.PNT | 1EDAS:RT067803.PNT | 10PGA50CT002 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE TEMP | RTD | 0 | 50 | °C
1234 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | 50-F290S-J0201-07 | OPC.1CWEXTNK:AO122207.OUT | 1CWEXTNK:AO122207.OUT | 10LCE18AA101XB11 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER | AO | 0 | 100 | %
1180 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120607.PNT | 1IDAS:ZT120607.PNT | 10LCE18AA101XB12 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER | AI | 0 | 100 | %
404 | 2 | UJRBG #10 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | 50-F290S-J0201-14 | OPC.1EDAS:LT066705.PNT | 1EDAS:LT066705.PNT | 10PGA10CL201 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK LEVEL | AI | 0 | 2.5 | m
353 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50-F290S-J0201-08 | OPC.1EDAS:CT050503.PNT | 1EDAS:CT050503.PNT | 10LAC11AP001XB13 | BOOSTER PUMP FOR T-BFP A CURRENT | AI | 0 | 100 | %
556 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50-F290S-K0301-05 | OPC.1EDAS:RT053101.PNT | 1EDAS:RT053101.PNT | 10LAC11CT001 | BOOSTER PUMP FOR T-BFP A DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
557 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50-F290S-K0301-05 | OPC.1EDAS:RT053102.PNT | 1EDAS:RT053102.PNT | 10LAC11CT002 | BOOSTER PUMP FOR T-BFP A FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
721 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093701.PNT | 1GDAS:RT093701.PNT | 10LAC11CT013 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 1 | RTD | 0 | 100 | °C
722 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093702.PNT | 1GDAS:RT093702.PNT | 10LAC11CT014 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 2 | RTD | 0 | 100 | °C
723 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093703.PNT | 1GDAS:RT093703.PNT | 10LAC11CT015 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 3 | RTD | 0 | 100 | °C
724 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093704.PNT | 1GDAS:RT093704.PNT | 10LAC11CT016 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 4 | RTD | 0 | 100 | °C
725 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093705.PNT | 1GDAS:RT093705.PNT | 10LAC11CT017 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 5 | RTD | 0 | 100 | °C
726 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093706.PNT | 1GDAS:RT093706.PNT | 10LAC11CT018 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 6 | RTD | 0 | 100 | °C
727 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093707.PNT | 1GDAS:RT093707.PNT | 10LAC11CT019 | MOTOR OF BOOSTER PUMP FOR T-BFP A BEARING TEMP 1 | RTD | 0 | 100 | °C
728 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #10A - BOOSTER PUMP | 50- | OPC.1GDAS:RT093708.PNT | 1GDAS:RT093708.PNT | 10LAC11CT020 | MOTOR OF BOOSTER PUMP FOR T-BFP A BEARING TEMP 2 | RTD | 0 | 100 | °C
406 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50- | OPC.1FDAS:CT072801.PNT | 1FDAS:CT072801.PNT | 10MAV50GC001AI01 | BFP TURBINE A TURNING GEAR MOTOR CURRENT | AI | 0 | 50 | A
1223 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-08 | OPC.1TFPAREC:AO122101.OUT | 1TFPAREC:AO122101.OUT | 10LAB11AA101XB11 | T-BFP A MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1184 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-08 | OPC.1IDAS:ZT120704.PNT | 1IDAS:ZT120704.PNT | 10LAB11AA101XB12 | T-BFP A MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1183 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-08 | OPC.1IDAS:FT120703.PNT | 1IDAS:FT120703.PNT | 10LAB11CF201 | T-BFP A INLET WATER FLOW | AI | 0 | 1000
351 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-08 | OPC.1EDAS:PT050501.PNT | 1EDAS:PT050501.PNT | 10LAB11CP201 | T-BFP A INLET WATER PRESS | AI | 0 | 4 | MPa
352 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-08 | OPC.1EDAS:PT050502.PNT | 1EDAS:PT050502.PNT | 10LAB11CP202 | T-BFP A OUTLET WATER PRESS | AI | 0 | 25 | MPa
558 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053103.PNT | 1EDAS:RT053103.PNT | 10LAC11CT003 | T-BFP A INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
559 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053104.PNT | 1EDAS:RT053104.PNT | 10LAC11CT004 | T-BFP A OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
560 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053105.PNT | 1EDAS:RT053105.PNT | 10LAC11CT005 | T-BFP A THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
561 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053106.PNT | 1EDAS:RT053106.PNT | 10LAC11CT006 | T-BFP A THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
563 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053201.PNT | 1EDAS:RT053201.PNT | 10LAC11CT007 | T-BFP A INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
564 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053202.PNT | 1EDAS:RT053202.PNT | 10LAC11CT008 | T-BFP A OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
565 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053203.PNT | 1EDAS:RT053203.PNT | 10LAC11CT009 | T-BFP A WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
566 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053204.PNT | 1EDAS:RT053204.PNT | 10LAC11CT010 | T-BFP A WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
567 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053205.PNT | 1EDAS:RT053205.PNT | 10LAC11CT011 | T-BFP A WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
568 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-K0301-05 | OPC.1EDAS:RT053206.PNT | 1EDAS:RT053206.PNT | 10LAC11CT012 | T-BFP A WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
485 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-04 | OPC.1FDAS:FT086806.PNT | 1FDAS:FT086806.PNT | 10LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | Mpa
779 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-04 | OPC.1FDAS:TE087503.PNT | 1FDAS:TE087503.PNT | 10LBR11CT001 | BFP TURBINE A INLET STEAM TEMP | TC | 0 | 400 | °C
477 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-04 | OPC.1FDAS:ZT086705.PNT | 1FDAS:ZT086705.PNT | 10LBR11GC001AI01 | BFP TURBINE A INLET STEAM SWITCHING VALVE POSITION INDICATION | AI
546 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50- | OPC.1GDAS:AO092806.OUT | 1GDAS:AO092806.OUT | 10LBR11GC001AO01 | CONTROL BFP TURBINE A INLET STEAM SWITCHING VALVE | AO | 0 | 100 | %
468 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:FT086603.PNT | 1FDAS:FT086603.PNT | 10LBR21CF201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30
457 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:PT086406.PNT | 1FDAS:PT086406.PNT | 10LBR21CP201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa
772 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:TE087401.PNT | 1FDAS:TE087401.PNT | 10LBR21CT001 | BFP TURBINE A INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 400 | °C
458 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:PT086407.PNT | 1FDAS:PT086407.PNT | 10LBR31CP201 | BFP TURBINE A EXHAUST STEAM PRESS | AI | -0.1 | 0.15 | MPa
562 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1EDAS:RT053107.PNT | 1EDAS:RT053107.PNT | 10LBR31CT001 | BFP TURBINE A EXHAUST STEAM TEMP 1 | RTD | 0 | 100 | °C
569 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1EDAS:RT053207.PNT | 1EDAS:RT053207.PNT | 10LBR31CT002 | BFP TURBINE A EXHAUST STEAM TEMP 2 | RTD | 0 | 100 | °C
575 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1EDAS:RT053307.PNT | 1EDAS:RT053307.PNT | 10LBR31CT003 | BFP TURBINE A EXHAUST STEAM TEMP 3 | RTD | 0 | 100 | °C
456 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:PT086405.PNT | 1FDAS:PT086405.PNT | 10LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa
763 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:TE087206.PNT | 1FDAS:TE087206.PNT | 10LBS41CT001 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 400 | °C
757 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1FDAS:TE087108.PNT | 1FDAS:TE087108.PNT | 10LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 400 | °C
823 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-05 | OPC.1GDAS:TE107307.PNT | 1GDAS:TE107307.PNT | 10LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 TEMP (TURBINE SIDE) | TC | 0 | 400 | °C
497 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50- | OPC.1GDAS:CT092705.PNT | 1GDAS:CT092705.PNT | 10MAV50AP103XB13 | BFP TURBINE A LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURREN | AI | 0 | 103 | %
354 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:LT050504.PNT | 1EDAS:LT050504.PNT | 10MAV50CL201 | BFP TURBINE A LUBE-OIL TANK LEVEL | AI | 0 | 750 | mm
570 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:RT053301.PNT | 1EDAS:RT053301.PNT | 10MAV50CT001 | BFP TURBINE A LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | °C
571 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:RT053302.PNT | 1EDAS:RT053302.PNT | 10MAV50CT002 | BFP TURBINE A LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | °C
572 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:RT053303.PNT | 1EDAS:RT053303.PNT | 10MAV50CT003 | BFP TURBINE A LUBE-OIL TANK TEMP. | RTD | 0 | 100 | °C
573 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:RT053304.PNT | 1EDAS:RT053304.PNT | 10MAV50CT004 | BFP TURBINE A FRONT BEARING BOX RETURN OIL TEMP | RTD | 0 | 100 | °C
574 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1EDAS:RT053305.PNT | 1EDAS:RT053305.PNT | 10MAV50CT005 | BFP TURBINE A #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | °C
1190 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0608-01 | OPC.1IDAS:AI120805.PNT | 1IDAS:AI120805.PNT | 10MEHADCS01 | BFP TURBINE A SPEED SET POINT SIGNAL | AI | 0 | 10000 | rpm |  |  | 2840 | 5945
356 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050506.PNT | 1EDAS:AI050506.PNT | 10MTSIADCS01 | BFP TURBINE A SPEED (4~20mA) | AI | 0 | 10000 | rpm
359 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050601.PNT | 1EDAS:AI050601.PNT | 10MTSIADCS03 | BFP TURBINE A NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
360 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050602.PNT | 1EDAS:AI050602.PNT | 10MTSIADCS04 | BFP TURBINE A NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
361 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050603.PNT | 1EDAS:AI050603.PNT | 10MTSIADCS05 | BFP TURBINE A NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
362 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050604.PNT | 1EDAS:AI050604.PNT | 10MTSIADCS06 | BFP TURBINE A NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
363 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050605.PNT | 1EDAS:AI050605.PNT | 10MTSIADCS07 | BFP TURBINE A NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
364 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050606.PNT | 1EDAS:AI050606.PNT | 10MTSIADCS08 | BFP TURBINE A NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
355 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI050505.PNT | 1EDAS:AI050505.PNT | 10MTSIADCS09 | BFP TURBINE A NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
383 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI064505.PNT | 1EDAS:AI064505.PNT | 10MTSIADCS10 | BFP TURBINE A AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
384 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI064506.PNT | 1EDAS:AI064506.PNT | 10MTSIADCS11 | BFP TURBINE A AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
385 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F289S-K0302-05 | OPC.1EDAS:AI064507.PNT | 1EDAS:AI064507.PNT | 10MTSIADCS12 | BFP TURBINE A ECCENTRICTIY (4~20mA) | AI | 0 | 100 | %
399 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-14 | OPC.1EDAS:ZT064807.PNT | 1EDAS:ZT064807.PNT | 10PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | %
659 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-14 | OPC.1EDAS:RT067804.PNT | 1EDAS:RT067804.PNT | 10PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
803 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107101.PNT | 1GDAS:TE107101.PNT | 10XAC11CT001 | BFP TURBINE A POSITION THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
804 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107102.PNT | 1GDAS:TE107102.PNT | 10XAC11CT002 | BFP TURBINE A POSITION THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
805 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107103.PNT | 1GDAS:TE107103.PNT | 10XAC11CT003 | BFP TURBINE A WORK THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
806 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107104.PNT | 1GDAS:TE107104.PNT | 10XAC11CT004 | BFP TURBINE A WORK THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
807 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107105.PNT | 1GDAS:TE107105.PNT | 10XAC11CT005 | BFP TURBINE A SUPPORT PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
808 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107106.PNT | 1GDAS:TE107106.PNT | 10XAC11CT006 | BFP TURBINE A SUPPORT PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
809 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107107.PNT | 1GDAS:TE107107.PNT | 10XAC11CT007 | BFP TURBINE A #2 BEARING PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
810 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:TE107201.PNT | 1GDAS:TE107201.PNT | 10XAC11CT008 | BFP TURBINE A #2 BEARING PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
737 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:RT104501.PNT | 1GDAS:RT104501.PNT | 10XAC11CT009 | BFP TURBINE A SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | °C |  | 0 | 0 | 65 | 75
738 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | 50-F290S-J0201-20 | OPC.1GDAS:RT104502.PNT | 1GDAS:RT104502.PNT | 10XAC11CT010 | BFP TURBINE A THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
381 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50-F290S-J0201-08 | OPC.1EDAS:CT064503.PNT | 1EDAS:CT064503.PNT | 10LAC12AP001XB13 | BOOSTER PUMP FOR T-BFP B CURRENT | AI | 0 | 100 | %
608 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50-F290S-K0301-06 | OPC.1EDAS:RT067101.PNT | 1EDAS:RT067101.PNT | 10LAC12CT001 | BOOSTER PUMP FOR T-BFP B DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
609 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50-F290S-K0301-06 | OPC.1EDAS:RT067102.PNT | 1EDAS:RT067102.PNT | 10LAC12CT002 | BOOSTER PUMP FOR T-BFP B FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
729 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093801.PNT | 1GDAS:RT093801.PNT | 10LAC12CT013 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 1 | RTD | 0 | 100 | °C
730 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093802.PNT | 1GDAS:RT093802.PNT | 10LAC12CT014 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 2 | RTD | 0 | 100 | °C
731 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093803.PNT | 1GDAS:RT093803.PNT | 10LAC12CT015 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 3 | RTD | 0 | 100 | °C
732 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093804.PNT | 1GDAS:RT093804.PNT | 10LAC12CT016 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 4 | RTD | 0 | 100 | °C
733 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093805.PNT | 1GDAS:RT093805.PNT | 10LAC12CT017 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 5 | RTD | 0 | 100 | °C
734 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093806.PNT | 1GDAS:RT093806.PNT | 10LAC12CT018 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 6 | RTD | 0 | 100 | °C
735 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093807.PNT | 1GDAS:RT093807.PNT | 10LAC12CT019 | MOTOR OF BOOSTER PUMP FOR T-BFP B BEARING TEMP 1 | RTD | 0 | 100 | °C
736 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #10B - BOOSTER PUMP | 50- | OPC.1GDAS:RT093808.PNT | 1GDAS:RT093808.PNT | 10LAC12CT020 | MOTOR OF BOOSTER PUMP FOR T-BFP B BEARING TEMP 2 | RTD | 0 | 100 | °C
407 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50- | OPC.1FDAS:CT072802.PNT | 1FDAS:CT072802.PNT | 10MAV60GC001AI01 | BFP TURBINE B TURNING GEAR MOTOR CURRENT | AI | 0 | 50 | A
1229 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-08 | OPC.1TFPBREC:AO122201.OUT | 1TFPBREC:AO122201.OUT | 10LAB12AA101XB11 | T-BFP B MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1189 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-08 | OPC.1IDAS:ZT120804.PNT | 1IDAS:ZT120804.PNT | 10LAB12AA101XB12 | T-BFP B MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1188 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-08 | OPC.1IDAS:FT120803.PNT | 1IDAS:FT120803.PNT | 10LAB12CF201 | T-BFP B INLET WATER FLOW | AI | 0 | 1000
379 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-08 | OPC.1EDAS:PT064501.PNT | 1EDAS:PT064501.PNT | 10LAB12CP201 | T-BFP B INLET WATER PRESS | AI | 0 | 4 | MPa
380 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-08 | OPC.1EDAS:PT064502.PNT | 1EDAS:PT064502.PNT | 10LAB12CP202 | T-BFP B OUTLET WATER PRESS | AI | 0 | 25 | MPa
610 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067103.PNT | 1EDAS:RT067103.PNT | 10LAC12CT003 | T-BFP B INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
611 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067104.PNT | 1EDAS:RT067104.PNT | 10LAC12CT004 | T-BFP B OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
612 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067105.PNT | 1EDAS:RT067105.PNT | 10LAC12CT005 | T-BFP B THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
613 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067106.PNT | 1EDAS:RT067106.PNT | 10LAC12CT006 | T-BFP B THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
615 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067201.PNT | 1EDAS:RT067201.PNT | 10LAC12CT007 | T-BFP B INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
616 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067202.PNT | 1EDAS:RT067202.PNT | 10LAC12CT008 | T-BFP B OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
617 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067203.PNT | 1EDAS:RT067203.PNT | 10LAC12CT009 | T-BFP B WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
618 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067204.PNT | 1EDAS:RT067204.PNT | 10LAC12CT010 | T-BFP B WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
619 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067205.PNT | 1EDAS:RT067205.PNT | 10LAC12CT011 | T-BFP B WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
620 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0301-06 | OPC.1EDAS:RT067206.PNT | 1EDAS:RT067206.PNT | 10LAC12CT012 | T-BFP B WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
786 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-04 | OPC.1FDAS:TE087603.PNT | 1FDAS:TE087603.PNT | 10LBR12CT001 | BFP TURBINE B INLET STEAM TEMP | TC | 0 | 400 | °C
484 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-04 | OPC.1FDAS:ZT086805.PNT | 1FDAS:ZT086805.PNT | 10LBR12GC001AI01 | BFP TURBINE B INLET STEAM SWITCHING VALVE POSITION INDICATION | AI | 0 | 20 | MPa
547 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50- | OPC.1GDAS:AO092807.OUT | 1GDAS:AO092807.OUT | 10LBR12GC001AO01 | CONTROL BFP TURBINE B INLET STEAM SWITCHING VALVE | AO | 0 | 100 | %
469 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1FDAS:FT086604.PNT | 1FDAS:FT086604.PNT | 10LBR22CF201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30
464 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1FDAS:PT086506.PNT | 1FDAS:PT086506.PNT | 10LBR22CP201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa
773 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1FDAS:TE087402.PNT | 1FDAS:TE087402.PNT | 10LBR22CT001 | BFP TURBINE B INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 400 | °C
465 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1FDAS:PT086507.PNT | 1FDAS:PT086507.PNT | 10LBR32CP201 | BFP TURBINE B EXHAUST STEAM PRESS | AI | -0.1 | 0.15 | MPa
614 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1EDAS:RT067107.PNT | 1EDAS:RT067107.PNT | 10LBR32CT001 | BFP TURBINE B EXHAUST STEAM TEMP 1 | RTD | 0 | 100 | °C
621 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1EDAS:RT067207.PNT | 1EDAS:RT067207.PNT | 10LBR32CT002 | BFP TURBINE B EXHAUST STEAM TEMP 2 | RTD | 0 | 100 | °C
627 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-05 | OPC.1EDAS:RT067307.PNT | 1EDAS:RT067307.PNT | 10LBR32CT003 | BFP TURBINE B EXHAUST STEAM TEMP 3 | RTD | 0 | 100 | °C
498 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50- | OPC.1GDAS:CT092706.PNT | 1GDAS:CT092706.PNT | 10MAV60AP103XB13 | BFP TURBINE B LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURREN | AI | 0 | 104 | %
382 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:LT064504.PNT | 1EDAS:LT064504.PNT | 10MAV60CL201 | BFP TURBINE B LUBE-OIL TANK LEVEL | AI | 0 | 750 | mm |  | 145 | 272 | 475 | 750
622 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:RT067301.PNT | 1EDAS:RT067301.PNT | 10MAV60CT001 | BFP TURBINE B LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | °C
623 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:RT067302.PNT | 1EDAS:RT067302.PNT | 10MAV60CT002 | BFP TURBINE B LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | °C
624 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:RT067303.PNT | 1EDAS:RT067303.PNT | 10MAV60CT003 | BFP TURBINE B LUBE-OIL TANK TEMP. | RTD | 0 | 100 | °C
625 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:RT067304.PNT | 1EDAS:RT067304.PNT | 10MAV60CT004 | BFP TURBINE B FRONT BEARING BOX RETURN OIL TEMP | RTD | 0 | 100 | °C
626 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1EDAS:RT067305.PNT | 1EDAS:RT067305.PNT | 10MAV60CT005 | BFP TURBINE B #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | °C
1191 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F289S-K0608-01 | OPC.1IDAS:AI120806.PNT | 1IDAS:AI120806.PNT | 10MEHBDCS01 | BFP TURBINE B SPEED SET POINT SIGNAL | AI | 0 | 10000 | rpm |  |  | 2840 | 5945
506 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104107.PNT | 1GDAS:AI104107.PNT | 10MTSIBDCS01 | BFP TURBINE B SPEED (4~20mA) | AI | 0 | 10000 | rpm
507 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104201.PNT | 1GDAS:AI104201.PNT | 10MTSIBDCS02 | BFP TURBINE B NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
508 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104202.PNT | 1GDAS:AI104202.PNT | 10MTSIBDCS03 | BFP TURBINE B NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
509 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104203.PNT | 1GDAS:AI104203.PNT | 10MTSIBDCS04 | BFP TURBINE B NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
510 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104204.PNT | 1GDAS:AI104204.PNT | 10MTSIBDCS05 | BFP TURBINE B NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
511 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104205.PNT | 1GDAS:AI104205.PNT | 10MTSIBDCS06 | BFP TURBINE B NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
512 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104206.PNT | 1GDAS:AI104206.PNT | 10MTSIBDCS07 | BFP TURBINE B NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
513 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104207.PNT | 1GDAS:AI104207.PNT | 10MTSIBDCS08 | BFP TURBINE B NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
514 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104301.PNT | 1GDAS:AI104301.PNT | 10MTSIBDCS09 | BFP TURBINE B NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
515 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104302.PNT | 1GDAS:AI104302.PNT | 10MTSIBDCS10 | BFP TURBINE B AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
516 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104303.PNT | 1GDAS:AI104303.PNT | 10MTSIBDCS11 | BFP TURBINE B AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
517 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-K0604-07 | OPC.1GDAS:AI104304.PNT | 1GDAS:AI104304.PNT | 10MTSIBDCS12 | BFP TURBINE B ECCENTRICTIY (4~20mA) | AI | 0 | 100 | %
811 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107202.PNT | 1GDAS:TE107202.PNT | 10XAC12CT001 | BFP TURBINE B POSITION THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
812 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107203.PNT | 1GDAS:TE107203.PNT | 10XAC12CT002 | BFP TURBINE B POSITION THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
813 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107204.PNT | 1GDAS:TE107204.PNT | 10XAC12CT003 | BFP TURBINE B WORK THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
814 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107205.PNT | 1GDAS:TE107205.PNT | 10XAC12CT004 | BFP TURBINE B WORK THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
815 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107206.PNT | 1GDAS:TE107206.PNT | 10XAC12CT005 | BFP TURBINE B SUPPORT PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
816 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107207.PNT | 1GDAS:TE107207.PNT | 10XAC12CT006 | BFP TURBINE B SUPPORT PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
817 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107301.PNT | 1GDAS:TE107301.PNT | 10XAC12CT007 | BFP TURBINE B #2 BEARING PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
818 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:TE107302.PNT | 1GDAS:TE107302.PNT | 10XAC12CT008 | BFP TURBINE B #2 BEARING PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
739 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:RT104503.PNT | 1GDAS:RT104503.PNT | 10XAC12CT009 | BFP TURBINE B SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
740 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #10B | 50-F290S-J0201-20 | OPC.1GDAS:RT104504.PNT | 1GDAS:RT104504.PNT | 10XAC12CT010 | BFP TURBINE B THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
1237 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1BFPREC:AO122303.OUT | 1BFPREC:AO122303.OUT | 10LAH10AA101XB11 | M-BFP MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1196 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1IDAS:ZT121104.PNT | 1IDAS:ZT121104.PNT | 10LAH10AA101XB12 | M-BFP MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1195 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1IDAS:FT121103.PNT | 1IDAS:FT121103.PNT | 10LAH10CF201 | M-BFP INLET WATER FLOW | AI | 0 | 400 |  |  |  | 0 | 367.2158
486 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1GDAS:PT092601.PNT | 1GDAS:PT092601.PNT | 10LAH10CP201 | M-BFP INLET PRESS | AI | 0 | 2.5 | MPa
487 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1GDAS:PT092602.PNT | 1GDAS:PT092602.PNT | 10LAH10CP202 | M-BFP OUTLET WATER PRESS | AI | 0 | 25 | MPa
802 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092504.PNT | 1GDAS:TE092504.PNT | 10LAH10CT001 | M-BFP OUTLET TEMPERATURE | TC | 0 | 200 | °C
1238 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1FWCNTL:AO122304.OUT | 1FWCNTL:AO122304.OUT | 10LAJ10AA101XB11 | M-BFP HYDRAULIC CUOPLE ACTUATOR CONTROL COMMAND | AO | 0 | 100 | %
1197 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1IDAS:ZT121105.PNT | 1IDAS:ZT121105.PNT | 10LAJ10AA101XB12 | M-BFP HYDRAULIC CUOPLE ACTUATOR POSITION | AI | 0 | 100 | %
490 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-08 | OPC.1GDAS:CT092605.PNT | 1GDAS:CT092605.PNT | 10LAJ10AP001XB13 | M-BFP GROUP CURRENT | AI | 0 | 100 | %
492 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:AI092607.PNT | 1GDAS:AI092607.PNT | 10LAJ10CS201 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min
687 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093205.PNT | 1GDAS:RT093205.PNT | 10LAJ10CT001 | BOOSTER PUMP FOR M-BFP FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
688 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093206.PNT | 1GDAS:RT093206.PNT | 10LAJ10CT002 | BOOSTER PUMP FOR M-BFP DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
696 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093306.PNT | 1GDAS:RT093306.PNT | 10LAJ10CT003 | M-BFP INLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
703 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093406.PNT | 1GDAS:RT093406.PNT | 10LAJ10CT004 | M-BFP OUTET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
697 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093307.PNT | 1GDAS:RT093307.PNT | 10LAJ10CT005 | M-BFP THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
704 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093407.PNT | 1GDAS:RT093407.PNT | 10LAJ10CT006 | M-BFP THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
689 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093207.PNT | 1GDAS:RT093207.PNT | 10LAJ10CT007 | M-BFP INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
690 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093208.PNT | 1GDAS:RT093208.PNT | 10LAJ10CT008 | M-BFP OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
691 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093301.PNT | 1GDAS:RT093301.PNT | 10LAJ10CT009 | M-BFP HYDRAULIC COUPLER B1 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
692 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093302.PNT | 1GDAS:RT093302.PNT | 10LAJ10CT010 | M-BFP HYDRAULIC COUPLER B2 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
693 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093303.PNT | 1GDAS:RT093303.PNT | 10LAJ10CT011 | M-BFP HYDRAULIC COUPLER B3 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
694 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093304.PNT | 1GDAS:RT093304.PNT | 10LAJ10CT012 | M-BFP HYDRAULIC COUPLER B4 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
695 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093305.PNT | 1GDAS:RT093305.PNT | 10LAJ10CT013 | M-BFP HYDRAULIC COUPLER B5 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
698 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093401.PNT | 1GDAS:RT093401.PNT | 10LAJ10CT014 | M-BFP HYDRAULIC COUPLER B6 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
699 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093402.PNT | 1GDAS:RT093402.PNT | 10LAJ10CT015 | M-BFP HYDRAULIC COUPLER B7 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
700 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093403.PNT | 1GDAS:RT093403.PNT | 10LAJ10CT016 | M-BFP HYDRAULIC COUPLER B8 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
701 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093404.PNT | 1GDAS:RT093404.PNT | 10LAJ10CT017 | M-BFP HYDRAULIC COUPLER B9 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
702 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093405.PNT | 1GDAS:RT093405.PNT | 10LAJ10CT018 | M-BFP HYDRAULIC COUPLER B10 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
679 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093104.PNT | 1GDAS:RT093104.PNT | 10LAJ10CT019 | M-BFP LUBE-OIL COOLER OUTLET TEMP | RTD | -50 | 180 | °C |  |  |  | 55 | 60
680 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093105.PNT | 1GDAS:RT093105.PNT | 10LAJ10CT020 | M-BFP WORKING OIL COOLER INLET TEMP | RTD | -50 | 180 | °C |  |  |  | 110 | 130
681 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093106.PNT | 1GDAS:RT093106.PNT | 10LAJ10CT021 | M-BFP WORKING OIL COOLER OUTLET TEMP | RTD | -50 | 180 | °C |  |  | 35 | 75 | 85
686 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093204.PNT | 1GDAS:RT093204.PNT | 10LAJ10CT022 | M-BFP HYDRAULIC COUPLER MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | °C |  |  |  | 80 | 90
682 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093107.PNT | 1GDAS:RT093107.PNT | 10LAJ10CT023 | BOOSTER PUMP FOR M-BFP MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | °C |  |  |  | 80 | 90
676 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093101.PNT | 1GDAS:RT093101.PNT | 10LAJ10CT024 | M-BFP MOTOR STATOR WINDING TEMP 1 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
677 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093102.PNT | 1GDAS:RT093102.PNT | 10LAJ10CT025 | M-BFP MOTOR STATOR WINDING TEMP 2 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
678 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093103.PNT | 1GDAS:RT093103.PNT | 10LAJ10CT026 | M-BFP MOTOR STATOR WINDING TEMP 3 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
683 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093201.PNT | 1GDAS:RT093201.PNT | 10LAJ10CT027 | M-BFP MOTOR STATOR WINDING TEMP 4 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
684 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093202.PNT | 1GDAS:RT093202.PNT | 10LAJ10CT028 | M-BFP MOTOR STATOR WINDING TEMP 5 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
685 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #10 | 50-F290S-J0201-21 | OPC.1GDAS:RT093203.PNT | 1GDAS:RT093203.PNT | 10LAJ10CT029 | M-BFP MOTOR STATOR WINDING TEMP 6 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
488 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-08 | OPC.1GDAS:PT092603.PNT | 1GDAS:PT092603.PNT | 10LAB30CP201 | HP HEATER MAIN PIPE INLET WATER PRESS | AI | 0 | 25 | MPa
792 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092401.PNT | 1GDAS:TE092401.PNT | 10LAB30CT001 | HP HEATER INLET WATER TEMP | TC | 0 | 200 | °C
794 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092403.PNT | 1GDAS:TE092403.PNT | 10LAB30CT002 | #3 HP HEATER OUTLET MAIN PIPE WATER TEMP | TC | 0 | 210 | °C
1141 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120107.PNT | 1IDAS:LT120107.PNT | 10LAD30CL201 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1149 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120207.PNT | 1IDAS:LT120207.PNT | 10LAD30CL202 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1157 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120307.PNT | 1IDAS:LT120307.PNT | 10LAD30CL203 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
472 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1FDAS:ZT086607.PNT | 1FDAS:ZT086607.PNT | 10LBQ30AA001XB12 | #3 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
454 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086403.PNT | 1FDAS:PT086403.PNT | 10LBQ30CP201 | #3 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 2 | MPa
502 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104103.PNT | 1GDAS:PT104103.PNT | 10LBQ30CP202 | #3 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 2 | MPa
758 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087201.PNT | 1FDAS:TE087201.PNT | 10LBQ30CT001 | #3 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | °C
759 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087202.PNT | 1FDAS:TE087202.PNT | 10LBQ30CT002 | #3 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | °C
760 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087203.PNT | 1FDAS:TE087203.PNT | 10LBQ30CT003 | #3 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | °C
821 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107305.PNT | 1GDAS:TE107305.PNT | 10LBQ30CT004 | #3 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | °C
1245 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP3LVL:AO122404.OUT | 1HP3LVL:AO122404.OUT | 10LCH30AA101XB11 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1204 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121204.PNT | 1IDAS:ZT121204.PNT | 10LCH30AA101XB12 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1246 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP3LVL:AO122405.OUT | 1HP3LVL:AO122405.OUT | 10LCH30AA102XB11 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1205 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121205.PNT | 1IDAS:ZT121205.PNT | 10LCH30AA102XB12 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
801 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #10 | 50-F290S-J0201-09(1/2) | OPC.1GDAS:TE092503.PNT | 1GDAS:TE092503.PNT | 10LCH30CT001 | #3 HP HEATER DRAIN WATER TEMP | TC | 0 | 190 | °C
796 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092405.PNT | 1GDAS:TE092405.PNT | 10LAB30CT003 | #2 HP HEATER OUTLET WATER TEMP | TC | 0 | 250 | °C
795 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092404.PNT | 1GDAS:TE092404.PNT | 10LAB30CT002 | #2 HP HEATER INLET WATER TEMP | TC | 0 | 210 | °C
1140 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120106.PNT | 1IDAS:LT120106.PNT | 10LAD20CL201 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1148 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120206.PNT | 1IDAS:LT120206.PNT | 10LAD20CL202 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1156 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120306.PNT | 1IDAS:LT120306.PNT | 10LAD20CL203 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
471 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1FDAS:ZT086606.PNT | 1FDAS:ZT086606.PNT | 10LBQ20AA001XB12 | #2 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
453 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086402.PNT | 1FDAS:PT086402.PNT | 10LBQ20CP201 | #2 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 4 | MPa
501 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104102.PNT | 1GDAS:PT104102.PNT | 10LBQ20CP202 | #2 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 4 | MPa
753 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087104.PNT | 1FDAS:TE087104.PNT | 10LBQ20CT001 | #2 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 600 | °C
754 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087105.PNT | 1FDAS:TE087105.PNT | 10LBQ20CT002 | #2 EXTRACTION PIPE TOP TEMP | TC | 0 | 600 | °C
755 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087106.PNT | 1FDAS:TE087106.PNT | 10LBQ20CT003 | #2 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 600 | °C
820 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107304.PNT | 1GDAS:TE107304.PNT | 10LBQ20CT004 | #2 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | °C
1242 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP2LVL:AO122401.OUT | 1HP2LVL:AO122401.OUT | 10LCH20AA101XB11 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1201 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121201.PNT | 1IDAS:ZT121201.PNT | 10LCH20AA101XB12 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1243 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP2LVL:AO122402.OUT | 1HP2LVL:AO122402.OUT | 10LCH20AA102XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1202 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121202.PNT | 1IDAS:ZT121202.PNT | 10LCH20AA102XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1244 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP2LVL:AO122403.OUT | 1HP2LVL:AO122403.OUT | 10LCH20AA103XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1203 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121203.PNT | 1IDAS:ZT121203.PNT | 10LCH20AA103XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
800 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #10 | 50-F290S-J0201-09(1/2) | OPC.1GDAS:TE092502.PNT | 1GDAS:TE092502.PNT | 10LCH20CT001 | #2 HP HEATER DRAIN WATER TEMP | TC | 0 | 210 | °C
798 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092407.PNT | 1GDAS:TE092407.PNT | 10LAB30CT004 | #1 HP HEATER OUTLET WATER TEMP | TC | 0 | 300 | °C
797 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-08 | OPC.1GDAS:TE092406.PNT | 1GDAS:TE092406.PNT | 10LAB30CT006 | #1 HP HEATER INLET WATER TEMP | TC | 0 | 250 | °C
489 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-08 | OPC.1GDAS:PT092604.PNT | 1GDAS:PT092604.PNT | 10LAB40CP201 | HP HEATER OUTLET WATER PRESS | AI | 0 | 25 | MPa
1139 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120105.PNT | 1IDAS:LT120105.PNT | 10LAD10CL201 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1147 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120205.PNT | 1IDAS:LT120205.PNT | 10LAD10CL202 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1155 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:LT120305.PNT | 1IDAS:LT120305.PNT | 10LAD10CL203 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
470 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1FDAS:ZT086605.PNT | 1FDAS:ZT086605.PNT | 10LBQ10AA001XB12 | #1 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
452 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1FDAS:PT086401.PNT | 1FDAS:PT086401.PNT | 10LBQ10CP201 | #1 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 6.5 | MPa
500 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1GDAS:PT104101.PNT | 1GDAS:PT104101.PNT | 10LBQ10CP202 | #1 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 6.5 | MPa
750 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087101.PNT | 1FDAS:TE087101.PNT | 10LBQ10CT001 | #1 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 450 | °C
751 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087102.PNT | 1FDAS:TE087102.PNT | 10LBQ10CT002 | #1 EXTRACTION PIPE TOP TEMP | TC | 0 | 450 | °C
752 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1FDAS:TE087103.PNT | 1FDAS:TE087103.PNT | 10LBQ10CT003 | #1 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 450 | °C
819 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-05 | OPC.1GDAS:TE107303.PNT | 1GDAS:TE107303.PNT | 10LBQ10CT004 | #1 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 450 | °C
1239 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP1LVL:AO122305.OUT | 1HP1LVL:AO122305.OUT | 10LCH10AA101XB11 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1198 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121106.PNT | 1IDAS:ZT121106.PNT | 10LCH10AA101XB12 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1240 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP1LVL:AO122306.OUT | 1HP1LVL:AO122306.OUT | 10LCH10AA102XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1199 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121107.PNT | 1IDAS:ZT121107.PNT | 10LCH10AA102XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1241 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1HP1LVL:AO122307.OUT | 1HP1LVL:AO122307.OUT | 10LCH10AA103XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1200 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1IDAS:ZT121108.PNT | 1IDAS:ZT121108.PNT | 10LCH10AA103XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
799 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #10 | 50-F290S-J0201-09(1/2) | OPC.1GDAS:TE092501.PNT | 1GDAS:TE092501.PNT | 10LCH10CT001 | #1 HP HEATER DRAIN WATER TEMP | TC | 0 | 260 | °C
548 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-K0601-03 | OPC.1GDAS:AO104701.OUT | 1GDAS:AO104701.OUT | 10DCSMEHA01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | %
549 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-K0601-03 | OPC.1GDAS:AO104702.OUT | 1GDAS:AO104702.OUT | 10DCSMEHB01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | %
228 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1ODAS:ZT193301.PNT | 1ODAS:ZT193301.PNT | 10LAB40AA002XB12 | BOILER FEED WATER MOTORIZED ORIFICE VALVE POSITION | AI | 0 | 100 | %
870 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1PDAS:FT200604C.PNT | 1PDAS:FT200604C.PNT | 10LAB40CF201 | FEED WATER FLOW | AI | 0 | 1500 | T/H
876 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1PDAS:FT200704C.PNT | 1PDAS:FT200704C.PNT | 10LAB40CF202 | FEED WATER FLOW | AI | 0 | 1500 | T/H
884 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1PDAS:FT200804C.PNT | 1PDAS:FT200804C.PNT | 10LAB40CF203 | FEED WATER FLOW | AI | 0 | 1500 | T/H
221 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1ODAS:PT193201.PNT | 1ODAS:PT193201.PNT | 10LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa
1119 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1PDAS:TE202808.PNT | 1PDAS:TE202808.PNT | 10LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | °C
240 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1ODAS:AO193601.OUT | 1ODAS:AO193601.OUT | 10LAB41AA101XB11 | BOILER FEED WATER BYPASS CONTROL VALVE CONTROL | AO | 0 | 100 | %
229 | 2 | UJRBG #10 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F290S-J0201-08 | OPC.1ODAS:ZT193303.PNT | 1ODAS:ZT193303.PNT | 10LAB41AA101XB12 | BOILER FEED WATER BYPASS CONTROL VALVE POSITION | AI | 0 | 100 | %
997 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #10A | 50-F290S-J0201-02 | OPC.1SAFVANE:AO202106.OUT | 1SAFVANE:AO202106.OUT | 10HFW11AA101XB11 | SAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
893 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT201106.PNT | 1PDAS:ZT201106.PNT | 10HFW11AA101XB12 | SAF A INLET VANE POSITION | AI | 0 | 100 | %
33 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #10A | 50-F290S-J0201-02 | OPC.1LDAS:CT150301.PNT | 1LDAS:CT150301.PNT | 10HFW11AN001XB13 | SAF A CURRENT | AI | 0 | 250 | A
1005 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #10B | 50-F290S-J0201-02 | OPC.1SAFVANE:AO202206.OUT | 1SAFVANE:AO202206.OUT | 10HFW12AA101XB11 | SAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
900 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT201206.PNT | 1PDAS:ZT201206.PNT | 10HFW12AA101XB12 | SAF B INLET VANE POSITION | AI | 0 | 100 | %
48 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #10B | 50-F290S-J0201-02 | OPC.1LDAS:CT150701.PNT | 1LDAS:CT150701.PNT | 10HFW12AN001XB13 | SAF B CURRENT | AI | 0 | 250 | A
153 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1MDAS:PT163107.PNT | 1MDAS:PT163107.PNT | 10HFW10CP201 | SAF OUTLET AIR PRESSURE | AI | 0 | 25 | KPa
872 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1PDAS:PT200606.PNT | 1PDAS:PT200606.PNT | 10HFW10CP301 | DIFFERENTIAL PRESSURE BETWEEN SAF OUTLET AND PRIMARY AIR PIPE | AI | 0 | 6.5 | KPa
317 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1MDAS:TE162606.PNT | 1MDAS:TE162606.PNT | 10HFW10CT001 | SAF OUTLET AIR TEMP. | TC | 0 | 400 | °C
1025 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1SAFASH:AO202504.OUT | 1SAFASH:AO202504.OUT | 10HFW13AA101XB11 | SAF EXHAUST ASH VAVLE CONTROL COMMAND | AO | 0 | 100 | %
895 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1PDAS:ZT201108.PNT | 1PDAS:ZT201108.PNT | 10HFW13AA101XB12 | SAF EXHAUST ASH VAVLE POSITION | AI | 0 | 100 | %
871 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F290S-J0201-02 | OPC.1PDAS:PT200605.PNT | 1PDAS:PT200605.PNT | 10HFW13DP201 | SAF DIFFERENTIAL PRESSURE BETWEEN FILTER AND DISCHARGE ASH OUTLET | AI | 0 | 1.37 | KPa
34 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 4 | COAL FEEDER #10A | 50-F290S-J0201-03 | OPC.1LDAS:FT150302.PNT | 1LDAS:FT150302.PNT | 10HFB10GC001AI01 | ECF A INSTANTANEOUS FEED RATE | AI | 0 | 60
56 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 4 | COAL FEEDER #10A | 50-F290S-J0201-03 | OPC.1LDAS:AO150402.OUT | 1LDAS:AO150402.OUT | 10HFB10GC001AO01 | ECF A FEED RATE COMMAND | AO | 0 | 60
8 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-03 | OPC.1JDAS:CT130608.PNT | 1JDAS:CT130608.PNT | 10HFC10AJ001XB13 | MSM A CURRENT | AI | 0 | 75 | A
61 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130101.PNT | 1JDAS:RT130101.PNT | 10HFC10CT001 | MSM A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
68 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130201.PNT | 1JDAS:RT130201.PNT | 10HFC10CT002 | MSM A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
62 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130102.PNT | 1JDAS:RT130102.PNT | 10HFC10CT003 | MSM A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
69 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130202.PNT | 1JDAS:RT130202.PNT | 10HFC10CT004 | MSM A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
63 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130103.PNT | 1JDAS:RT130103.PNT | 10HFC10CT005 | MSM A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
70 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130203.PNT | 1JDAS:RT130203.PNT | 10HFC10CT006 | MSM A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
64 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130104.PNT | 1JDAS:RT130104.PNT | 10HFC10CT007 | MSM A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
71 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130204.PNT | 1JDAS:RT130204.PNT | 10HFC10CT008 | MSM A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
65 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130105.PNT | 1JDAS:RT130105.PNT | 10HFC10CT009 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
66 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130106.PNT | 1JDAS:RT130106.PNT | 10HFC10CT010 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
72 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130205.PNT | 1JDAS:RT130205.PNT | 10HFC10CT011 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
73 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130206.PNT | 1JDAS:RT130206.PNT | 10HFC10CT012 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
67 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130107.PNT | 1JDAS:RT130107.PNT | 10HFC10CT013 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
74 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130207.PNT | 1JDAS:RT130207.PNT | 10HFC10CT014 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130501.PNT | 1JDAS:RT130501.PNT | 10HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1090 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1PDAS:RT201701.PNT | 1PDAS:RT201701.PNT | 10HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1095 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1PDAS:RT201801.PNT | 1PDAS:RT201801.PNT | 10HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
90 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130502.PNT | 1JDAS:RT130502.PNT | 10HFC10CT018 | MSM A LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
91 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1JDAS:RT130503.PNT | 1JDAS:RT130503.PNT | 10HFC10CT019 | MSM A LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
170 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1MDAS:PT163403.PNT | 1MDAS:PT163403.PNT | 10HFC10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4 | %
51 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-35 | OPC.1LDAS:AI150702.PNT | 1LDAS:AI150702.PNT | 10HFC10GC003AI01 | MSM A OUTLET CO CONTENT | AI | 0 | 100 | %
1 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1JDAS:PT130601.PNT | 1JDAS:PT130601.PNT | 10HFE10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
993 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1MILLAHCAD:AO202102.OUT | 1MILLAHCAD:AO202102.OUT | 10HFE41AA101XB11 | MSM A INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
841 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT200105.PNT | 1PDAS:ZT200105.PNT | 10HFE41AA101XB12 | MSM A INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
992 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1MILLAHCAD:AO202101.OUT | 1MILLAHCAD:AO202101.OUT | 10HFE51AA101XB11 | MSM A INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
840 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT200104.PNT | 1PDAS:ZT200104.PNT | 10HFE51AA101XB12 | MSM A INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
994 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1MILLAPAD:AO202103.OUT | 1MILLAPAD:AO202103.OUT | 10HFE51AA102XB11 | MSM A INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
842 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT200106.PNT | 1PDAS:ZT200106.PNT | 10HFE51AA102XB12 | MSM A INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
838 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:FT200102.PNT | 1PDAS:FT200102.PNT | 10HFE51CF201 | MSM A INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
839 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:FT200103.PNT | 1PDAS:FT200103.PNT | 10HFE51CF202 | MSM A INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
837 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:PT200101.PNT | 1PDAS:PT200101.PNT | 10HFE51CP201 | MSM A INLET AIR PRESSURE | AI | 0 | 20 | KPa
1100 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-02 | OPC.1PDAS:TE202601.PNT | 1PDAS:TE202601.PNT | 10HFE51CT001 | MSM A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-34 | OPC.1VMS2:AIN5.PNT | 1VMS2:AIN5.PNT | 10HFC10CY001X | #10 MSM A BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #10A | 50-F290S-J0201-34 | OPC.1VMS2:AIN6.PNT | 1VMS2:AIN6.PNT | 10HFC10CY001Y | #10 MSM A BEARING VIBRATION Y | AI | 0 | 20 | µm
172 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163501.PNT | 1MDAS:FT163501.PNT | 10HFF11CF201 | 1# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
1081 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211705.OUT | 1RHTTEM:AO211705.OUT | 10HHA10KV001XB11 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
984 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210705.PNT | 1QDAS:ZT210705.PNT | 10HHA10KV001XB12 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1082 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211706.OUT | 1RHTTEM:AO211706.OUT | 10HHA10KV002XB11 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
985 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210706.PNT | 1QDAS:ZT210706.PNT | 10HHA10KV002XB12 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
2 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130602.PNT | 1JDAS:AI130602.PNT | 10HHA11CB201B | 1# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1029 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAA:AO211101.OUT | 1AUXDAMPAA:AO211101.OUT | 10HLA11AA001XB11 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
932 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210101.PNT | 1QDAS:ZT210101.PNT | 10HLA11AA001XB12 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1030 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPA:AO211102.OUT | 1CYCDAMPA:AO211102.OUT | 10HLA11AA002XB11 | 1# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
933 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210102.PNT | 1QDAS:ZT210102.PNT | 10HLA11AA002XB12 | 1# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1031 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAB:AO211103.OUT | 1AUXDAMPAB:AO211103.OUT | 10HLA11AA003XB11 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
934 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210103.PNT | 1QDAS:ZT210103.PNT | 10HLA11AA003XB12 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
173 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163502.PNT | 1MDAS:FT163502.PNT | 10HFF12CF201 | 2# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
3 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130603.PNT | 1JDAS:AI130603.PNT | 10HHA12CB201B | 2# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1083 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211707.OUT | 1RHTTEM:AO211707.OUT | 10HHA20KV001XB11 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
986 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210707.PNT | 1QDAS:ZT210707.PNT | 10HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1084 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211708.OUT | 1RHTTEM:AO211708.OUT | 10HHA20KV002XB11 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
987 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210708.PNT | 1QDAS:ZT210708.PNT | 10HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1042 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAA:AO211206.OUT | 1AUXDAMPAA:AO211206.OUT | 10HLA21AA001XB11 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
945 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210206.PNT | 1QDAS:ZT210206.PNT | 10HLA21AA001XB12 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1043 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPA:AO211207.OUT | 1CYCDAMPA:AO211207.OUT | 10HLA21AA002XB11 | 2# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
946 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210207.PNT | 1QDAS:ZT210207.PNT | 10HLA21AA002XB12 | 2# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1044 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAB:AO211208.OUT | 1AUXDAMPAB:AO211208.OUT | 10HLA21AA003XB11 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
947 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210208.PNT | 1QDAS:ZT210208.PNT | 10HLA21AA003XB12 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
174 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163503.PNT | 1MDAS:FT163503.PNT | 10HFF13CF201 | 3# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
4 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130604.PNT | 1JDAS:AI130604.PNT | 10HHA13CB201B | 3# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1085 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211801.OUT | 1RHTTEM:AO211801.OUT | 10HHA30KV001XB11 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
988 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210801.PNT | 1QDAS:ZT210801.PNT | 10HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1086 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211802.OUT | 1RHTTEM:AO211802.OUT | 10HHA30KV002XB11 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
989 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210802.PNT | 1QDAS:ZT210802.PNT | 10HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1055 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAA:AO211403.OUT | 1AUXDAMPAA:AO211403.OUT | 10HLA31AA001XB11 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
958 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210403.PNT | 1QDAS:ZT210403.PNT | 10HLA31AA001XB12 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1056 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPA:AO211404.OUT | 1CYCDAMPA:AO211404.OUT | 10HLA31AA002XB11 | 3# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
959 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210404.PNT | 1QDAS:ZT210404.PNT | 10HLA31AA002XB12 | 3# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1057 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAB:AO211405.OUT | 1AUXDAMPAB:AO211405.OUT | 10HLA31AA003XB11 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
960 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210405.PNT | 1QDAS:ZT210405.PNT | 10HLA31AA003XB12 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
175 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163504.PNT | 1MDAS:FT163504.PNT | 10HFF14CF201 | 4# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
5 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130605.PNT | 1JDAS:AI130605.PNT | 10HHA14CB201B | 4# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1087 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211803.OUT | 1RHTTEM:AO211803.OUT | 10HHA40KV001XB11 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
990 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210803.PNT | 1QDAS:ZT210803.PNT | 10HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1088 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1RHTTEM:AO211804.OUT | 1RHTTEM:AO211804.OUT | 10HHA40KV002XB11 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
991 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-34 | OPC.1QDAS:ZT210804.PNT | 1QDAS:ZT210804.PNT | 10HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1068 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAA:AO211508.OUT | 1AUXDAMPAA:AO211508.OUT | 10HLA41AA001XB11 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
971 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210508.PNT | 1QDAS:ZT210508.PNT | 10HLA41AA001XB12 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1069 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPA:AO211601.OUT | 1CYCDAMPA:AO211601.OUT | 10HLA41AA002XB11 | 4# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
972 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210601.PNT | 1QDAS:ZT210601.PNT | 10HLA41AA002XB12 | 4# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1070 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPAB:AO211602.OUT | 1AUXDAMPAB:AO211602.OUT | 10HLA41AA003XB11 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
973 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210602.PNT | 1QDAS:ZT210602.PNT | 10HLA41AA003XB12 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
35 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 11 | COAL FEEDER #10B | 50-F290S-J0201-03 | OPC.1LDAS:FT150303.PNT | 1LDAS:FT150303.PNT | 10HFB20GC001AI01 | ECF B INSTANTANEOUS FEED RATE | AI | 0 | 60
57 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 11 | COAL FEEDER #10B | 50-F290S-J0201-03 | OPC.1LDAS:AO150403.OUT | 1LDAS:AO150403.OUT | 10HFB20GC001AO01 | ECF B FEED RATE COMMAND | AO | 0 | 60
52 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1LDAS:AI150703.PNT | 1LDAS:AI150703.PNT | 10HFC10GC003AI02 | MSM B OUTLET CO CONTENT | AI | 0 | 100 | %
16 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-03 | OPC.1JDAS:CT130708.PNT | 1JDAS:CT130708.PNT | 10HFC20AJ001XB13 | MSM B CURRENT | AI | 0 | 75 | A
75 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130301.PNT | 1JDAS:RT130301.PNT | 10HFC20CT001 | MSM B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
82 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130401.PNT | 1JDAS:RT130401.PNT | 10HFC20CT002 | MSM B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
76 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130302.PNT | 1JDAS:RT130302.PNT | 10HFC20CT003 | MSM B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
83 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130402.PNT | 1JDAS:RT130402.PNT | 10HFC20CT004 | MSM B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
77 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130303.PNT | 1JDAS:RT130303.PNT | 10HFC20CT005 | MSM B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
84 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130403.PNT | 1JDAS:RT130403.PNT | 10HFC20CT006 | MSM B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
78 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130304.PNT | 1JDAS:RT130304.PNT | 10HFC20CT007 | MSM B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
85 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130404.PNT | 1JDAS:RT130404.PNT | 10HFC20CT008 | MSM B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
79 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130305.PNT | 1JDAS:RT130305.PNT | 10HFC20CT009 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
80 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130306.PNT | 1JDAS:RT130306.PNT | 10HFC20CT010 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
86 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130405.PNT | 1JDAS:RT130405.PNT | 10HFC20CT011 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
87 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130406.PNT | 1JDAS:RT130406.PNT | 10HFC20CT012 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
81 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130307.PNT | 1JDAS:RT130307.PNT | 10HFC20CT013 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
88 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130407.PNT | 1JDAS:RT130407.PNT | 10HFC20CT014 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
92 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130504.PNT | 1JDAS:RT130504.PNT | 10HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1091 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1PDAS:RT201702.PNT | 1PDAS:RT201702.PNT | 10HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1096 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1PDAS:RT201802.PNT | 1PDAS:RT201802.PNT | 10HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
93 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130505.PNT | 1JDAS:RT130505.PNT | 10HFC20CT018 | MSM B LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
94 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1JDAS:RT130506.PNT | 1JDAS:RT130506.PNT | 10HFC20CT019 | MSM B LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
171 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1MDAS:PT163404.PNT | 1MDAS:PT163404.PNT | 10HFC20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4 | %
9 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1JDAS:PT130701.PNT | 1JDAS:PT130701.PNT | 10HFE20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1001 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1MILLBHCAD:AO202202.OUT | 1MILLBHCAD:AO202202.OUT | 10HFE42AA101XB11 | MSM B INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
847 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT200205.PNT | 1PDAS:ZT200205.PNT | 10HFE42AA101XB12 | MSM B INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1000 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1MILLBHCAD:AO202201.OUT | 1MILLBHCAD:AO202201.OUT | 10HFE52AA101XB11 | MSM B INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
846 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT200204.PNT | 1PDAS:ZT200204.PNT | 10HFE52AA101XB12 | MSM B INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1002 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1MILLBPAD:AO202203.OUT | 1MILLBPAD:AO202203.OUT | 10HFE52AA102XB11 | MSM B INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
848 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT200206.PNT | 1PDAS:ZT200206.PNT | 10HFE52AA102XB12 | MSM B INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
844 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:FT200202.PNT | 1PDAS:FT200202.PNT | 10HFE52CF201 | MSM B INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
845 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:FT200203.PNT | 1PDAS:FT200203.PNT | 10HFE52CF202 | MSM B INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
843 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:PT200201.PNT | 1PDAS:PT200201.PNT | 10HFE52CP201 | MSM B INLET AIR PRESSURE | AI | 0 | 20 | KPa
1101 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-02 | OPC.1PDAS:TE202602.PNT | 1PDAS:TE202602.PNT | 10HFE52CT001 | MSM B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1VMS2:AIN7.PNT | 1VMS2:AIN7.PNT | 10HFC20CY001X | #10 MSM B BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #10B | 50-F290S-J0201-35 | OPC.1VMS2:AIN8.PNT | 1VMS2:AIN8.PNT | 10HFC20CY001Y | #10 MSM B BEARING VIBRATION Y | AI | 0 | 20 | µm
176 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163505.PNT | 1MDAS:FT163505.PNT | 10HFF21CF201 | 1# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
10 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130702.PNT | 1JDAS:AI130702.PNT | 10HHA21CB201B | 1# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1032 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPB:AO211104.OUT | 1CYCDAMPB:AO211104.OUT | 10HLA11AA004XB11 | 1# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
935 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210104.PNT | 1QDAS:ZT210104.PNT | 10HLA11AA004XB12 | 1# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1033 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPBC:AO211105.OUT | 1AUXDAMPBC:AO211105.OUT | 10HLA11AA005XB11 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
936 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210105.PNT | 1QDAS:ZT210105.PNT | 10HLA11AA005XB12 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
177 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163506.PNT | 1MDAS:FT163506.PNT | 10HFF22CF201 | 2# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
11 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130703.PNT | 1JDAS:AI130703.PNT | 10HHA22CB201B | 2# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1045 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPB:AO211301.OUT | 1CYCDAMPB:AO211301.OUT | 10HLA21AA004XB11 | 2# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
948 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210301.PNT | 1QDAS:ZT210301.PNT | 10HLA21AA004XB12 | 2# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1046 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPBC:AO211302.OUT | 1AUXDAMPBC:AO211302.OUT | 10HLA21AA005XB11 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
949 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210302.PNT | 1QDAS:ZT210302.PNT | 10HLA21AA005XB12 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
178 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163507.PNT | 1MDAS:FT163507.PNT | 10HFF23CF201 | 3# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
12 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130704.PNT | 1JDAS:AI130704.PNT | 10HHA23CB201B | 3# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1058 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPB:AO211406.OUT | 1CYCDAMPB:AO211406.OUT | 10HLA31AA004XB11 | 3# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
961 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210406.PNT | 1QDAS:ZT210406.PNT | 10HLA31AA004XB12 | 3# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1059 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPBC:AO211407.OUT | 1AUXDAMPBC:AO211407.OUT | 10HLA31AA005XB11 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
962 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210407.PNT | 1QDAS:ZT210407.PNT | 10HLA31AA005XB12 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
179 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1MDAS:FT163508.PNT | 1MDAS:FT163508.PNT | 10HFF24CF201 | 4# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
13 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1JDAS:AI130705.PNT | 1JDAS:AI130705.PNT | 10HHA24CB201B | 4# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1071 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPB:AO211603.OUT | 1CYCDAMPB:AO211603.OUT | 10HLA41AA004XB11 | 4# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
974 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210603.PNT | 1QDAS:ZT210603.PNT | 10HLA41AA004XB12 | 4# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1072 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPBC:AO211604.OUT | 1AUXDAMPBC:AO211604.OUT | 10HLA41AA005XB11 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
975 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210604.PNT | 1QDAS:ZT210604.PNT | 10HLA41AA005XB12 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
36 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 18 | COAL FEEDER #10C | 50-F290S-J0201-03 | OPC.1LDAS:FT150304.PNT | 1LDAS:FT150304.PNT | 10HFB30GC001AI01 | ECF C INSTANTANEOUS FEED RATE | AI | 0 | 60
58 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 18 | COAL FEEDER #10C | 50-F290S-J0201-03 | OPC.1LDAS:AO150404.OUT | 1LDAS:AO150404.OUT | 10HFB30GC001AO01 | ECF C FEED RATE COMMAND | AO | 0 | 60
53 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1LDAS:AI150704.PNT | 1LDAS:AI150704.PNT | 10HFC10GC003AI03 | MSM C OUTLET CO CONTENT | AI | 0 | 100 | %
24 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-03 | OPC.1KDAS:CT140608.PNT | 1KDAS:CT140608.PNT | 10HFC30AJ001XB13 | MSM C CURRENT | AI | 0 | 75 | A
95 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140101.PNT | 1KDAS:RT140101.PNT | 10HFC30CT001 | MSM C MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
102 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140201.PNT | 1KDAS:RT140201.PNT | 10HFC30CT002 | MSM C MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
96 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140102.PNT | 1KDAS:RT140102.PNT | 10HFC30CT003 | MSM C MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
103 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140202.PNT | 1KDAS:RT140202.PNT | 10HFC30CT004 | MSM C MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
97 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140103.PNT | 1KDAS:RT140103.PNT | 10HFC30CT005 | MSM C MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
104 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140203.PNT | 1KDAS:RT140203.PNT | 10HFC30CT006 | MSM C MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
98 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140104.PNT | 1KDAS:RT140104.PNT | 10HFC30CT007 | MSM C MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
105 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140204.PNT | 1KDAS:RT140204.PNT | 10HFC30CT008 | MSM C MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
99 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140105.PNT | 1KDAS:RT140105.PNT | 10HFC30CT009 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
100 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140106.PNT | 1KDAS:RT140106.PNT | 10HFC30CT010 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
106 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140205.PNT | 1KDAS:RT140205.PNT | 10HFC30CT011 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
107 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140206.PNT | 1KDAS:RT140206.PNT | 10HFC30CT012 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
101 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140107.PNT | 1KDAS:RT140107.PNT | 10HFC30CT013 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
108 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140207.PNT | 1KDAS:RT140207.PNT | 10HFC30CT014 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
123 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140501.PNT | 1KDAS:RT140501.PNT | 10HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1092 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1PDAS:RT201703.PNT | 1PDAS:RT201703.PNT | 10HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1097 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1PDAS:RT201803.PNT | 1PDAS:RT201803.PNT | 10HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
124 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140502.PNT | 1KDAS:RT140502.PNT | 10HFC30CT018 | MSM C LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
125 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1KDAS:RT140503.PNT | 1KDAS:RT140503.PNT | 10HFC30CT019 | MSM C LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
202 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1NDAS:PT183403.PNT | 1NDAS:PT183403.PNT | 10HFC30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
17 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1KDAS:PT140601.PNT | 1KDAS:PT140601.PNT | 10HFE30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1009 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1MILLCHCAD:AO202302.OUT | 1MILLCHCAD:AO202302.OUT | 10HFE43AA101XB11 | MSM C INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
853 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:ZT200305.PNT | 1PDAS:ZT200305.PNT | 10HFE43AA101XB12 | MSM C INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1008 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1MILLCHCAD:AO202301.OUT | 1MILLCHCAD:AO202301.OUT | 10HFE53AA101XB11 | MSM C INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
852 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:ZT200304.PNT | 1PDAS:ZT200304.PNT | 10HFE53AA101XB12 | MSM C INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1010 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1MILLCPAD:AO202303.OUT | 1MILLCPAD:AO202303.OUT | 10HFE53AA102XB11 | MSM C INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
854 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:ZT200306.PNT | 1PDAS:ZT200306.PNT | 10HFE53AA102XB12 | MSM C INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
850 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:FT200302.PNT | 1PDAS:FT200302.PNT | 10HFE53CF201 | MSM C INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
851 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:FT200303.PNT | 1PDAS:FT200303.PNT | 10HFE53CF202 | MSM C INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
849 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:PT200301.PNT | 1PDAS:PT200301.PNT | 10HFE53CP201 | MSM C INLET AIR PRESSURE | AI | 0 | 20 | KPa
1102 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-02 | OPC.1PDAS:TE202603.PNT | 1PDAS:TE202603.PNT | 10HFE53CT001 | MSM C INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1VMS2:AIN9.PNT | 1VMS2:AIN9.PNT | 10HFC30CY001X | #10 MSM C BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #10C | 50-F290S-J0201-35 | OPC.1VMS2:AIN10.PNT | 1VMS2:AIN10.PNT | 10HFC30CY001Y | #10 MSM C BEARING VIBRATION Y | AI | 0 | 20 | µm
206 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183501.PNT | 1NDAS:FT183501.PNT | 10HFF31CF201 | 1# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
18 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140602.PNT | 1KDAS:AI140602.PNT | 10HHA31CB201B | 1# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1034 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPC:AO211106.OUT | 1CYCDAMPC:AO211106.OUT | 10HLA11AA006XB11 | 1# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
937 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210106.PNT | 1QDAS:ZT210106.PNT | 10HLA11AA006XB12 | 1# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1035 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPCC:AO211107.OUT | 1AUXDAMPCC:AO211107.OUT | 10HLA11AA007XB11 | 1#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
938 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210107.PNT | 1QDAS:ZT210107.PNT | 10HLA11AA007XB12 | 1# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
207 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183502.PNT | 1NDAS:FT183502.PNT | 10HFF32CF201 | 2# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
19 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140603.PNT | 1KDAS:AI140603.PNT | 10HHA32CB201B | 2# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1047 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPC:AO211303.OUT | 1CYCDAMPC:AO211303.OUT | 10HLA21AA006XB11 | 2# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
950 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210303.PNT | 1QDAS:ZT210303.PNT | 10HLA21AA006XB12 | 2# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1048 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPCC:AO211304.OUT | 1AUXDAMPCC:AO211304.OUT | 10HLA21AA007XB11 | 2#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
951 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210304.PNT | 1QDAS:ZT210304.PNT | 10HLA21AA007XB12 | 2# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
208 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183503.PNT | 1NDAS:FT183503.PNT | 10HFF33CF201 | 3# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
20 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140604.PNT | 1KDAS:AI140604.PNT | 10HHA33CB201B | 3# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1060 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPC:AO211408.OUT | 1CYCDAMPC:AO211408.OUT | 10HLA31AA006XB11 | 3# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
963 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210408.PNT | 1QDAS:ZT210408.PNT | 10HLA31AA006XB12 | 3# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1061 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPCC:AO211501.OUT | 1AUXDAMPCC:AO211501.OUT | 10HLA31AA007XB11 | 3#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
964 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210501.PNT | 1QDAS:ZT210501.PNT | 10HLA31AA007XB12 | 3# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
209 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183504.PNT | 1NDAS:FT183504.PNT | 10HFF34CF201 | 4# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
21 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140605.PNT | 1KDAS:AI140605.PNT | 10HHA34CB201B | 4# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1073 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPC:AO211605.OUT | 1CYCDAMPC:AO211605.OUT | 10HLA41AA006XB11 | 4# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
976 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210605.PNT | 1QDAS:ZT210605.PNT | 10HLA41AA006XB12 | 4# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1074 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPCC:AO211606.OUT | 1AUXDAMPCC:AO211606.OUT | 10HLA41AA007XB11 | 4#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
977 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210606.PNT | 1QDAS:ZT210606.PNT | 10HLA41AA007XB12 | 4# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
37 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 25 | COAL FEEDER #10D | 50-F290S-J0201-03 | OPC.1LDAS:FT150305.PNT | 1LDAS:FT150305.PNT | 10HFB40GC001AI01 | ECF D INSTANTANEOUS FEED RATE | AI | 0 | 60
59 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 25 | COAL FEEDER #10D | 50-F290S-J0201-03 | OPC.1LDAS:AO150405.OUT | 1LDAS:AO150405.OUT | 10HFB40GC001AO01 | ECF D FEED RATE COMMAND | AO | 0 | 60
54 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1LDAS:AI150705.PNT | 1LDAS:AI150705.PNT | 10HFC10GC003AI04 | MSM D OUTLET CO CONTENT | AI | 0 | 100 | %
32 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-03 | OPC.1KDAS:CT140708.PNT | 1KDAS:CT140708.PNT | 10HFC40AJ001XB13 | MSM D CURRENT | AI | 0 | 75 | A
109 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140301.PNT | 1KDAS:RT140301.PNT | 10HFC40CT001 | MSM D MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
116 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140401.PNT | 1KDAS:RT140401.PNT | 10HFC40CT002 | MSM D MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
110 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140302.PNT | 1KDAS:RT140302.PNT | 10HFC40CT003 | MSM D MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
117 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140402.PNT | 1KDAS:RT140402.PNT | 10HFC40CT004 | MSM D MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
111 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140303.PNT | 1KDAS:RT140303.PNT | 10HFC40CT005 | MSM D MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
118 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140403.PNT | 1KDAS:RT140403.PNT | 10HFC40CT006 | MSM D MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
112 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140304.PNT | 1KDAS:RT140304.PNT | 10HFC40CT007 | MSM D MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
119 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140404.PNT | 1KDAS:RT140404.PNT | 10HFC40CT008 | MSM D MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
113 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140305.PNT | 1KDAS:RT140305.PNT | 10HFC40CT009 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
114 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140306.PNT | 1KDAS:RT140306.PNT | 10HFC40CT010 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
120 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140405.PNT | 1KDAS:RT140405.PNT | 10HFC40CT011 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
121 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140406.PNT | 1KDAS:RT140406.PNT | 10HFC40CT012 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
115 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140307.PNT | 1KDAS:RT140307.PNT | 10HFC40CT013 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
122 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140407.PNT | 1KDAS:RT140407.PNT | 10HFC40CT014 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
126 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140504.PNT | 1KDAS:RT140504.PNT | 10HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1093 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1PDAS:RT201704.PNT | 1PDAS:RT201704.PNT | 10HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1098 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1PDAS:RT201804.PNT | 1PDAS:RT201804.PNT | 10HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
127 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140505.PNT | 1KDAS:RT140505.PNT | 10HFC40CT018 | MSM D LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
128 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1KDAS:RT140506.PNT | 1KDAS:RT140506.PNT | 10HFC40CT019 | MSM D LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
203 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1NDAS:PT183404.PNT | 1NDAS:PT183404.PNT | 10HFC40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
25 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1KDAS:PT140701.PNT | 1KDAS:PT140701.PNT | 10HFE40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1016 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1MILLDHCAD:AO202402.OUT | 1MILLDHCAD:AO202402.OUT | 10HFE44AA101XB11 | MSM D INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
859 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:ZT200405.PNT | 1PDAS:ZT200405.PNT | 10HFE44AA101XB12 | MSM D INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1015 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1MILLDHCAD:AO202401.OUT | 1MILLDHCAD:AO202401.OUT | 10HFE54AA101XB11 | MSM D INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
858 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:ZT200404.PNT | 1PDAS:ZT200404.PNT | 10HFE54AA101XB12 | MSM D INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1017 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1MILLDPAD:AO202403.OUT | 1MILLDPAD:AO202403.OUT | 10HFE54AA102XB11 | MSM D INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
860 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:ZT200406.PNT | 1PDAS:ZT200406.PNT | 10HFE54AA102XB12 | MSM D INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
856 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:FT200402.PNT | 1PDAS:FT200402.PNT | 10HFE54CF201 | MSM D INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
857 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:FT200403.PNT | 1PDAS:FT200403.PNT | 10HFE54CF202 | MSM D INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
855 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:PT200401.PNT | 1PDAS:PT200401.PNT | 10HFE54CP201 | MSM D INLET AIR PRESSURE | AI | 0 | 20 | KPa
1103 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-02 | OPC.1PDAS:TE202604.PNT | 1PDAS:TE202604.PNT | 10HFE54CT001 | MSM D INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1VMS2:AIN11.PNT | 1VMS2:AIN11.PNT | 10HFC40CY001X | #10 MSM D BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #10D | 50-F290S-J0201-35 | OPC.1VMS2:AIN12.PNT | 1VMS2:AIN12.PNT | 10HFC40CY001Y | #10 MSM D BEARING VIBRATION Y | AI | 0 | 20 | µm
210 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183505.PNT | 1NDAS:FT183505.PNT | 10HFF41CF201 | 1# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
26 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140702.PNT | 1KDAS:AI140702.PNT | 10HHA41CB201B | 1# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1036 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDD:AO211108.OUT | 1AUXDAMPDD:AO211108.OUT | 10HLA11AA008XB11 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
939 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210108.PNT | 1QDAS:ZT210108.PNT | 10HLA11AA008XB12 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1037 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPD:AO211201.OUT | 1CYCDAMPD:AO211201.OUT | 10HLA11AA009XB11 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
940 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210201.PNT | 1QDAS:ZT210201.PNT | 10HLA11AA009XB12 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1038 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDE:AO211202.OUT | 1AUXDAMPDE:AO211202.OUT | 10HLA11AA010XB11 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
941 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210202.PNT | 1QDAS:ZT210202.PNT | 10HLA11AA010XB12 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
211 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183506.PNT | 1NDAS:FT183506.PNT | 10HFF42CF201 | 2# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
27 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140703.PNT | 1KDAS:AI140703.PNT | 10HHA42CB201B | 2# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1049 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDD:AO211305.OUT | 1AUXDAMPDD:AO211305.OUT | 10HLA21AA008XB11 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
952 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210305.PNT | 1QDAS:ZT210305.PNT | 10HLA21AA008XB12 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1050 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPD:AO211306.OUT | 1CYCDAMPD:AO211306.OUT | 10HLA21AA009XB11 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
953 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210306.PNT | 1QDAS:ZT210306.PNT | 10HLA21AA009XB12 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1051 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDE:AO211307.OUT | 1AUXDAMPDE:AO211307.OUT | 10HLA21AA010XB11 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
954 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210307.PNT | 1QDAS:ZT210307.PNT | 10HLA21AA010XB12 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
212 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183507.PNT | 1NDAS:FT183507.PNT | 10HFF43CF201 | 3# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
28 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140704.PNT | 1KDAS:AI140704.PNT | 10HHA43CB201B | 3# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1062 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDD:AO211502.OUT | 1AUXDAMPDD:AO211502.OUT | 10HLA31AA008XB11 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
965 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210502.PNT | 1QDAS:ZT210502.PNT | 10HLA31AA008XB12 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1063 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPD:AO211503.OUT | 1CYCDAMPD:AO211503.OUT | 10HLA31AA009XB11 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
966 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210503.PNT | 1QDAS:ZT210503.PNT | 10HLA31AA009XB12 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1064 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDE:AO211504.OUT | 1AUXDAMPDE:AO211504.OUT | 10HLA31AA010XB11 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
967 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210504.PNT | 1QDAS:ZT210504.PNT | 10HLA31AA010XB12 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
213 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1NDAS:FT183508.PNT | 1NDAS:FT183508.PNT | 10HFF44CF201 | 4# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
29 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1KDAS:AI140705.PNT | 1KDAS:AI140705.PNT | 10HHA44CB201B | 4# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1075 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDD:AO211607.OUT | 1AUXDAMPDD:AO211607.OUT | 10HLA41AA008XB11 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
978 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210607.PNT | 1QDAS:ZT210607.PNT | 10HLA41AA008XB12 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1076 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPD:AO211608.OUT | 1CYCDAMPD:AO211608.OUT | 10HLA41AA009XB11 | 4# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
979 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210608.PNT | 1QDAS:ZT210608.PNT | 10HLA41AA009XB12 | 4# CORNER D LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1077 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPDE:AO211701.OUT | 1AUXDAMPDE:AO211701.OUT | 10HLA41AA010XB11 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
980 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210701.PNT | 1QDAS:ZT210701.PNT | 10HLA41AA010XB12 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
38 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 32 | COAL FEEDER #10E | 50-F290S-J0201-03 | OPC.1LDAS:FT150306.PNT | 1LDAS:FT150306.PNT | 10HFB50GC001AI01 | ECF E INSTANTANEOUS FEED RATE | AI | 0 | 60
60 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 32 | COAL FEEDER #10E | 50-F290S-J0201-03 | OPC.1LDAS:AO150406.OUT | 1LDAS:AO150406.OUT | 10HFB50GC001AO01 | ECF E FEED RATE COMMAND | AO | 0 | 60
55 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:AI150708.PNT | 1LDAS:AI150708.PNT | 10HFC10GC003AI05 | MSM E OUTLET CO CONTENT | AI | 0 | 100 | %
47 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-03 | OPC.1LDAS:CT150608.PNT | 1LDAS:CT150608.PNT | 10HFC50AJ001XB13 | MSM E CURRENT | AI | 0 | 75 | A
129 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150101.PNT | 1LDAS:RT150101.PNT | 10HFC50CT001 | MSM E MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
136 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150201.PNT | 1LDAS:RT150201.PNT | 10HFC50CT002 | MSM E MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
130 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150102.PNT | 1LDAS:RT150102.PNT | 10HFC50CT003 | MSM E MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
137 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150202.PNT | 1LDAS:RT150202.PNT | 10HFC50CT004 | MSM E MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
131 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150103.PNT | 1LDAS:RT150103.PNT | 10HFC50CT005 | MSM E MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
138 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150203.PNT | 1LDAS:RT150203.PNT | 10HFC50CT006 | MSM E MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
132 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150104.PNT | 1LDAS:RT150104.PNT | 10HFC50CT007 | MSM E MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
139 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150204.PNT | 1LDAS:RT150204.PNT | 10HFC50CT008 | MSM E MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
133 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150105.PNT | 1LDAS:RT150105.PNT | 10HFC50CT009 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
134 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150106.PNT | 1LDAS:RT150106.PNT | 10HFC50CT010 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
140 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150205.PNT | 1LDAS:RT150205.PNT | 10HFC50CT011 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
141 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150206.PNT | 1LDAS:RT150206.PNT | 10HFC50CT012 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
135 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150107.PNT | 1LDAS:RT150107.PNT | 10HFC50CT013 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
142 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150207.PNT | 1LDAS:RT150207.PNT | 10HFC50CT014 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
143 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150501.PNT | 1LDAS:RT150501.PNT | 10HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1094 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1PDAS:RT201705.PNT | 1PDAS:RT201705.PNT | 10HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1099 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1PDAS:RT201805.PNT | 1PDAS:RT201805.PNT | 10HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
144 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150502.PNT | 1LDAS:RT150502.PNT | 10HFC50CT018 | MSM E LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
145 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1LDAS:RT150503.PNT | 1LDAS:RT150503.PNT | 10HFC50CT019 | MSM E LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
230 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1ODAS:PT193304.PNT | 1ODAS:PT193304.PNT | 10HFC50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
1023 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1MILLEHCAD:AO202502.OUT | 1MILLEHCAD:AO202502.OUT | 10HFE45AA101XB11 | MSM E INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
865 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:ZT200505.PNT | 1PDAS:ZT200505.PNT | 10HFE45AA101XB12 | MSM E INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
40 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1LDAS:PT150601.PNT | 1LDAS:PT150601.PNT | 10HFE50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1022 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1MILLEHCAD:AO202501.OUT | 1MILLEHCAD:AO202501.OUT | 10HFE55AA101XB11 | MSM E INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
864 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:ZT200504.PNT | 1PDAS:ZT200504.PNT | 10HFE55AA101XB12 | MSM E INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1024 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1MILLEPAD:AO202503.OUT | 1MILLEPAD:AO202503.OUT | 10HFE55AA102XB11 | MSM E INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
866 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:ZT200506.PNT | 1PDAS:ZT200506.PNT | 10HFE55AA102XB12 | MSM E INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
862 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:FT200502.PNT | 1PDAS:FT200502.PNT | 10HFE55CF201 | MSM E INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
863 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:FT200503.PNT | 1PDAS:FT200503.PNT | 10HFE55CF202 | MSM E INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
861 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:PT200501.PNT | 1PDAS:PT200501.PNT | 10HFE55CP201 | MSM E INLET AIR PRESSURE | AI | 0 | 20 | KPa
1104 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-02 | OPC.1PDAS:TE202605.PNT | 1PDAS:TE202605.PNT | 10HFE55CT001 | MSM E INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1VMS2:AIN13.PNT | 1VMS2:AIN13.PNT | 10HFC50CY001X | #10 MSM E BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #10E | 50-F290S-J0201-35 | OPC.1VMS2:AIN14.PNT | 1VMS2:AIN14.PNT | 10HFC50CY001Y | #10 MSM E BEARING VIBRATION Y | AI | 0 | 20 | µm
231 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1ODAS:FT193305.PNT | 1ODAS:FT193305.PNT | 10HFF51CF201 | 1# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
41 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1LDAS:AI150602.PNT | 1LDAS:AI150602.PNT | 10HHA51CB201B | 1# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1039 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPE:AO211203.OUT | 1CYCDAMPE:AO211203.OUT | 10HLA11AA011XB11 | 1# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
942 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210203.PNT | 1QDAS:ZT210203.PNT | 10HLA11AA011XB12 | 1# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1040 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPEF:AO211204.OUT | 1AUXDAMPEF:AO211204.OUT | 10HLA11AA012XB11 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
943 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210204.PNT | 1QDAS:ZT210204.PNT | 10HLA11AA012XB12 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1041 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1BUTDAMEFF:AO211205.OUT | 1BUTDAMEFF:AO211205.OUT | 10HLA11AA013XB11 | 1# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
944 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210205.PNT | 1QDAS:ZT210205.PNT | 10HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
232 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1ODAS:FT193306.PNT | 1ODAS:FT193306.PNT | 10HFF52CF201 | 2# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
42 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1LDAS:AI150603.PNT | 1LDAS:AI150603.PNT | 10HHA52CB201B | 2# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1052 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPE:AO211308.OUT | 1CYCDAMPE:AO211308.OUT | 10HLA21AA011XB11 | 2# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
955 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210308.PNT | 1QDAS:ZT210308.PNT | 10HLA21AA011XB12 | 2# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1053 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPEF:AO211401.OUT | 1AUXDAMPEF:AO211401.OUT | 10HLA21AA012XB11 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
956 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210401.PNT | 1QDAS:ZT210401.PNT | 10HLA21AA012XB12 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1054 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1BUTDAMEFF:AO211402.OUT | 1BUTDAMEFF:AO211402.OUT | 10HLA21AA013XB11 | 2# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
957 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210402.PNT | 1QDAS:ZT210402.PNT | 10HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
233 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1ODAS:FT193307.PNT | 1ODAS:FT193307.PNT | 10HFF53CF201 | 3# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
43 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1LDAS:AI150604.PNT | 1LDAS:AI150604.PNT | 10HHA53CB201B | 3# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1065 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPE:AO211505.OUT | 1CYCDAMPE:AO211505.OUT | 10HLA31AA011XB11 | 3# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
968 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210505.PNT | 1QDAS:ZT210505.PNT | 10HLA31AA011XB12 | 3# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1066 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPEF:AO211506.OUT | 1AUXDAMPEF:AO211506.OUT | 10HLA31AA012XB11 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
969 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210506.PNT | 1QDAS:ZT210506.PNT | 10HLA31AA012XB12 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1067 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1BUTDAMEFF:AO211507.OUT | 1BUTDAMEFF:AO211507.OUT | 10HLA31AA013XB11 | 3# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
970 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210507.PNT | 1QDAS:ZT210507.PNT | 10HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
234 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1ODAS:FT193308.PNT | 1ODAS:FT193308.PNT | 10HFF54CF201 | 4# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
44 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1LDAS:AI150605.PNT | 1LDAS:AI150605.PNT | 10HHA54CB201B | 4# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1078 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1CYCDAMPE:AO211702.OUT | 1CYCDAMPE:AO211702.OUT | 10HLA41AA011XB11 | 4# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
981 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210702.PNT | 1QDAS:ZT210702.PNT | 10HLA41AA011XB12 | 4# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1079 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1AUXDAMPEF:AO211703.OUT | 1AUXDAMPEF:AO211703.OUT | 10HLA41AA012XB11 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
982 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210703.PNT | 1QDAS:ZT210703.PNT | 10HLA41AA012XB12 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1080 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1BUTDAMEFF:AO211704.OUT | 1BUTDAMEFF:AO211704.OUT | 10HLA41AA013XB11 | 4# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
983 | 2 | UJRBG #10 | 5 | PULVERIZER SYSTEM#1 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #10 | 50-F290S-J0201-03 | OPC.1QDAS:ZT210704.PNT | 1QDAS:ZT210704.PNT | 10HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
154 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER TUBE #10 | 50-F290S-J0201-02 | OPC.1MDAS:PT163201.PNT | 1MDAS:PT163201.PNT | 10HNA10CP201 | A SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa
314 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER TUBE #10 | 50-F290S-J0201-02 | OPC.1MDAS:TE162603.PNT | 1MDAS:TE162603.PNT | 10HNA10CT001 | A SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | °C
186 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER TUBE #10 | 50-F290S-J0201-02 | OPC.1NDAS:PT183201.PNT | 1NDAS:PT183201.PNT | 10HNA20CP201 | B SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa
328 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER TUBE #10 | 50-F290S-J0201-02 | OPC.1NDAS:TE182603.PNT | 1NDAS:TE182603.PNT | 10HNA20CT001 | B SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
869 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:LT200603.PNT | 1PDAS:LT200603.PNT | 10HAG10CL201 | DRUM LEVEL | AI | -300 | 300 | mm
875 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:LT200703.PNT | 1PDAS:LT200703.PNT | 10HAG10CL202 | DRUM LEVEL | AI | -300 | 300 | mm
883 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:LT200803.PNT | 1PDAS:LT200803.PNT | 10HAG10CL203 | DRUM LEVEL | AI | -300 | 300 | mm
868 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:PT200602.PNT | 1PDAS:PT200602.PNT | 10HAG10CP201 | DRUM PRESSURE | AI | 0 | 20 | MPa
874 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:PT200702.PNT | 1PDAS:PT200702.PNT | 10HAG10CP202 | DRUM PRESSURE | AI | 0 | 20 | MPa
882 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #10 | 50-F290S-J0201-04 | OPC.1PDAS:PT200802.PNT | 1PDAS:PT200802.PNT | 10HAG10CP203 | DRUM PRESSURE | AI | 0 | 20 | MPa
1268 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254301.PNT | 1ODAS:TE254301.PNT | 10HAG10CT001 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1276 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254401.PNT | 1ODAS:TE254401.PNT | 10HAG10CT002 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1284 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254501.PNT | 1ODAS:TE254501.PNT | 10HAG10CT003 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1291 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254601.PNT | 1ODAS:TE254601.PNT | 10HAG10CT004 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1298 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254701.PNT | 1ODAS:TE254701.PNT | 10HAG10CT005 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1305 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254801.PNT | 1ODAS:TE254801.PNT | 10HAG10CT006 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1311 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255101.PNT | 1ODAS:TE255101.PNT | 10HAG10CT007 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1269 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254302.PNT | 1ODAS:TE254302.PNT | 10HAG10CT008 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1270 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254303.PNT | 1ODAS:TE254303.PNT | 10HAG10CT009 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1277 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254402.PNT | 1ODAS:TE254402.PNT | 10HAG10CT010 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1278 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254403.PNT | 1ODAS:TE254403.PNT | 10HAG10CT011 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1271 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254304.PNT | 1ODAS:TE254304.PNT | 10HAG10CT012 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 5th TUBE | TC | 0 | 600 | °C
1279 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WATER WALL TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254404.PNT | 1ODAS:TE254404.PNT | 10HAG10CT013 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 12th TUBE | TC | 0 | 600 | °C
167 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1MDAS:PT163307.PNT | 1MDAS:PT163307.PNT | 10H10CP205 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa
923 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1PDAS:AI201506.PNT | 1PDAS:AI201506.PNT | 10H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
930 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1PDAS:AI201606.PNT | 1PDAS:AI201606.PNT | 10H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
325 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1MDAS:TE162707.PNT | 1MDAS:TE162707.PNT | 10H10CT009 | A SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | °C
199 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1NDAS:PT183307.PNT | 1NDAS:PT183307.PNT | 10H20CP205 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa
924 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1PDAS:AI201507.PNT | 1PDAS:AI201507.PNT | 10H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
931 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-34 | OPC.1PDAS:AI201607.PNT | 1PDAS:AI201607.PNT | 10H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
1272 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254305.PNT | 1ODAS:TE254305.PNT | 10HAH10CT001 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1273 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254306.PNT | 1ODAS:TE254306.PNT | 10HAH10CT002 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1280 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254405.PNT | 1ODAS:TE254405.PNT | 10HAH10CT003 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1281 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254406.PNT | 1ODAS:TE254406.PNT | 10HAH10CT004 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1285 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254502.PNT | 1ODAS:TE254502.PNT | 10HAH10CT005 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 4th | TC | 0 | 600 | °C
1286 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254503.PNT | 1ODAS:TE254503.PNT | 10HAH10CT006 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 7th | TC | 0 | 600 | °C
1292 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254602.PNT | 1ODAS:TE254602.PNT | 10HAH10CT007 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 10th | TC | 0 | 600 | °C
1293 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254603.PNT | 1ODAS:TE254603.PNT | 10HAH10CT008 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 12th | TC | 0 | 600 | °C
1299 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254702.PNT | 1ODAS:TE254702.PNT | 10HAH10CT009 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FEOM LEFT 15th | TC | 0 | 600 | °C
1300 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254703.PNT | 1ODAS:TE254703.PNT | 10HAH10CT010 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 18th | TC | 0 | 600 | °C
1287 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254504.PNT | 1ODAS:TE254504.PNT | 10HAH10CT011 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1288 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254505.PNT | 1ODAS:TE254505.PNT | 10HAH10CT012 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1294 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254604.PNT | 1ODAS:TE254604.PNT | 10HAH10CT013 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1295 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254605.PNT | 1ODAS:TE254605.PNT | 10HAH10CT014 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1301 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254704.PNT | 1ODAS:TE254704.PNT | 10HAH10CT015 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1302 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254705.PNT | 1ODAS:TE254705.PNT | 10HAH10CT016 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1274 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254307.PNT | 1ODAS:TE254307.PNT | 10HAH10CT017 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LE | TC | 0 | 600 | °C
1275 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254308.PNT | 1ODAS:TE254308.PNT | 10HAH10CT018 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LE | TC | 0 | 600 | °C
1282 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254407.PNT | 1ODAS:TE254407.PNT | 10HAH10CT019 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1283 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254408.PNT | 1ODAS:TE254408.PNT | 10HAH10CT020 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
339 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193401.PNT | 1ODAS:TE193401.PNT | 10HAH11CT001 | SUPERHEATER 1st STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1107 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202704.PNT | 1PDAS:TE202704.PNT | 10HAH11CT002 | SUPERHEATER 1st STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1108 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202705.PNT | 1PDAS:TE202705.PNT | 10HAH11CT003 | SUPERHEATER 1st STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
340 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193402.PNT | 1ODAS:TE193402.PNT | 10HAH21CT001 | SUPERHEATER 2nd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1109 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202706.PNT | 1PDAS:TE202706.PNT | 10HAH21CT002 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1110 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202707.PNT | 1PDAS:TE202707.PNT | 10HAH21CT003 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1112 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202801.PNT | 1PDAS:TE202801.PNT | 10HAH21CT004 | SUPERHEATER 3rd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1113 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202802.PNT | 1PDAS:TE202802.PNT | 10HAH21CT005 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1114 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202803.PNT | 1PDAS:TE202803.PNT | 10HAH21CT006 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
341 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193403.PNT | 1ODAS:TE193403.PNT | 10HAH22CT001 | SUPERHEATER 2nd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1111 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202708.PNT | 1PDAS:TE202708.PNT | 10HAH22CT002 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
342 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193404.PNT | 1ODAS:TE193404.PNT | 10HAH22CT003 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
343 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193405.PNT | 1ODAS:TE193405.PNT | 10HAH22CT004 | SUPERHEATER 3rd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1115 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202804.PNT | 1PDAS:TE202804.PNT | 10HAH22CT005 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1116 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202805.PNT | 1PDAS:TE202805.PNT | 10HAH22CT006 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
219 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1ODAS:PT193106.PNT | 1ODAS:PT193106.PNT | 10LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa
350 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1ODAS:TE193505.PNT | 1ODAS:TE193505.PNT | 10LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | °C
1021 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1SHTDESUP1:AO202407.OUT | 1SHTDESUP1:AO202407.OUT | 10LAE41AA101XB11 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
917 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201408.PNT | 1PDAS:ZT201408.PNT | 10LAE41AA101XB12 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
916 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201407.PNT | 1PDAS:FT201407.PNT | 10LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1012 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1SHTDESUP2A:AO202305.OUT | 1SHTDESUP2A:AO202305.OUT | 10LAE42AA101XB11 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
906 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201305.PNT | 1PDAS:ZT201305.PNT | 10LAE42AA101XB12 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
903 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201302.PNT | 1PDAS:FT201302.PNT | 10LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1019 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1SHTDESUP2B:AO202405.OUT | 1SHTDESUP2B:AO202405.OUT | 10LAE43AA101XB11 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
914 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201405.PNT | 1PDAS:ZT201405.PNT | 10LAE43AA101XB12 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
911 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201402.PNT | 1PDAS:FT201402.PNT | 10LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1013 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1SHTDESUP3A:AO202306.OUT | 1SHTDESUP3A:AO202306.OUT | 10LAE44AA101XB11 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
907 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201306.PNT | 1PDAS:ZT201306.PNT | 10LAE44AA101XB12 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
904 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201303.PNT | 1PDAS:FT201303.PNT | 10LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1020 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1SHTDESUP3B:AO202406.OUT | 1SHTDESUP3B:AO202406.OUT | 10LAE45AA101XB11 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
915 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201406.PNT | 1PDAS:ZT201406.PNT | 10LAE45AA101XB12 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
912 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201403.PNT | 1PDAS:FT201403.PNT | 10LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
214 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:PT193101.PNT | 1ODAS:PT193101.PNT | 10LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1135 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120101.PNT | 1IDAS:PT120101.PNT | 10LBA10CP202 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1143 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120201.PNT | 1IDAS:PT120201.PNT | 10LBA10CP203 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1151 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120301.PNT | 1IDAS:PT120301.PNT | 10LBA10CP204 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1117 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202806.PNT | 1PDAS:TE202806.PNT | 10LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | °C
1118 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE202807.PNT | 1PDAS:TE202807.PNT | 10LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | °C
1118 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER TUBE #10 |  | OPC.1MSTFLOW:CALCA2.RO01 | 1MSTFLOW:CALCA2.RO01 | 10LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h
1306 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254802.PNT | 1ODAS:TE254802.PNT | 10HAJ10CT001 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1307 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254803.PNT | 1ODAS:TE254803.PNT | 10HAJ10CT002 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1308 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254804.PNT | 1ODAS:TE254804.PNT | 10HAJ10CT003 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1309 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254805.PNT | 1ODAS:TE254805.PNT | 10HAJ10CT004 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1310 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254806.PNT | 1ODAS:TE254806.PNT | 10HAJ10CT005 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1312 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255102.PNT | 1ODAS:TE255102.PNT | 10HAJ10CT006 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1313 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255103.PNT | 1ODAS:TE255103.PNT | 10HAJ10CT007 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1314 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255104.PNT | 1ODAS:TE255104.PNT | 10HAJ10CT008 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1315 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255105.PNT | 1ODAS:TE255105.PNT | 10HAJ10CT009 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1316 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE255106.PNT | 1ODAS:TE255106.PNT | 10HAJ10CT010 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
346 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193501.PNT | 1ODAS:TE193501.PNT | 10HAJ21CT001 | REHEATER DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1124 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203105.PNT | 1PDAS:TE203105.PNT | 10HAJ21CT002 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1125 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203106.PNT | 1PDAS:TE203106.PNT | 10HAJ21CT003 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
347 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193502.PNT | 1ODAS:TE193502.PNT | 10HAJ22CT001 | REHEATER DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1126 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203107.PNT | 1PDAS:TE203107.PNT | 10HAJ22CT002 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1127 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203108.PNT | 1PDAS:TE203108.PNT | 10HAJ22CT003 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1289 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254506.PNT | 1ODAS:TE254506.PNT | 10HAK10CT001 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1290 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254507.PNT | 1ODAS:TE254507.PNT | 10HAK10CT002 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1296 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254606.PNT | 1ODAS:TE254606.PNT | 10HAK10CT003 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1297 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254607.PNT | 1ODAS:TE254607.PNT | 10HAK10CT004 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1303 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254706.PNT | 1ODAS:TE254706.PNT | 10HAK10CT005 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1304 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-16 | OPC.1ODAS:TE254707.PNT | 1ODAS:TE254707.PNT | 10HAK10CT006 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
218 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1ODAS:PT193105.PNT | 1ODAS:PT193105.PNT | 10LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa
349 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1ODAS:TE193504.PNT | 1ODAS:TE193504.PNT | 10LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | °C
1014 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1RHTDESUPEMG:AO202307.OUT | 1RHTDESUPEMG:AO202307.OUT | 10LAF61AA101XB11 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
909 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201308.PNT | 1PDAS:ZT201308.PNT | 10LAF61AA101XB12 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
908 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201307.PNT | 1PDAS:FT201307.PNT | 10LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1011 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1RHTDESUPA:AO202304.OUT | 1RHTDESUPA:AO202304.OUT | 10LAF62AA101XB11 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
905 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201304.PNT | 1PDAS:ZT201304.PNT | 10LAF62AA101XB12 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
902 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201301.PNT | 1PDAS:FT201301.PNT | 10LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1018 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1RHTDESUPB:AO202404.OUT | 1RHTDESUPB:AO202404.OUT | 10LAF63AA101XB11 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
913 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:ZT201404.PNT | 1PDAS:ZT201404.PNT | 10LAF63AA101XB12 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
910 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-08 | OPC.1PDAS:FT201401.PNT | 1PDAS:FT201401.PNT | 10LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
217 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:PT193104.PNT | 1ODAS:PT193104.PNT | 10LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa
348 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193503.PNT | 1ODAS:TE193503.PNT | 10LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | °C
215 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:PT193102.PNT | 1ODAS:PT193102.PNT | 10LBC21CP201 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
344 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193406.PNT | 1ODAS:TE193406.PNT | 10LBC21CT001 | REHEATER EMERGENCY DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1120 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203101.PNT | 1PDAS:TE203101.PNT | 10LBC21CT002 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1121 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203102.PNT | 1PDAS:TE203102.PNT | 10LBC21CT003 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
216 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:PT193103.PNT | 1ODAS:PT193103.PNT | 10LBC22CP201 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
345 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1ODAS:TE193407.PNT | 1ODAS:TE193407.PNT | 10LBC22CT001 | REHEATER EMERGENCY DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1122 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203103.PNT | 1PDAS:TE203103.PNT | 10LBC22CT002 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1123 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEAT TUBE #10 | 50-F290S-J0201-04 | OPC.1PDAS:TE203104.PNT | 1PDAS:TE203104.PNT | 10LBC22CT003 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
239 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOTBLOWER #10 |  | OPC.1NDAS:AO183603.OUT | 1NDAS:AO183603.OUT | 10HCB00AA101XB11 | SOOT BLOWING STEAM SOURCE CONTROL SIGNAL | AO
204 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOTBLOWER #10 |  | OPC.1NDAS:ZT183405.PNT | 1NDAS:ZT183405.PNT | 10HCB00AA101XB12 | SOOT BLOWING STEAM SOURCE POSITION FEEDBACK OF REGULATING VALVE | AI | 0 | 100 | %
205 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOTBLOWER #10 |  | OPC.1NDAS:PT183406.PNT | 1NDAS:PT183406.PNT | 10HCB00CP201 | SOOT BLOWING STEAM SOURCE PRESSURE | AI | 0 | 10
920 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201503.PNT | 1PDAS:PT201503.PNT | 10H10CP201 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
927 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201603.PNT | 1PDAS:PT201603.PNT | 10H10CP202 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
165 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:PT163305.PNT | 1MDAS:PT163305.PNT | 10H10CP203 | A SIDE FURNACE PRESSURE | AI | -2 | 2 | KPa
166 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:PT163306.PNT | 1MDAS:PT163306.PNT | 10H10CP204 | A SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa
318 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162607.PNT | 1MDAS:TE162607.PNT | 10H10CT002 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
319 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162701.PNT | 1MDAS:TE162701.PNT | 10H10CT003 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
320 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162702.PNT | 1MDAS:TE162702.PNT | 10H10CT004 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
321 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162703.PNT | 1MDAS:TE162703.PNT | 10H10CT005 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
322 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162704.PNT | 1MDAS:TE162704.PNT | 10H10CT006 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
323 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162705.PNT | 1MDAS:TE162705.PNT | 10H10CT007 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
324 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1MDAS:TE162706.PNT | 1MDAS:TE162706.PNT | 10H10CT008 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
919 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201502.PNT | 1PDAS:PT201502.PNT | 10H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
926 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201602.PNT | 1PDAS:PT201602.PNT | 10H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
1499 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F289S-K0503-02 | OPC.1QDAS:AI212501.PNT | 1QDAS:AI212501.PNT | 10H10GC001AI01 | SIDE A FURNACE FLUE GAS TEMPERATURE PROBE TEMPERATURE | AI | 0 | 580 | °C
1500 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F289S-K0503-02 | OPC.1QDAS:ZT212502.PNT | 1QDAS:ZT212502.PNT | 10H10GC001AI02 | SIDE A FURNACE FLUE GAS TEMPERATURE PROBE POSITION | AI | 0 | 100 | %
922 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201505.PNT | 1PDAS:PT201505.PNT | 10H20CP201 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
929 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201605.PNT | 1PDAS:PT201605.PNT | 10H20CP202 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
197 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:PT183305.PNT | 1NDAS:PT183305.PNT | 10H20CP203 | B SIDE FURNACE PRESSURE | AI | -2 | 2 | KPa
198 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:PT183306.PNT | 1NDAS:PT183306.PNT | 10H20CP204 | B SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa
331 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182607.PNT | 1NDAS:TE182607.PNT | 10H20CT002 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
332 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182701.PNT | 1NDAS:TE182701.PNT | 10H20CT003 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
333 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182702.PNT | 1NDAS:TE182702.PNT | 10H20CT004 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
334 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182703.PNT | 1NDAS:TE182703.PNT | 10H20CT005 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
335 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182704.PNT | 1NDAS:TE182704.PNT | 10H20CT006 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
336 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182705.PNT | 1NDAS:TE182705.PNT | 10H20CT007 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
337 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182706.PNT | 1NDAS:TE182706.PNT | 10H20CT008 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
338 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1NDAS:TE182707.PNT | 1NDAS:TE182707.PNT | 10H20CT009 | B SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | °C
921 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201504.PNT | 1PDAS:PT201504.PNT | 10H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
928 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-34 | OPC.1PDAS:PT201604.PNT | 1PDAS:PT201604.PNT | 10H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
1501 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F289S-K0503-03 | OPC.1QDAS:AI212503.PNT | 1QDAS:AI212503.PNT | 10H20GC001AI01 | SIDE B FURNACE FLUE GAS TEMPERATURE PROBE TEMPERATURE | AI | 0 | 580 | °C
1502 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F289S-K0503-03 | OPC.1QDAS:ZT212504.PNT | 1QDAS:ZT212504.PNT | 10H20GC001AI02 | SIDE B FURNACE FLUE GAS TEMPERATURE PROBE POSITION | AI | 0 | 100 | %
889 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-02 | OPC.1PDAS:FT201101.PNT | 1PDAS:FT201101.PNT | 10HLA10CF201 | GAH A OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
890 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-02 | OPC.1PDAS:FT201102.PNT | 1PDAS:FT201102.PNT | 10HLA10CF202 | GAH A OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
896 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-02 | OPC.1PDAS:FT201201.PNT | 1PDAS:FT201201.PNT | 10HLA20CF201 | GAH B OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
897 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F290S-J0201-02 | OPC.1PDAS:FT201202.PNT | 1PDAS:FT201202.PNT | 10HLA20CF202 | GAH B OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
1870 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.1FURPRESS:AINFURPRE.PNT | 1FURPRESS:AINFURPRE.PNT | 10H10CP201C1 | FURNACE PRESSURE | AI | -2500 | 2500 | Pa
1874 | 2 | UJRBG #10 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.1FUELMASTER:AINCOAL.PNT | 1FUELMASTER:AINCOAL.PNT | 10HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
996 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-02 | OPC.1PAFLOW:AO202105.OUT | 1PAFLOW:AO202105.OUT | 10HFE10AA101XB11 | PAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
892 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT201105.PNT | 1PDAS:ZT201105.PNT | 10HFE10AA101XB12 | PAF A INLET VANE POSITION | AI | 0 | 100 | %
159 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-02 | OPC.1MDAS:CT163206.PNT | 1MDAS:CT163206.PNT | 10HFE10AN001XB13 | PAF A CURRENT | AI | 0 | 250 | A
150 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163104.PNT | 1MDAS:PT163104.PNT | 10HFE10CP201 | PAF A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
313 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-02 | OPC.1MDAS:TE162602.PNT | 1MDAS:TE162602.PNT | 10HFE10CT001 | PAF A INLET AIR TEMPERATURE | TC | 0 | 100 | °C
255 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162301.PNT | 1MDAS:RT162301.PNT | 10HFE10CT006 | PAF A MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | °C
256 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162302.PNT | 1MDAS:RT162302.PNT | 10HFE10CT007 | PAF A MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | °C
257 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162303.PNT | 1MDAS:RT162303.PNT | 10HFE10CT008 | PAF A MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | °C
258 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162304.PNT | 1MDAS:RT162304.PNT | 10HFE10CT009 | PAF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C
259 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162305.PNT | 1MDAS:RT162305.PNT | 10HFE10CT010 | PAF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162306.PNT | 1MDAS:RT162306.PNT | 10HFE10CT011 | PAF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1MDAS:RT162307.PNT | 1MDAS:RT162307.PNT | 10HFE10CT012 | PAF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1VMS:AIN1.PNT | 1VMS:AIN1.PNT | 10HFE10CY001X | #10 PAF A BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1VMS:AIN2.PNT | 1VMS:AIN2.PNT | 10HFE10CY001Y | #10 PAF A BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1VMS:AIN3.PNT | 1VMS:AIN3.PNT | 10HFE10CY002X | #10 PAF A BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #10A | 50-F290S-J0201-37 | OPC.1VMS:AIN4.PNT | 1VMS:AIN4.PNT | 10HFE10CY002Y | #10 PAF A BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
147 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163101.PNT | 1MDAS:PT163101.PNT | 10HLA10CP201 | FDF A OUTLET AIR PRESSURE | AI | 0 | 5 | KPa
312 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:TE162601.PNT | 1MDAS:TE162601.PNT | 10HLA10CT001 | FDF A INLET AIR TEMPERATURE | TC | 0 | 100 | °C
995 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-02 | OPC.1AIRFLOW:AO202104.OUT | 1AIRFLOW:AO202104.OUT | 10HLB10AA101XB11 | FDF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
891 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT201104.PNT | 1PDAS:ZT201104.PNT | 10HLB10AA101XB12 | FDF A INLET VANE POSITION | AI | 0 | 100 | %
158 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:CT163205.PNT | 1MDAS:CT163205.PNT | 10HLB10AN001XB13 | FDF A CURRENT | AI | 0 | 75 | A
241 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162101.PNT | 1MDAS:RT162101.PNT | 10HLB10CT001 | FDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
248 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162201.PNT | 1MDAS:RT162201.PNT | 10HLB10CT002 | FDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
242 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162102.PNT | 1MDAS:RT162102.PNT | 10HLB10CT003 | FDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
249 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162202.PNT | 1MDAS:RT162202.PNT | 10HLB10CT004 | FDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
243 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162103.PNT | 1MDAS:RT162103.PNT | 10HLB10CT005 | FDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
250 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162203.PNT | 1MDAS:RT162203.PNT | 10HLB10CT006 | FDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
244 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162104.PNT | 1MDAS:RT162104.PNT | 10HLB10CT007 | FDF A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C
251 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162204.PNT | 1MDAS:RT162204.PNT | 10HLB10CT008 | FDF A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C
245 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162105.PNT | 1MDAS:RT162105.PNT | 10HLB10CT009 | FDF A BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
252 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162205.PNT | 1MDAS:RT162205.PNT | 10HLB10CT010 | FDF A BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
246 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162106.PNT | 1MDAS:RT162106.PNT | 10HLB10CT011 | FDF A BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
253 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162206.PNT | 1MDAS:RT162206.PNT | 10HLB10CT012 | FDF A BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
247 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162107.PNT | 1MDAS:RT162107.PNT | 10HLB10CT013 | FDF A BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
254 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1MDAS:RT162207.PNT | 1MDAS:RT162207.PNT | 10HLB10CT014 | FDF A BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1VMS:AIN9.PNT | 1VMS:AIN9.PNT | 10HLB10CY001X | #10 FDF A BR VIBE H (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1VMS:AIN10.PNT | 1VMS:AIN10.PNT | 10HLB10CY001Y | #10 FDF A BR VIBE H (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1VMS:AIN11.PNT | 1VMS:AIN11.PNT | 10HLB10CY002X | #10 FDF A BR VIBE H (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #10A | 50-F290S-J0201-36 | OPC.1VMS:AIN12.PNT | 1VMS:AIN12.PNT | 10HLB10CY002Y | #10 FDF A BR VIBE H (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
999 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A |  | OPC.1APHCUR:AO202108.OUT | 1APHCUR:AO202108.OUT | 10CFF01DCSAO01 | AIR PRE-HEATER A MAIN AND AUXILIARY MOTOR CURRENT SELECTION LARGE OUTPUT | AO | 0 | 100 | %
151 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163105.PNT | 1MDAS:PT163105.PNT | 10HFE10CP202 | GAH A INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
152 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163106.PNT | 1MDAS:PT163106.PNT | 10HFE10CP203 | GAH A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
1132 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1QDAS:TE212201.PNT | 1QDAS:TE212201.PNT | 10HFE10CT002 | GAH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | °C
1133 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1QDAS:TE212204.PNT | 1QDAS:TE212204.PNT | 10HFE10CT005 | GAH A OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | °C
148 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163102.PNT | 1MDAS:PT163102.PNT | 10HLA10CP202 | GAH A INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
149 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163103.PNT | 1MDAS:PT163103.PNT | 10HLA10CP203 | GAH A OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
1128 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1QDAS:TE212101.PNT | 1QDAS:TE212101.PNT | 10HLA10CT002 | GAH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | °C
1129 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1QDAS:TE212104.PNT | 1QDAS:TE212104.PNT | 10HLA10CT005 | GAH A OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | °C
161 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:CT163301.PNT | 1MDAS:CT163301.PNT | 10HLD11GC001AI01 | AIR PRE-HEATER A MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
162 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:CT163302.PNT | 1MDAS:CT163302.PNT | 10HLD11GC001AI02 | AIR PRE-HEATER A AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
163 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:AI163303.PNT | 1MDAS:AI163303.PNT | 10HLD11GC001AI03 | AIR PRE-HEATER A MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 100 | %
164 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:AI163304.PNT | 1MDAS:AI163304.PNT | 10HLD11GC001AI04 | AIR PRE-HEATER A AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 100 | %
235 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:AO163601.OUT | 1MDAS:AO163601.OUT | 10HLD11GC001AO01 | AIR PRE-HEATER A MAIN MOTOR ROTATIONAL SPEED PRESET | AO
236 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:AO163602.OUT | 1MDAS:AO163602.OUT | 10HLD11GC001AO02 | AIR PRE-HEATER A AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO
155 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163202.PNT | 1MDAS:PT163202.PNT | 10HNA10CP202 | GAH A OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa
1105 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10A | 50-F290S-J0201-02 | OPC.1PDAS:TE202606.PNT | 1PDAS:TE202606.PNT | 10HNA10CT002 | GAH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | °C
867 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F290S-J0201-02 | OPC.1PDAS:PT200601.PNT | 1PDAS:PT200601.PNT | 10HFE50CP201 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
873 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F290S-J0201-02 | OPC.1PDAS:PT200701.PNT | 1PDAS:PT200701.PNT | 10HFE50CP202 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
881 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F290S-J0201-02 | OPC.1PDAS:PT200801.PNT | 1PDAS:PT200801.PNT | 10HFE50CP203 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
191 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-02 | OPC.1NDAS:CT183206.PNT | 1NDAS:CT183206.PNT | 10HFE20AN001XB13 | PAF B CURRENT | AI | 0 | 250 | A
183 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183104.PNT | 1NDAS:PT183104.PNT | 10HFE20CP201 | PAF B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
327 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-02 | OPC.1NDAS:TE182602.PNT | 1NDAS:TE182602.PNT | 10HFE20CT001 | PAF B INLET AIR TEMPERATURE | TC | 0 | 100 | °C
291 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182301.PNT | 1NDAS:RT182301.PNT | 10HFE20CT006 | PAF B MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | °C
292 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182302.PNT | 1NDAS:RT182302.PNT | 10HFE20CT007 | PAF B MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | °C
293 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182303.PNT | 1NDAS:RT182303.PNT | 10HFE20CT008 | PAF B MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | °C
294 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182304.PNT | 1NDAS:RT182304.PNT | 10HFE20CT009 | PAF B MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C
295 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182305.PNT | 1NDAS:RT182305.PNT | 10HFE20CT010 | PAF B MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C
296 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182306.PNT | 1NDAS:RT182306.PNT | 10HFE20CT011 | PAF B BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
297 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1NDAS:RT182307.PNT | 1NDAS:RT182307.PNT | 10HFE20CT012 | PAF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 80 | 85
1004 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-02 | OPC.1PAFLOW:AO202205.OUT | 1PAFLOW:AO202205.OUT | 10HFE20HB001XB11 | PAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
899 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT201205.PNT | 1PDAS:ZT201205.PNT | 10HFE20HB001XB12 | PAF B INLET VANE POSITION | AI | 0 | 100 | %
899 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1VMS:AIN5.PNT | 1VMS:AIN5.PNT | 10HFE20CY001X | #10 PAF B BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1VMS:AIN6.PNT | 1VMS:AIN6.PNT | 10HFE20CY001Y | #10 PAF B BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1VMS:AIN7.PNT | 1VMS:AIN7.PNT | 10HFE20CY002X | #10 PAF B BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #10B | 50-F290S-J0201-37 | OPC.1VMS:AIN8.PNT | 1VMS:AIN8.PNT | 10HFE20CY002Y | #10 PAF B BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
180 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183101.PNT | 1NDAS:PT183101.PNT | 10HLA20CP201 | FDF B OUTLET AIR PRESSURE | AI | 0 | 5 | KPa
326 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:TE182601.PNT | 1NDAS:TE182601.PNT | 10HLA20CT001 | FDF B INLET AIR TEMPERATURE | TC | 0 | 100 | °C
1003 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-02 | OPC.1AIRFLOW:AO202204.OUT | 1AIRFLOW:AO202204.OUT | 10HLB20AA101XB11 | FDF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
898 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT201204.PNT | 1PDAS:ZT201204.PNT | 10HLB20AA101XB12 | FDF B INLET VANE POSITION | AI | 0 | 100 | %
190 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:CT183205.PNT | 1NDAS:CT183205.PNT | 10HLB20AN001XB13 | FDF B CURRENT | AI | 0 | 75 | A
276 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182101.PNT | 1NDAS:RT182101.PNT | 10HLB20CT001 | FDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
284 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182201.PNT | 1NDAS:RT182201.PNT | 10HLB20CT002 | FDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
277 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182102.PNT | 1NDAS:RT182102.PNT | 10HLB20CT003 | FDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
285 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182202.PNT | 1NDAS:RT182202.PNT | 10HLB20CT004 | FDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
278 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182103.PNT | 1NDAS:RT182103.PNT | 10HLB20CT005 | FDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
286 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182203.PNT | 1NDAS:RT182203.PNT | 10HLB20CT006 | FDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
279 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182104.PNT | 1NDAS:RT182104.PNT | 10HLB20CT007 | FDF B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C
287 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182204.PNT | 1NDAS:RT182204.PNT | 10HLB20CT008 | FDF B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C
280 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182105.PNT | 1NDAS:RT182105.PNT | 10HLB20CT009 | FDF B BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
288 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182205.PNT | 1NDAS:RT182205.PNT | 10HLB20CT010 | FDF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
281 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182106.PNT | 1NDAS:RT182106.PNT | 10HLB20CT011 | FDF B BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
289 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182206.PNT | 1NDAS:RT182206.PNT | 10HLB20CT012 | FDF B BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
282 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182107.PNT | 1NDAS:RT182107.PNT | 10HLB20CT013 | FDF B BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
290 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1NDAS:RT182207.PNT | 1NDAS:RT182207.PNT | 10HLB20CT014 | FDF B BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1VMS:AIN13.PNT | 1VMS:AIN13.PNT | 10HLB20CY001X | #10 FDF B BR VIBE H (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1VMS:AIN14.PNT | 1VMS:AIN14.PNT | 10HLB20CY001Y | #10 FDF B BR VIBE H (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1VMS:AIN15.PNT | 1VMS:AIN15.PNT | 10HLB20CY002X | #10 FDF B BR VIBE H (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #10B | 50-F290S-J0201-36 | OPC.1VMS:AIN16.PNT | 1VMS:AIN16.PNT | 10HLB20CY002Y | #10 FDF B BR VIBE H (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
1007 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B |  | OPC.1APHCUR:AO202208.OUT | 1APHCUR:AO202208.OUT | 10CFF01DCSAO02 | AIR PRE-HEATER B MAIN AND AUXILIARY MOTOR CURRENT SELECTION LARGE OUTPUT | AO | 0 | 100 | %
184 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183105.PNT | 1NDAS:PT183105.PNT | 10HFE20CP202 | GAH B INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
185 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183106.PNT | 1NDAS:PT183106.PNT | 10HFE20CP203 | GAH B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
1134 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1QDAS:TE212205.PNT | 1QDAS:TE212205.PNT | 10HFE20CT002 | GAH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | °C
1089 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1QDAS:TE212208.PNT | 1QDAS:TE212208.PNT | 10HFE20CT005 | GAH B OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
181 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183102.PNT | 1NDAS:PT183102.PNT | 10HLA20CP202 | GAH B INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
182 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183103.PNT | 1NDAS:PT183103.PNT | 10HLA20CP203 | GAH B OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
1130 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1QDAS:TE212105.PNT | 1QDAS:TE212105.PNT | 10HLA20CT002 | GAH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | °C
1131 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1QDAS:TE212108.PNT | 1QDAS:TE212108.PNT | 10HLA20CT005 | GAH B OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | °C
193 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:CT183301.PNT | 1NDAS:CT183301.PNT | 10HLD12GC001AI01 | AIR PRE-HEATER B MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
194 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:CT183302.PNT | 1NDAS:CT183302.PNT | 10HLD12GC001AI02 | AIR PRE-HEATER B AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
195 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:AI183303.PNT | 1NDAS:AI183303.PNT | 10HLD12GC001AI03 | AIR PRE-HEATER B MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1
196 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:AI183304.PNT | 1NDAS:AI183304.PNT | 10HLD12GC001AI04 | AIR PRE-HEATER B AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1
237 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:AO183601.OUT | 1NDAS:AO183601.OUT | 10HLD12GC001AO01 | AIR PRE-HEATER B MAIN MOTOR ROTATIONAL SPEED PRESET | AO
238 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:AO183602.OUT | 1NDAS:AO183602.OUT | 10HLD12GC001AO02 | AIR PRE-HEATER B AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO
187 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183202.PNT | 1NDAS:PT183202.PNT | 10HNA20CP202 | GAH B OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa
1106 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #10B | 50-F290S-J0201-02 | OPC.1PDAS:TE202701.PNT | 1PDAS:TE202701.PNT | 10HNA20CT002 | GAH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
156 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163203.PNT | 1MDAS:PT163203.PNT | 10HNA11CP201 | ESP A OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa
315 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:TE162604.PNT | 1MDAS:TE162604.PNT | 10HNA11CT001 | ESP A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
157 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:PT163204.PNT | 1MDAS:PT163204.PNT | 10HNA12CP201 | IDF A OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa
316 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:TE162605.PNT | 1MDAS:TE162605.PNT | 10HNA12CT001 | IDF A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
998 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1FURPRESS:AO202107.OUT | 1FURPRESS:AO202107.OUT | 10HNC11AA101XB11 | IDF A INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | %
894 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1PDAS:ZT201107.PNT | 1PDAS:ZT201107.PNT | 10HNC11AA101XB12 | IDF A INLET STATIONARY BLADE POSITION | AI | 0 | 100 | %
160 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-02 | OPC.1MDAS:CT163207.PNT | 1MDAS:CT163207.PNT | 10HNC11AN001XB13 | IDF A CURRENT | AI | 0 | 300 | A
168 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:CT163401.PNT | 1MDAS:CT163401.PNT | 10HNC11AN002XB13 | IDF A #1 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
169 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:CT163402.PNT | 1MDAS:CT163402.PNT | 10HNC11AN003XB13 | IDF A #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
262 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162401.PNT | 1MDAS:RT162401.PNT | 10HNC11CT001 | IDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
269 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162501.PNT | 1MDAS:RT162501.PNT | 10HNC11CT002 | IDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
263 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162402.PNT | 1MDAS:RT162402.PNT | 10HNC11CT003 | IDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
270 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162502.PNT | 1MDAS:RT162502.PNT | 10HNC11CT004 | IDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
264 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162403.PNT | 1MDAS:RT162403.PNT | 10HNC11CT005 | IDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
271 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162503.PNT | 1MDAS:RT162503.PNT | 10HNC11CT006 | IDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
265 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162404.PNT | 1MDAS:RT162404.PNT | 10HNC11CT007 | IDF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C
272 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162504.PNT | 1MDAS:RT162504.PNT | 10HNC11CT008 | IDF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C
266 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162405.PNT | 1MDAS:RT162405.PNT | 10HNC11CT009 | IDF A BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
273 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162505.PNT | 1MDAS:RT162505.PNT | 10HNC11CT010 | IDF A BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
267 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162406.PNT | 1MDAS:RT162406.PNT | 10HNC11CT011 | IDF A BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
274 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162506.PNT | 1MDAS:RT162506.PNT | 10HNC11CT012 | IDF A BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
268 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162407.PNT | 1MDAS:RT162407.PNT | 10HNC11CT013 | IDF A BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
275 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1MDAS:RT162507.PNT | 1MDAS:RT162507.PNT | 10HNC11CT014 | IDF A BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1VMS:AIN17.PNT | 1VMS:AIN17.PNT | 10HNC11CY001X | #10 IDF A BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1VMS:AIN18.PNT | 1VMS:AIN18.PNT | 10HNC11CY001Y | #10 IDF A BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1VMS:AIN19.PNT | 1VMS:AIN19.PNT | 10HNC11CY002X | #10 IDF A BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #10A | 50-F290S-J0201-38 | OPC.1VMS:AIN20.PNT | 1VMS:AIN20.PNT | 10HNC11CY002Y | #10 IDF A BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
188 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183203.PNT | 1NDAS:PT183203.PNT | 10HNA21CP201 | ESP B OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa
329 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:TE182604.PNT | 1NDAS:TE182604.PNT | 10HNA21CT001 | ESP B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
189 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:PT183204.PNT | 1NDAS:PT183204.PNT | 10HNA22CP201 | IDF B OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa
330 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:TE182605.PNT | 1NDAS:TE182605.PNT | 10HNA22CT001 | IDF B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
1006 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1FURPRESS:AO202207.OUT | 1FURPRESS:AO202207.OUT | 10HNC21AA101XB11 | IDF B INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | %
901 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1PDAS:ZT201207.PNT | 1PDAS:ZT201207.PNT | 10HNC21AA101XB12 | IDF B INLET STATIONARY BLADE POSITION | AI | 0 | 100 | %
192 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-02 | OPC.1NDAS:CT183207.PNT | 1NDAS:CT183207.PNT | 10HNC21AN001XB13 | IDF B CURRENT | AI | 0 | 300 | A
200 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:CT183401.PNT | 1NDAS:CT183401.PNT | 10HNC21AN002XB13 | IDF B #1 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
201 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:CT183402.PNT | 1NDAS:CT183402.PNT | 10HNC21AN003XB13 | IDF B #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
298 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182401.PNT | 1NDAS:RT182401.PNT | 10HNC21CT001 | IDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
305 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182501.PNT | 1NDAS:RT182501.PNT | 10HNC21CT002 | IDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
299 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182402.PNT | 1NDAS:RT182402.PNT | 10HNC21CT003 | IDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
306 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182502.PNT | 1NDAS:RT182502.PNT | 10HNC21CT004 | IDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
300 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182403.PNT | 1NDAS:RT182403.PNT | 10HNC21CT005 | IDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
307 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182503.PNT | 1NDAS:RT182503.PNT | 10HNC21CT006 | IDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
301 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182404.PNT | 1NDAS:RT182404.PNT | 10HNC21CT007 | IDF B MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C
308 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182504.PNT | 1NDAS:RT182504.PNT | 10HNC21CT008 | IDF B MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C
302 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182405.PNT | 1NDAS:RT182405.PNT | 10HNC21CT009 | IDF B BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
309 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182505.PNT | 1NDAS:RT182505.PNT | 10HNC21CT010 | IDF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
303 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182406.PNT | 1NDAS:RT182406.PNT | 10HNC21CT011 | IDF B BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
310 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182506.PNT | 1NDAS:RT182506.PNT | 10HNC21CT012 | IDF B BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
304 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182407.PNT | 1NDAS:RT182407.PNT | 10HNC21CT013 | IDF B BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C
311 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1NDAS:RT182507.PNT | 1NDAS:RT182507.PNT | 10HNC21CT014 | IDF B BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1VMS:AIN21.PNT | 1VMS:AIN21.PNT | 10HNC21CY001X | #10 IDF B BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1VMS:AIN22.PNT | 1VMS:AIN22.PNT | 10HNC21CY001Y | #10 IDF B BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1VMS:AIN23.PNT | 1VMS:AIN23.PNT | 10HNC21CY002X | #10 IDF B BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 2 | UJRBG #10 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #10B | 50-F290S-J0201-38 | OPC.1VMS:AIN24.PNT | 1VMS:AIN24.PNT | 10HNC21CY002Y | #10 IDF B BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
417 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50-F290S-J0201-19 | OPC.1FDAS:PT073203.PNT | 1FDAS:PT073203.PNT | 10MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa
451 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50-F290S-J0201-25 | OPC.1FDAS:LT073608.PNT | 1FDAS:LT073608.PNT | 10MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 900 | mm |  |  | 340 | 810
443 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50-F290S-J0201-25 | OPC.1FDAS:PT073508.PNT | 1FDAS:PT073508.PNT | 10MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 0.4 | MPa
747 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50-F290S-J0201-25 | OPC.1FDAS:TE070802.PNT | 1FDAS:TE070802.PNT | 10MKW10CT003 | GENERATOR EXCITER SIDE H2 SIDE SEAL RETURN OIL TEMP | TC | 0 | 100 | °C
377 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50- | OPC.1EDAS:CT050803.PNT | 1EDAS:CT050803.PNT | 10MKW20AP101XB13 | GENERATOR H2 SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 100 | %
673 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL-H2 SIDE #10A | 50-F290S-J0201-25 | OPC.1FDAS:RT073805.PNT | 1FDAS:RT073805.PNT | 10MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | °C
1243 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #10A | F296S-J0201-25 | OPC.1FDAS:TE070801.PNT | 1FDAS:TE070801.PNT | 10MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C
378 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #10B | 50- | OPC.1EDAS:CT050804.PNT | 1EDAS:CT050804.PNT | 10MKW20AP102XB13 | GENERATOR H3 SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 100 | %
499 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 5 | GENERATOR SEAL OIL #10 - AIR SIDE DC EMERGENCY PUMP | 50- | OPC.1GDAS:CT092707.PNT | 1GDAS:CT092707.PNT | 10MKW10AP103XB13 | GENERATOR AIR SIDE DC EMERGENCY SEAL OIL PUMP CURRENT | AI | 0 | 105 | %
1260 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1GESTAT:AO122605.OUT | 1GESTAT:AO122605.OUT | 10MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1219 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1IDAS:ZT121404.PNT | 1IDAS:ZT121404.PNT | 10MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | %
424 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:CT073303.PNT | 1FDAS:CT073303.PNT | 10MKF10AP001XB13 | GENERATOR STATOR COOLING WATER PUMP A CURRENT | AI | 0 | 100 | %
433 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:FT073405.PNT | 1FDAS:FT073405.PNT | 10MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 45 | t/h
434 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:AI073406.PNT | 1FDAS:AI073406.PNT | 10MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2
435 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:AI073407.PNT | 1FDAS:AI073407.PNT | 10MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5
1263 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1IDAS:RT121602.PNT | 1IDAS:RT121602.PNT | 10MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | °C |  |  | 42 | 48
427 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:PT073306.PNT | 1FDAS:PT073306.PNT | 10MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.6 | MPa
428 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:PT073307.PNT | 1FDAS:PT073307.PNT | 10MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.6 | MPa
669 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-24 | OPC.1FDAS:RT073801.PNT | 1FDAS:RT073801.PNT | 10MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | °C |  |  |  | 80
660 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #10A | 50-F290S-J0201-14 | OPC.1EDAS:RT067805.PNT | 1EDAS:RT067805.PNT | 10PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | °C
431 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #10B | 50-F290S-J0201-24 | OPC.1FDAS:CT073403.PNT | 1FDAS:CT073403.PNT | 10MKF10AP002XB13 | GENERATOR STATOR COOLING WATER PUMP B CURRENT | AI | 0 | 100 | %
1267 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_6 | 1ATC:1BD117AIN.PNT_6 | 10MKA00CT0143 | GENERATOR TURBINE SIDE BABBIT TEMP | RTD | 0 | 120 | C
1268 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_5 | 1ATC:1BD115AIN.PNT_5 | 10MKA00CT0144 | GENERATOR TURBINE SIDE BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1269 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_7 | 1ATC:1BD104AIN.PNT_7 | 10TSIDEH16 | SHAFT NO.5 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1270 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_8 | 1ATC:1BD104AIN.PNT_8 | 10TSIDEH17 | SHAFT NO.5 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1271 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_7 | 1ATC:1BD105AIN.PNT_7 | 10TSIDEH24 | BEARING COVER NO.5 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1272 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_7 | 1ATC:1BD117AIN.PNT_7 | 10MKA00CT0146 | GENERATOR COLECTOR SIDE BABBIT TEMP | RTD | 0 | 120 | C
1273 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_6 | 1ATC:1BD115AIN.PNT_6 | 10MKA00CT0147 | GENERATOR COLECTOR SIDE BEARING RETURN OIL TEMP | RTD | 0 | 120 | C
1274 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_1 | 1ATC:1BD105AIN.PNT_1 | 10TSIDEH18 | SHAFT NO.6 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1275 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_2 | 1ATC:1BD105AIN.PNT_2 | 10TSIDEH19 | SHAFT NO.6 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1276 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_8 | 1ATC:1BD105AIN.PNT_8 | 10TSIDEH25 | BEARING COVER NO.6 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1261 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F289S-K0606-01 | OPC.1CCSDMD:AO122606.OUT | 1CCSDMD:AO122606.OUT | 10DCSDEH01 | CCS DEMAND 1 | AO | 0 | 100 | %
1255 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F289S-K0606-01 | OPC.1CCSDMD:AO122507.OUT | 1CCSDMD:AO122507.OUT | 10DCSDEH02 | CCS DEMAND 2 | AO | 0 | 100 | %
1221 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F289S-K0606-01 | OPC.1IDAS:AI121406.PNT | 1IDAS:AI121406.PNT | 10DEHDCS02 | GENERATOR LOAD | AI | 0 | 400 | MW |  | 0 | 0 | 350 | 400
1348 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245101.PNT | 1HDAS:TE245101.PNT | 10MKA00CT001 | GENERATOR STATOR COIL OUTLET WATER TEMP 1 | RTD | 0 | 500 | °C
1349 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245102.PNT | 1HDAS:TE245102.PNT | 10MKA00CT002 | GENERATOR STATOR COIL OUTLET WATER TEMP 2 | RTD | 0 | 500 | °C
1350 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245103.PNT | 1HDAS:TE245103.PNT | 10MKA00CT003 | GENERATOR STATOR COIL OUTLET WATER TEMP 3 | RTD | 0 | 500 | °C
1351 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245104.PNT | 1HDAS:TE245104.PNT | 10MKA00CT004 | GENERATOR STATOR COIL OUTLET WATER TEMP 4 | RTD | 0 | 500 | °C
1352 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245105.PNT | 1HDAS:TE245105.PNT | 10MKA00CT005 | GENERATOR STATOR COIL OUTLET WATER TEMP 5 | RTD | 0 | 500 | °C
1353 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245106.PNT | 1HDAS:TE245106.PNT | 10MKA00CT006 | GENERATOR STATOR COIL OUTLET WATER TEMP 6 | RTD | 0 | 500 | °C
1354 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245107.PNT | 1HDAS:TE245107.PNT | 10MKA00CT007 | GENERATOR STATOR COIL OUTLET WATER TEMP 7 | RTD | 0 | 500 | °C
1355 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245108.PNT | 1HDAS:TE245108.PNT | 10MKA00CT008 | GENERATOR STATOR COIL OUTLET WATER TEMP 8 | RTD | 0 | 500 | °C
1356 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245201.PNT | 1HDAS:TE245201.PNT | 10MKA00CT009 | GENERATOR STATOR COIL OUTLET WATER TEMP 9 | RTD | 0 | 500 | °C
1357 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245202.PNT | 1HDAS:TE245202.PNT | 10MKA00CT010 | GENERATOR STATOR COIL OUTLET WATER TEMP 10 | RTD | 0 | 500 | °C
1447 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246606.PNT | 1HDAS:TE246606.PNT | 10MKA00CT0100 | GENERATOR STATOR BARS TEMP 46 | RTD | 0 | 500 | °C
1448 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246607.PNT | 1HDAS:TE246607.PNT | 10MKA00CT0101 | GENERATOR STATOR BARS TEMP 47 | RTD | 0 | 500 | °C
1449 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246608.PNT | 1HDAS:TE246608.PNT | 10MKA00CT0102 | GENERATOR STATOR BARS TEMP 48 | RTD | 0 | 500 | °C
1450 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246701.PNT | 1HDAS:TE246701.PNT | 10MKA00CT0103 | GENERATOR STATOR BARS TEMP 49 | RTD | 0 | 500 | °C
1451 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246702.PNT | 1HDAS:TE246702.PNT | 10MKA00CT0104 | GENERATOR STATOR BARS TEMP 50 | RTD | 0 | 500 | °C
1452 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246703.PNT | 1HDAS:TE246703.PNT | 10MKA00CT0105 | GENERATOR STATOR BARS TEMP 51 | RTD | 0 | 500 | °C
1453 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246704.PNT | 1HDAS:TE246704.PNT | 10MKA00CT0106 | GENERATOR STATOR BARS TEMP 52 | RTD | 0 | 500 | °C
1454 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246705.PNT | 1HDAS:TE246705.PNT | 10MKA00CT0107 | GENERATOR STATOR BARS TEMP 53 | RTD | 0 | 500 | °C
1455 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246706.PNT | 1HDAS:TE246706.PNT | 10MKA00CT0108 | GENERATOR STATOR BARS TEMP 54 | RTD | 0 | 500 | °C
1456 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247101.PNT | 1HDAS:TE247101.PNT | 10MKA00CT0109 | GENERATOR STATOR CORE TEMP 1 | RTD | 0 | 500 | °C
1358 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245203.PNT | 1HDAS:TE245203.PNT | 10MKA00CT011 | GENERATOR STATOR COIL OUTLET WATER TEMP 11 | RTD | 0 | 500 | °C
1457 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247102.PNT | 1HDAS:TE247102.PNT | 10MKA00CT0110 | GENERATOR STATOR CORE TEMP 2 | RTD | 0 | 500 | °C
1458 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247103.PNT | 1HDAS:TE247103.PNT | 10MKA00CT0111 | GENERATOR STATOR CORE TEMP 3 | RTD | 0 | 500 | °C
1459 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247104.PNT | 1HDAS:TE247104.PNT | 10MKA00CT0112 | GENERATOR STATOR CORE TEMP 4 | RTD | 0 | 500 | °C
1460 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247105.PNT | 1HDAS:TE247105.PNT | 10MKA00CT0113 | GENERATOR STATOR CORE TEMP 5 | RTD | 0 | 500 | °C
1461 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247106.PNT | 1HDAS:TE247106.PNT | 10MKA00CT0114 | GENERATOR STATOR CORE TEMP 6 | RTD | 0 | 500 | °C
1464 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247201.PNT | 1HDAS:TE247201.PNT | 10MKA00CT0115 | GENERATOR STATOR CORE TEMP 7 | RTD | 0 | 500 | °C
1465 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247202.PNT | 1HDAS:TE247202.PNT | 10MKA00CT0116 | GENERATOR STATOR CORE TEMP 8 | RTD | 0 | 500 | °C
1466 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247203.PNT | 1HDAS:TE247203.PNT | 10MKA00CT0117 | GENERATOR STATOR CORE TEMP 9 | RTD | 0 | 500 | °C
1467 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247204.PNT | 1HDAS:TE247204.PNT | 10MKA00CT0118 | GENERATOR STATOR CORE TEMP 10 | RTD | 0 | 500 | °C
1468 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247205.PNT | 1HDAS:TE247205.PNT | 10MKA00CT0119 | GENERATOR STATOR CORE TEMP 11 | RTD | 0 | 500 | °C
1359 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245204.PNT | 1HDAS:TE245204.PNT | 10MKA00CT012 | GENERATOR STATOR COIL OUTLET WATER TEMP 12 | RTD | 0 | 500 | °C
1469 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247206.PNT | 1HDAS:TE247206.PNT | 10MKA00CT0120 | GENERATOR STATOR CORE TEMP 12 | RTD | 0 | 500 | °C
1472 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247301.PNT | 1HDAS:TE247301.PNT | 10MKA00CT0121 | GENERATOR STATOR CORE TEMP 13 | RTD | 0 | 500 | °C
1473 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247302.PNT | 1HDAS:TE247302.PNT | 10MKA00CT0122 | GENERATOR STATOR CORE TEMP 14 | RTD | 0 | 500 | °C
1474 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247303.PNT | 1HDAS:TE247303.PNT | 10MKA00CT0123 | GENERATOR STATOR CORE TEMP 15 | RTD | 0 | 500 | °C
1475 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247304.PNT | 1HDAS:TE247304.PNT | 10MKA00CT0124 | GENERATOR STATOR CORE TEMP 16 | RTD | 0 | 500 | °C
1476 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247305.PNT | 1HDAS:TE247305.PNT | 10MKA00CT0125 | GENERATOR STATOR CORE TEMP 17 | RTD | 0 | 500 | °C
1477 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247306.PNT | 1HDAS:TE247306.PNT | 10MKA00CT0126 | GENERATOR STATOR CORE TEMP 18 | RTD | 0 | 500 | °C
1479 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247402.PNT | 1HDAS:TE247402.PNT | 10MKA00CT0127 | GENERATOR COLD/HOT H2 TEMP 1 | RTD | 0 | 500 | °C
1480 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247403.PNT | 1HDAS:TE247403.PNT | 10MKA00CT0128 | GENERATOR COLD/HOT H2 TEMP 2 | RTD | 0 | 500 | °C
1481 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247404.PNT | 1HDAS:TE247404.PNT | 10MKA00CT0129 | GENERATOR COLD/HOT H2 TEMP 3 | RTD | 0 | 500 | °C
1360 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245205.PNT | 1HDAS:TE245205.PNT | 10MKA00CT013 | GENERATOR STATOR COIL OUTLET WATER TEMP 13 | RTD | 0 | 500 | °C
1482 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247405.PNT | 1HDAS:TE247405.PNT | 10MKA00CT0130 | GENERATOR COLD/HOT H2 TEMP 4 | RTD | 0 | 500 | °C
1486 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247502.PNT | 1HDAS:TE247502.PNT | 10MKA00CT0131 | GENERATOR COLD/HOT H2 TEMP 5 | RTD | 0 | 500 | °C
1487 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247503.PNT | 1HDAS:TE247503.PNT | 10MKA00CT0132 | GENERATOR COLD/HOT H2 TEMP 6 | RTD | 0 | 500 | °C
1488 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247504.PNT | 1HDAS:TE247504.PNT | 10MKA00CT0133 | GENERATOR COLD/HOT H2 TEMP 7 | RTD | 0 | 500 | °C
1489 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247505.PNT | 1HDAS:TE247505.PNT | 10MKA00CT0134 | GENERATOR COLD/HOT H2 TEMP 8 | RTD | 0 | 500 | °C
1493 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247602.PNT | 1HDAS:TE247602.PNT | 10MKA00CT0135 | GENERATOR COLD/HOT H2 TEMP 9 | RTD | 0 | 500 | °C
1494 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247603.PNT | 1HDAS:TE247603.PNT | 10MKA00CT0136 | GENERATOR COLD/HOT H2 TEMP 10 | RTD | 0 | 500 | °C
1495 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247604.PNT | 1HDAS:TE247604.PNT | 10MKA00CT0137 | GENERATOR COLD/HOT H2 TEMP 11 | RTD | 0 | 500 | °C
1496 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247605.PNT | 1HDAS:TE247605.PNT | 10MKA00CT0138 | GENERATOR COLD/HOT H2 TEMP 12 | RTD | 0 | 500 | °C
1497 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247606.PNT | 1HDAS:TE247606.PNT | 10MKA00CT0139 | GENERATOR COLD/HOT H2 TEMP 13 | RTD | 0 | 500 | °C
1361 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245206.PNT | 1HDAS:TE245206.PNT | 10MKA00CT014 | GENERATOR STATOR COIL OUTLET WATER TEMP 14 | RTD | 0 | 500 | °C
1478 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247401.PNT | 1HDAS:TE247401.PNT | 10MKA00CT0140 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 1 | RTD | 0 | 500 | °C
1485 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247501.PNT | 1HDAS:TE247501.PNT | 10MKA00CT0141 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 2 | RTD | 0 | 500 | °C
1492 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE247601.PNT | 1HDAS:TE247601.PNT | 10MKA00CT0142 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 3 | RTD | 0 | 500 | °C
1362 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245207.PNT | 1HDAS:TE245207.PNT | 10MKA00CT015 | GENERATOR STATOR COIL OUTLET WATER TEMP 15 | RTD | 0 | 500 | °C
1363 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245208.PNT | 1HDAS:TE245208.PNT | 10MKA00CT016 | GENERATOR STATOR COIL OUTLET WATER TEMP 16 | RTD | 0 | 500 | °C
1329 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244501.PNT | 1HDAS:TE244501.PNT | 10MKA00CT0160 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 500 | °C
1330 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244502.PNT | 1HDAS:TE244502.PNT | 10MKA00CT0161 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 500 | °C
1331 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244503.PNT | 1HDAS:TE244503.PNT | 10MKA00CT0162 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 500 | °C
1336 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244601.PNT | 1HDAS:TE244601.PNT | 10MKA00CT0163 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 4 | TC | 0 | 500 | °C
1337 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244602.PNT | 1HDAS:TE244602.PNT | 10MKA00CT0164 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 5 | TC | 0 | 500 | °C
1338 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244603.PNT | 1HDAS:TE244603.PNT | 10MKA00CT0165 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 6 | TC | 0 | 500 | °C
1343 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244701.PNT | 1HDAS:TE244701.PNT | 10MKA00CT0166 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 7 | TC | 0 | 500 | °C
1344 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244702.PNT | 1HDAS:TE244702.PNT | 10MKA00CT0167 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 8 | TC | 0 | 500 | °C
1345 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244703.PNT | 1HDAS:TE244703.PNT | 10MKA00CT0168 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 9 | TC | 0 | 500 | °C
1332 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244504.PNT | 1HDAS:TE244504.PNT | 10MKA00CT0169 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 500 | °C
1364 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245301.PNT | 1HDAS:TE245301.PNT | 10MKA00CT017 | GENERATOR STATOR COIL OUTLET WATER TEMP 17 | RTD | 0 | 500 | °C
1339 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244604.PNT | 1HDAS:TE244604.PNT | 10MKA00CT0170 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 500 | °C
1346 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE244704.PNT | 1HDAS:TE244704.PNT | 10MKA00CT0171 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 500 | °C
1365 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245302.PNT | 1HDAS:TE245302.PNT | 10MKA00CT018 | GENERATOR STATOR COIL OUTLET WATER TEMP 18 | RTD | 0 | 500 | °C
1366 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245303.PNT | 1HDAS:TE245303.PNT | 10MKA00CT019 | GENERATOR STATOR COIL OUTLET WATER TEMP 19 | RTD | 0 | 500 | °C
1367 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245304.PNT | 1HDAS:TE245304.PNT | 10MKA00CT020 | GENERATOR STATOR COIL OUTLET WATER TEMP 20 | RTD | 0 | 500 | °C
1368 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245305.PNT | 1HDAS:TE245305.PNT | 10MKA00CT021 | GENERATOR STATOR COIL OUTLET WATER TEMP 21 | RTD | 0 | 500 | °C
1369 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245306.PNT | 1HDAS:TE245306.PNT | 10MKA00CT022 | GENERATOR STATOR COIL OUTLET WATER TEMP 22 | RTD | 0 | 500 | °C
1370 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245307.PNT | 1HDAS:TE245307.PNT | 10MKA00CT023 | GENERATOR STATOR COIL OUTLET WATER TEMP 23 | RTD | 0 | 500 | °C
1371 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245308.PNT | 1HDAS:TE245308.PNT | 10MKA00CT024 | GENERATOR STATOR COIL OUTLET WATER TEMP 24 | RTD | 0 | 500 | °C
1372 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245401.PNT | 1HDAS:TE245401.PNT | 10MKA00CT025 | GENERATOR STATOR COIL OUTLET WATER TEMP 25 | RTD | 0 | 500 | °C
1373 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245402.PNT | 1HDAS:TE245402.PNT | 10MKA00CT026 | GENERATOR STATOR COIL OUTLET WATER TEMP 26 | RTD | 0 | 500 | °C
1374 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245403.PNT | 1HDAS:TE245403.PNT | 10MKA00CT027 | GENERATOR STATOR COIL OUTLET WATER TEMP 27 | RTD | 0 | 500 | °C
1375 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245404.PNT | 1HDAS:TE245404.PNT | 10MKA00CT028 | GENERATOR STATOR COIL OUTLET WATER TEMP 28 | RTD | 0 | 500 | °C
1376 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245405.PNT | 1HDAS:TE245405.PNT | 10MKA00CT029 | GENERATOR STATOR COIL OUTLET WATER TEMP 29 | RTD | 0 | 500 | °C
1377 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245406.PNT | 1HDAS:TE245406.PNT | 10MKA00CT030 | GENERATOR STATOR COIL OUTLET WATER TEMP 30 | RTD | 0 | 500 | °C
1378 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245407.PNT | 1HDAS:TE245407.PNT | 10MKA00CT031 | GENERATOR STATOR COIL OUTLET WATER TEMP 31 | RTD | 0 | 500 | °C
1379 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245408.PNT | 1HDAS:TE245408.PNT | 10MKA00CT032 | GENERATOR STATOR COIL OUTLET WATER TEMP 32 | RTD | 0 | 500 | °C
1380 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245501.PNT | 1HDAS:TE245501.PNT | 10MKA00CT033 | GENERATOR STATOR COIL OUTLET WATER TEMP 33 | RTD | 0 | 500 | °C
1381 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245502.PNT | 1HDAS:TE245502.PNT | 10MKA00CT034 | GENERATOR STATOR COIL OUTLET WATER TEMP 34 | RTD | 0 | 500 | °C
1382 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245503.PNT | 1HDAS:TE245503.PNT | 10MKA00CT035 | GENERATOR STATOR COIL OUTLET WATER TEMP 35 | RTD | 0 | 500 | °C
1383 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245504.PNT | 1HDAS:TE245504.PNT | 10MKA00CT036 | GENERATOR STATOR COIL OUTLET WATER TEMP 36 | RTD | 0 | 500 | °C
1384 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245505.PNT | 1HDAS:TE245505.PNT | 10MKA00CT037 | GENERATOR STATOR COIL OUTLET WATER TEMP 37 | RTD | 0 | 500 | °C
1385 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245506.PNT | 1HDAS:TE245506.PNT | 10MKA00CT038 | GENERATOR STATOR COIL OUTLET WATER TEMP 38 | RTD | 0 | 500 | °C
1386 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245507.PNT | 1HDAS:TE245507.PNT | 10MKA00CT039 | GENERATOR STATOR COIL OUTLET WATER TEMP 39 | RTD | 0 | 500 | °C
1387 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245508.PNT | 1HDAS:TE245508.PNT | 10MKA00CT040 | GENERATOR STATOR COIL OUTLET WATER TEMP 40 | RTD | 0 | 500 | °C
1388 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245601.PNT | 1HDAS:TE245601.PNT | 10MKA00CT041 | GENERATOR STATOR COIL OUTLET WATER TEMP 41 | RTD | 0 | 500 | °C
1389 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245602.PNT | 1HDAS:TE245602.PNT | 10MKA00CT042 | GENERATOR STATOR COIL OUTLET WATER TEMP 42 | RTD | 0 | 500 | °C
1390 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245603.PNT | 1HDAS:TE245603.PNT | 10MKA00CT043 | GENERATOR STATOR COIL OUTLET WATER TEMP 43 | RTD | 0 | 500 | °C
1391 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245604.PNT | 1HDAS:TE245604.PNT | 10MKA00CT044 | GENERATOR STATOR COIL OUTLET WATER TEMP 44 | RTD | 0 | 500 | °C
1392 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245605.PNT | 1HDAS:TE245605.PNT | 10MKA00CT045 | GENERATOR STATOR COIL OUTLET WATER TEMP 45 | RTD | 0 | 500 | °C
1393 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245606.PNT | 1HDAS:TE245606.PNT | 10MKA00CT046 | GENERATOR STATOR COIL OUTLET WATER TEMP 46 | RTD | 0 | 500 | °C
1394 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245607.PNT | 1HDAS:TE245607.PNT | 10MKA00CT047 | GENERATOR STATOR COIL OUTLET WATER TEMP 47 | RTD | 0 | 500 | °C
1395 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245608.PNT | 1HDAS:TE245608.PNT | 10MKA00CT048 | GENERATOR STATOR COIL OUTLET WATER TEMP 48 | RTD | 0 | 500 | °C
1396 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245701.PNT | 1HDAS:TE245701.PNT | 10MKA00CT049 | GENERATOR STATOR COIL OUTLET WATER TEMP 49 | RTD | 0 | 500 | °C
1397 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245702.PNT | 1HDAS:TE245702.PNT | 10MKA00CT050 | GENERATOR STATOR COIL OUTLET WATER TEMP 50 | RTD | 0 | 500 | °C
1398 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245703.PNT | 1HDAS:TE245703.PNT | 10MKA00CT051 | GENERATOR STATOR COIL OUTLET WATER TEMP 51 | RTD | 0 | 500 | °C
1399 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245704.PNT | 1HDAS:TE245704.PNT | 10MKA00CT052 | GENERATOR STATOR COIL OUTLET WATER TEMP 52 | RTD | 0 | 500 | °C
1400 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245705.PNT | 1HDAS:TE245705.PNT | 10MKA00CT053 | GENERATOR STATOR COIL OUTLET WATER TEMP 53 | RTD | 0 | 500 | °C
1401 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE245706.PNT | 1HDAS:TE245706.PNT | 10MKA00CT054 | GENERATOR STATOR COIL OUTLET WATER TEMP 54 | RTD | 0 | 500 | °C
1402 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246101.PNT | 1HDAS:TE246101.PNT | 10MKA00CT055 | GENERATOR STATOR BARS TEMP 1 | RTD | 0 | 500 | °C
1403 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246102.PNT | 1HDAS:TE246102.PNT | 10MKA00CT056 | GENERATOR STATOR BARS TEMP 2 | RTD | 0 | 500 | °C
1404 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246103.PNT | 1HDAS:TE246103.PNT | 10MKA00CT057 | GENERATOR STATOR BARS TEMP 3 | RTD | 0 | 500 | °C
1405 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246104.PNT | 1HDAS:TE246104.PNT | 10MKA00CT058 | GENERATOR STATOR BARS TEMP 4 | RTD | 0 | 500 | °C
1406 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246105.PNT | 1HDAS:TE246105.PNT | 10MKA00CT059 | GENERATOR STATOR BARS TEMP 5 | RTD | 0 | 500 | °C
1407 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246106.PNT | 1HDAS:TE246106.PNT | 10MKA00CT060 | GENERATOR STATOR BARS TEMP 6 | RTD | 0 | 500 | °C
1408 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246107.PNT | 1HDAS:TE246107.PNT | 10MKA00CT061 | GENERATOR STATOR BARS TEMP 7 | RTD | 0 | 500 | °C
1409 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246108.PNT | 1HDAS:TE246108.PNT | 10MKA00CT062 | GENERATOR STATOR BARS TEMP 8 | RTD | 0 | 500 | °C
1410 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246201.PNT | 1HDAS:TE246201.PNT | 10MKA00CT063 | GENERATOR STATOR BARS TEMP 9 | RTD | 0 | 500 | °C
1411 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246202.PNT | 1HDAS:TE246202.PNT | 10MKA00CT064 | GENERATOR STATOR BARS TEMP 10 | RTD | 0 | 500 | °C
1412 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246203.PNT | 1HDAS:TE246203.PNT | 10MKA00CT065 | GENERATOR STATOR BARS TEMP 11 | RTD | 0 | 500 | °C
1413 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246204.PNT | 1HDAS:TE246204.PNT | 10MKA00CT066 | GENERATOR STATOR BARS TEMP 12 | RTD | 0 | 500 | °C
1414 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246205.PNT | 1HDAS:TE246205.PNT | 10MKA00CT067 | GENERATOR STATOR BARS TEMP 13 | RTD | 0 | 500 | °C
1415 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246206.PNT | 1HDAS:TE246206.PNT | 10MKA00CT068 | GENERATOR STATOR BARS TEMP 14 | RTD | 0 | 500 | °C
1416 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246207.PNT | 1HDAS:TE246207.PNT | 10MKA00CT069 | GENERATOR STATOR BARS TEMP 15 | RTD | 0 | 500 | °C
1417 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246208.PNT | 1HDAS:TE246208.PNT | 10MKA00CT070 | GENERATOR STATOR BARS TEMP 16 | RTD | 0 | 500 | °C
1418 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246301.PNT | 1HDAS:TE246301.PNT | 10MKA00CT071 | GENERATOR STATOR BARS TEMP 17 | RTD | 0 | 500 | °C
1419 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246302.PNT | 1HDAS:TE246302.PNT | 10MKA00CT072 | GENERATOR STATOR BARS TEMP 18 | RTD | 0 | 500 | °C
1420 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246303.PNT | 1HDAS:TE246303.PNT | 10MKA00CT073 | GENERATOR STATOR BARS TEMP 19 | RTD | 0 | 500 | °C
1421 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246304.PNT | 1HDAS:TE246304.PNT | 10MKA00CT074 | GENERATOR STATOR BARS TEMP 20 | RTD | 0 | 500 | °C
1422 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246305.PNT | 1HDAS:TE246305.PNT | 10MKA00CT075 | GENERATOR STATOR BARS TEMP 21 | RTD | 0 | 500 | °C
1423 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246306.PNT | 1HDAS:TE246306.PNT | 10MKA00CT076 | GENERATOR STATOR BARS TEMP 22 | RTD | 0 | 500 | °C
1424 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246307.PNT | 1HDAS:TE246307.PNT | 10MKA00CT077 | GENERATOR STATOR BARS TEMP 23 | RTD | 0 | 500 | °C
1425 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246308.PNT | 1HDAS:TE246308.PNT | 10MKA00CT078 | GENERATOR STATOR BARS TEMP 24 | RTD | 0 | 500 | °C
1426 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246401.PNT | 1HDAS:TE246401.PNT | 10MKA00CT079 | GENERATOR STATOR BARS TEMP 25 | RTD | 0 | 500 | °C
1427 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246402.PNT | 1HDAS:TE246402.PNT | 10MKA00CT080 | GENERATOR STATOR BARS TEMP 26 | RTD | 0 | 500 | °C
1428 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246403.PNT | 1HDAS:TE246403.PNT | 10MKA00CT081 | GENERATOR STATOR BARS TEMP 27 | RTD | 0 | 500 | °C
1429 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246404.PNT | 1HDAS:TE246404.PNT | 10MKA00CT082 | GENERATOR STATOR BARS TEMP 28 | RTD | 0 | 500 | °C
1430 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246405.PNT | 1HDAS:TE246405.PNT | 10MKA00CT083 | GENERATOR STATOR BARS TEMP 29 | RTD | 0 | 500 | °C
1431 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246406.PNT | 1HDAS:TE246406.PNT | 10MKA00CT084 | GENERATOR STATOR BARS TEMP 30 | RTD | 0 | 500 | °C
1432 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246407.PNT | 1HDAS:TE246407.PNT | 10MKA00CT085 | GENERATOR STATOR BARS TEMP 31 | RTD | 0 | 500 | °C
1433 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246408.PNT | 1HDAS:TE246408.PNT | 10MKA00CT086 | GENERATOR STATOR BARS TEMP 32 | RTD | 0 | 500 | °C
1434 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246501.PNT | 1HDAS:TE246501.PNT | 10MKA00CT087 | GENERATOR STATOR BARS TEMP 33 | RTD | 0 | 500 | °C
1435 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246502.PNT | 1HDAS:TE246502.PNT | 10MKA00CT088 | GENERATOR STATOR BARS TEMP 34 | RTD | 0 | 500 | °C
1436 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246503.PNT | 1HDAS:TE246503.PNT | 10MKA00CT089 | GENERATOR STATOR BARS TEMP 35 | RTD | 0 | 500 | °C
1437 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246504.PNT | 1HDAS:TE246504.PNT | 10MKA00CT090 | GENERATOR STATOR BARS TEMP 36 | RTD | 0 | 500 | °C
1438 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246505.PNT | 1HDAS:TE246505.PNT | 10MKA00CT091 | GENERATOR STATOR BARS TEMP 37 | RTD | 0 | 500 | °C
1439 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246506.PNT | 1HDAS:TE246506.PNT | 10MKA00CT092 | GENERATOR STATOR BARS TEMP 38 | RTD | 0 | 500 | °C
1440 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246507.PNT | 1HDAS:TE246507.PNT | 10MKA00CT093 | GENERATOR STATOR BARS TEMP 39 | RTD | 0 | 500 | °C
1441 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246508.PNT | 1HDAS:TE246508.PNT | 10MKA00CT094 | GENERATOR STATOR BARS TEMP 40 | RTD | 0 | 500 | °C
1442 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246601.PNT | 1HDAS:TE246601.PNT | 10MKA00CT095 | GENERATOR STATOR BARS TEMP 41 | RTD | 0 | 500 | °C
1443 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246602.PNT | 1HDAS:TE246602.PNT | 10MKA00CT096 | GENERATOR STATOR BARS TEMP 42 | RTD | 0 | 500 | °C
1444 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246603.PNT | 1HDAS:TE246603.PNT | 10MKA00CT097 | GENERATOR STATOR BARS TEMP 43 | RTD | 0 | 500 | °C
1445 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246604.PNT | 1HDAS:TE246604.PNT | 10MKA00CT098 | GENERATOR STATOR BARS TEMP 44 | RTD | 0 | 500 | °C
1446 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50-F290S-K0301-04 | OPC.1HDAS:TE246605.PNT | 1HDAS:TE246605.PNT | 10MKA00CT099 | GENERATOR STATOR BARS TEMP 45 | RTD | 0 | 500 | °C
1185 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50- | OPC.1IDAS:AI120707.PNT | 1IDAS:AI120707.PNT | 10RPSP001 | REAL POWER SET POINT | AI | 0 | 330 | MW
1192 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50- | OPC.1IDAS:AI120807.PNT | 1IDAS:AI120807.PNT | 10MPVSP001 | MAX POWER VARIATION SET POINT | AI | 0 | 15 | MW/Min
1222 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | 50- | OPC.1IDAS:AI121407.PNT | 1IDAS:AI121407.PNT | 10LFC001 | LOAD FREQ CONTROL N_LEVEL | AI | -1 | 1
1434 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD106AIN.PNT_3 | 1VALVE:1AD106AIN.PNT_3 | 10DCSDEHAI01 | CCS DEMAND 1 | AI | 0 | 100 | %
1435 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD107AIN.PNT_3 | 1VALVE:1AD107AIN.PNT_3 | 10DCSDEHAI02 | CCS DEMAND 2 | AI | 0 | 100 | %
1436 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD11206AOUT.OUT | 1VALVE:1AD11206AOUT.OUT | 10DEHDCSAO02 | GENERATOR LOAD | AO | 0 | 519.6 | MW
1437 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD106AIN.PNT_1 | 1VALVE:1AD106AIN.PNT_1 | 10DQDEH01 | GENERATOR LOAD 1 | AI | 0 | 519.6 | MW
1438 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD107AIN.PNT_1 | 1VALVE:1AD107AIN.PNT_1 | 10DQDEH02 | GENERATOR LOAD 2 | AI | 0 | 519.6 | MW
1439 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #10 | F296S-K0606 | OPC.1VALVE:1AD108AIN.PNT_1 | 1VALVE:1AD108AIN.PNT_1 | 10DQDEH03 | GENERATOR LOAD 3 | AI | 0 | 519.6 | MW
1464 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1RDAS:AI220101.PNT | 1RDAS:AI220101.PNT | 10BAT10CE001XR01 | GT HV WINDING TEMPERATURE | AI | 0 | 150 | C
1465 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1RDAS:AI220102.PNT | 1RDAS:AI220102.PNT | 10BAT10CE002XR01 | GT LV WINDING TEMPERATURE | AI | 0 | 150 | C
1462 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1RDAS:AI220103.PNT | 1RDAS:AI220103.PNT | 10BAT10CE003XR01 | GT OIL TEMPERATURE | AI | 0 | 150 | C
1466 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-12 | OPC.1RDAS:AI220104.PNT | 1RDAS:AI220104.PNT | 10BAT10CE004XR01 | GT OLTC CHANGING POSITION | AI | 0 | 20 | TAP
1443 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174101.PNT | 1SDAS:CT174101.PNT | 10MKA01-01 | GEN. CURRENT Ia | AI | 0 | 15000 | A
1444 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174102.PNT | 1SDAS:CT174102.PNT | 10MKA01-02 | GEN. CURRENT Ib | AI | 0 | 15000 | A
1445 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174103.PNT | 1SDAS:CT174103.PNT | 10MKA01-03 | GEN. CURRENT Ic | AI | 0 | 15000 | A
1446 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174104.PNT | 1SDAS:CT174104.PNT | 10MKA01-04 | GEN. NEGATIVE-SEQUENCE CURRENT | AI | 0 | 15000 | A
1447 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174105.PNT | 1SDAS:CT174105.PNT | 10MKA01-05 | GEN. NEUTRAL POINT CURRENT | AI | 0 | 5 | A
1448 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174201.PNT | 1SDAS:CT174201.PNT | 10MKA01-06 | EXCITING TR. HV SIDE CURRENT Ia | AI | 0 | 300 | A
1449 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174202.PNT | 1SDAS:CT174202.PNT | 10MKA01-07 | EXCITING TR. HV SIDE CURRENT Ib | AI | 0 | 300 | A
1450 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:CT174203.PNT | 1SDAS:CT174203.PNT | 10MKA01-08 | EXCITING TR. HV SIDE CURRENT Ic | AI | 0 | 300 | A
1451 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174106.PNT | 1SDAS:AI174106.PNT | 10MKA01-09 | GEN. A-C VOLTAGE | AI | 0 | 24 | kV
1452 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174107.PNT | 1SDAS:AI174107.PNT | 10MKA01-10 | GEN. OUTLET ZERO-SEQUENCE VOLTAGE | AI | 0 | 100 | V
1456 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174108.PNT | 1SDAS:AI174108.PNT | 10MKA01-11 | GEN. ACTIVE POWER | AI | 0 | 450 | MW
1454 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174204.PNT | 1SDAS:AI174204.PNT | 10MKA01-12 | GEN. REACTIVE POWER | AI | -400 | 400 | MVAR
1457 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174205.PNT | 1SDAS:AI174205.PNT | 10MKA01-13 | GEN. POWER FACTOR | AI | -1 | 1 | pF
1458 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-05 | OPC.1SDAS:AI174206.PNT | 1SDAS:AI174206.PNT | 10MKA01-14 | GEN. FREQUENCY | AI | 0 | 60 | Hz
1460 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-14 | OPC.1SDAS:CT174207.PNT | 1SDAS:CT174207.PNT | 10MKA01-15 | FIELD CURRENT | AI | 0 | 3000 | A
1461 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-14 | OPC.1SDAS:AI174208.PNT | 1SDAS:AI174208.PNT | 10MKA01-16 | FIELD VOLTAGE | AI | 0 | 1000 | V
1467 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1SDAS:AI174301.PNT | 1SDAS:AI174301.PNT | 10MKA01-17A | ET A PHASE TEMPERATURE | AI | 0 | 150 | C
1468 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1SDAS:AI174302.PNT | 1SDAS:AI174302.PNT | 10MKA01-18B | ET B PHASE TEMPERATURE | AI | 0 | 150 | C
1469 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #10 | F296S-D0606-11 | OPC.1SDAS:AI174303.PNT | 1SDAS:AI174303.PNT | 10MKA01-19C | ET C PHASE TEMPERATURE | AI | 0 | 150 | C
440 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073505.PNT | 1FDAS:AI073505.PNT | 10MKG00GH001AI01 | GENERATOR H2 LEAKAGE RATE 1 | AI | 0.1 | 2 | %
441 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073506.PNT | 1FDAS:AI073506.PNT | 10MKG00GH001AI02 | GENERATOR H2 LEAKAGE RATE 2 | AI | 0.1 | 2 | %
442 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073507.PNT | 1FDAS:AI073507.PNT | 10MKG00GH001AI03 | GENERATOR H2 LEAKAGE RATE 3 | AI | 0.1 | 2 | %
444 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073601.PNT | 1FDAS:AI073601.PNT | 10MKG00GH001AI04 | GENERATOR H2 LEAKAGE RATE 4 | AI | 0.1 | 2 | %
445 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073602.PNT | 1FDAS:AI073602.PNT | 10MKG00GH001AI05 | GENERATOR H2 LEAKAGE RATE 5 | AI | 0.1 | 2 | %
446 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073603.PNT | 1FDAS:AI073603.PNT | 10MKG00GH001AI06 | GENERATOR H2 LEAKAGE RATE 6 | AI | 0.1 | 2 | %
447 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073604.PNT | 1FDAS:AI073604.PNT | 10MKG00GH001AI07 | GENERATOR H2 LEAKAGE RATE 7 | AI | 0.1 | 2 | %
448 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073605.PNT | 1FDAS:AI073605.PNT | 10MKG00GH001AI08 | GENERATOR H2 LEAKAGE RATE 8 | AI | 0.1 | 2 | %
436 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:PT073501.PNT | 1FDAS:PT073501.PNT | 10MKG10CP201 | GENERATOR INLET HYDROGEN PRESS | AI | 0 | 0.6 | MPa
670 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:RT073802.PNT | 1FDAS:RT073802.PNT | 10MKG10CT001 | GENERATOR INLET HYDROGEN TEMP | RTD | 0 | 100 | °C
671 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:RT073803.PNT | 1FDAS:RT073803.PNT | 10MKG11CT001 | GENERATOR EXHAUST HYDROGEN TEMP | RTD | 0 | 100 | °C
438 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073503.PNT | 1FDAS:AI073503.PNT | 10MKG30CQ201 | GENERATOR TURBINE SIDE HYDROGEN HUMIDITY | AI | 0 | 4 | g/m3
439 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073504.PNT | 1FDAS:AI073504.PNT | 10MKG30CQ202 | GENERATOR COLLECTOR SIDE HYDROGEN HUMIDITY | AI | 0 | 4 | g/m3
437 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.1FDAS:AI073502.PNT | 1FDAS:AI073502.PNT | 10MKG50CQ201 | GENERATOR HYDROGEN PURITY | AI | 75 | 100 | % |  |  | 95
1498 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1HDAS:TE247607.PNT | 1HDAS:TE247607.PNT | 10PGA33CT001 | GENERATOR HYDROGEN COOLER MAIN PIPE INLET TEMP | RTD | 0 | 50 | °C
1462 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1HDAS:TE247107.PNT | 1HDAS:TE247107.PNT | 10PGA33CT002 | GENERATOR HYDROGEN COOLER NO.1 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1463 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1HDAS:TE247108.PNT | 1HDAS:TE247108.PNT | 10PGA33CT003 | GENERATOR HYDROGEN COOLER NO.2 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1470 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1HDAS:TE247207.PNT | 1HDAS:TE247207.PNT | 10PGA33CT004 | GENERATOR HYDROGEN COOLER NO.3 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1471 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1HDAS:TE247208.PNT | 1HDAS:TE247208.PNT | 10PGA33CT005 | GENERATOR HYDROGEN COOLER NO.4 OUTLET WATER TEMP | RTD | 0 | 50 | °C
648 | 2 | UJRBG #10 | 9 | GENERATOR SYSTEM #1 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.1EDAS:RT067607.PNT | 1EDAS:RT067607.PNT | 10PGA33CT006 | TURBINE HOUSER COOLING RETURN WATER TEMP 3 | RTD | 0 | 50 | °C
1870 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 1 | AUX TRANSFORMER #10 SYSTEM |  | OPC.1RDAS:AI220105.PNT | 1RDAS:AI220105.PNT | 10BBT10CE001XR01 | UAT-1 HV Wdg. Temp. | AI | 0 | 150 | ℃
1871 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 1 | AUX TRANSFORMER #10 SYSTEM |  | OPC.1RDAS:AI220106.PNT | 1RDAS:AI220106.PNT | 10BBT10CE002XR01 | UAT-1 LV-1 Wdg. Temp. | AI | 0 | 150 | ℃
1872 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 1 | AUX TRANSFORMER #10 SYSTEM |  | OPC.1RDAS:AI220107.PNT | 1RDAS:AI220107.PNT | 10BBT10CE003XR01 | UAT-1 LV-1 Wdg. Temp. | AI | 0 | 150 | ℃
1873 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 1 | AUX TRANSFORMER #10 SYSTEM |  | OPC.1RDAS:AI220201.PNT | 1RDAS:AI220201.PNT | 10BBT10CE004XR01 | UAT-1 Oil Temp. | AI | 0 | 150 | ℃
1874 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 1 | AUX TRANSFORMER #10 SYSTEM |  | OPC.1RDAS:AI220202.PNT | 1RDAS:AI220202.PNT | 10BBT10CE005XR01 | UAT-1 Tap Position | AI | 1 | 17 | tap
1875 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220203.PNT | 1RDAS:AI220203.PNT | 10BFA10CE001XR01 | 400V Unit PCC#1A-Bus-A R-Y Voltage | AI | 0 | 440 | V
1876 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220204.PNT | 1RDAS:AI220204.PNT | 10BFA10CE001XR02 | 400V Unit PCC#1A-Bus-A Y-B Voltage | AI | 0 | 440 | V
1877 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220205.PNT | 1RDAS:AI220205.PNT | 10BFA10CE001XR03 | 400V Unit PCC#1A-Bus-A B-R Voltage | AI | 0 | 440 | V
1878 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220206.PNT | 1RDAS:AI220206.PNT | 10BFA20CE001XR01 | 400V Unit PCC#1A-Bus-B R-Y Voltage | AI | 0 | 440 | V
1879 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220207.PNT | 1RDAS:AI220207.PNT | 10BFA20CE001XR02 | 400V Unit PCC#1A-Bus-B Y-B Voltage | AI | 0 | 440 | V
1880 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220208.PNT | 1RDAS:AI220208.PNT | 10BFA20CE001XR03 | 400V Unit PCC#1A-Bus-B B-R Voltage | AI | 0 | 440 | V
1881 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220301.PNT | 1RDAS:AI220301.PNT | 10BFB10CE001XR01 | 400V UNIT PCC#1B-Bus-A R-Y Voltage | AI | 0 | 440 | V
1882 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220302.PNT | 1RDAS:AI220302.PNT | 10BFB10CE001XR02 | 400V UNIT PCC#1B-Bus-A Y-B Voltage | AI | 0 | 440 | V
1883 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220303.PNT | 1RDAS:AI220303.PNT | 10BFB10CE001XR03 | 400V UNIT PCC#1B-Bus-A B-R Voltage | AI | 0 | 440 | V
1884 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220304.PNT | 1RDAS:AI220304.PNT | 10BFB20CE001XR01 | 400V UNIT PCC#1B-Bus-B R-Y Voltage | AI | 0 | 440 | V
1885 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220305.PNT | 1RDAS:AI220305.PNT | 10BFB20CE001XR02 | 400V UNIT PCC#1B-Bus-B Y-B Voltage | AI | 0 | 440 | V
1886 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220306.PNT | 1RDAS:AI220306.PNT | 10BFB20CE001XR03 | 400V UNIT PCC#1B-Bus-B B-R Voltage | AI | 0 | 440 | V
1887 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220401.PNT | 1RDAS:AI220401.PNT | 10BMA20CE001XR01 | 400V N/E Switchboard-1 R-Y Voltage | AI | 0 | 440 | V
1888 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220402.PNT | 1RDAS:AI220402.PNT | 10BMA20CE001XR02 | 400V N/E Switchboard-1 Y-B Voltage | AI | 0 | 440 | V
1889 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220403.PNT | 1RDAS:AI220403.PNT | 10BMA20CE001XR03 | 400V N/E Switchboard-1 B-R Voltage | AI | 0 | 440 | V
1893 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220501.PNT | 1RDAS:AI220501.PNT | 10BFC10CE001XR01 | 400V ESP PCC#1-Bus-A R-Y Voltage | AI | 0 | 440 | V
1894 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220502.PNT | 1RDAS:AI220502.PNT | 10BFC10CE001XR02 | 400V ESP PCC#1-Bus-A Y-B Voltage | AI | 0 | 440 | V
1895 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220503.PNT | 1RDAS:AI220503.PNT | 10BFC10CE001XR03 | 400V ESP PCC#1A-Bus-A B-R Voltage | AI | 0 | 440 | V
1896 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220504.PNT | 1RDAS:AI220504.PNT | 10BFC20CE001XR01 | 400V ESP PCC#1-BUS-B R-Y Voltage | AI | 0 | 440 | V
1897 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220505.PNT | 1RDAS:AI220505.PNT | 10BFC20CE001XR02 | 400V ESP PCC#1-BUS-B Y-B Voltage | AI | 0 | 440 | V
1898 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #10 |  | OPC.1RDAS:AI220506.PNT | 1RDAS:AI220506.PNT | 10BFC20CE001XR03 | 400V ESP PCC#1-BUS-B B-R Voltage | AI | 0 | 440 | V
1905 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 3 | 6,3KV UNIT SWBD 1A |  | OPC.1SDAS:AI231101.PNT | 1SDAS:AI231101.PNT | 10BBA21CE001XR01 | 6.3kV UNIT SWBD #1A Bus R-Y Voltage | AI | 0 | 7.2 | kV
1906 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 3 | 6,3KV UNIT SWBD 1A |  | OPC.1SDAS:AI231102.PNT | 1SDAS:AI231102.PNT | 10BBA21CE001XR02 | 6.3kV UNIT SWBD #1A Bus Y-B Voltage | AI | 0 | 7.2 | kV
1907 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 3 | 6,3KV UNIT SWBD 1A |  | OPC.1SDAS:AI231103.PNT | 1SDAS:AI231103.PNT | 10BBA21CE001XR03 | 6.3kV UNIT SWBD #1A Bus B-R Voltage | AI | 0 | 7.2 | kV
1908 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 4 | 6,3KV UNIT SWBD 1B |  | OPC.1SDAS:AI231201.PNT | 1SDAS:AI231201.PNT | 10BBB21CE001XR01 | 6.3kV UNIT SWBD #1B Bus R-Y Voltage | AI | 0 | 7.2 | kV
1909 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 4 | 6,3KV UNIT SWBD 1B |  | OPC.1SDAS:AI231202.PNT | 1SDAS:AI231202.PNT | 10BBB21CE001XR02 | 6.3kV UNIT SWBD #1B Bus Y-B Voltage | AI | 0 | 7.2 | kV
1910 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 4 | 6,3KV UNIT SWBD 1B |  | OPC.1SDAS:AI231203.PNT | 1SDAS:AI231203.PNT | 10BBB21CE001XR03 | 6.3kV UNIT SWBD #1B Bus B-R Voltage | AI | 0 | 7.2 | kV
1899 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 5 | 220V CUM BOOST BATTERY CHARGER #10 |  | OPC.1RDAS:AI220601.PNT | 1RDAS:AI220601.PNT | 10BTL10CE001XR01 | Unit-1 220V DC battery Voltage | AI | 0 | 250 | V
1900 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 5 | 220V CUM BOOST BATTERY CHARGER #10 |  | OPC.1RDAS:AI220602.PNT | 1RDAS:AI220602.PNT | 10BTL10CE001XR02 | Unit-1 220V DCDB Bus Voltage | AI | 0 | 250 | V
1901 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 6 | 110V CUM BOOST BATTERY CHARGER #10 |  | OPC.1RDAS:AI220603.PNT | 1RDAS:AI220603.PNT | 10BTM10CE001XR01 | Unit-1 110V DC battery Voltage | AI | 0 | 150 | V
1902 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 6 | 110V CUM BOOST BATTERY CHARGER #10 |  | OPC.1RDAS:AI220604.PNT | 1RDAS:AI220604.PNT | 10BTM10CE001XR02 | Unit-1 110V DCDB Bus Voltage | AI | 0 | 150 | V
1903 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 7 | UPS #10 |  | OPC.1RDAS:AI220605.PNT | 1RDAS:AI220605.PNT | 10BRU11CE001XR01 | Unit-1 UPS-1A DB bus Voltage | AI | 0 | 300 | V
1904 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 7 | UPS #10 |  | OPC.1RDAS:AI220606.PNT | 1RDAS:AI220606.PNT | 10BRU12CE001XR01 | Unit-1 UPS-1B DB bus Voltage | AI | 0 | 300 | V
1890 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 8 | EDG #10 |  | OPC.1RDAS:AI220404.PNT | 1RDAS:AI220404.PNT | 10XK10CE001XR01 | Unit-1 EDG Voltage (R-Y ph) | AI | 0 | 440 | V
1891 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 8 | EDG #10 |  | OPC.1RDAS:AI220405.PNT | 1RDAS:AI220405.PNT | 10XK10CE001XR02 | Unit-1 EDG Voltage (Y-B ph) | AI | 0 | 440 | V
1892 | 2 | UJRBG #10 | 10 | POWER TRANSFORMER #10 | 8 | EDG #10 |  | OPC.1RDAS:AI220406.PNT | 1RDAS:AI220406.PNT | 10XK10CE001XR03 | Unit-1 EDG Voltage (R-B ph) | AI | 0 | 440 | V
918 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:PT201501.PNT | 1PDAS:PT201501.PNT | 10EGD10CP201 | OIL FEED MAIN PIPE PRESSURE 1 | AI | 0 | 5 | MPa
925 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:PT201601.PNT | 1PDAS:PT201601.PNT | 10EGD10CP202 | OIL FEED MAIN PIPE PRESSURE 2 | AI | 0 | 5 | MPa
283 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1NDAS:RT182108.PNT | 1NDAS:RT182108.PNT | 10EGD10CT001 | OIL FEED MAIN PIPE TEMPERATURE | RTD | 0 | 100 | °C
475 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-06 | OPC.1FDAS:PT086703.PNT | 1FDAS:PT086703.PNT | 10HCB12CP201 | AFTER FUEL OIL ATTEMPERATOR PRESS | AI | 0 | 1 | MPa
1264 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-06 | OPC.1IDAS:TE121501.PNT | 1IDAS:TE121501.PNT | 10HCB12CT001 | AFTER FUEL OIL ATTEMPERATOR TEMP | TC | 0 | 400 | °C
886 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:FT200806.PNT | 1PDAS:FT200806.PNT | 10HJF50CF201 | SUPPLYING OIL FLOW | AI | 0 | 25 | t/h
885 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:PT200805.PNT | 1PDAS:PT200805.PNT | 10HJF50CP201 | SUPPLYING OIL PRESSURE | AI | 0 | 4 | MPa
146 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1LDAS:RT150504.PNT | 1LDAS:RT150504.PNT | 10HJF50CT001 | SUPPLYING OIL TEMPERATURE | RTD | 0 | 100 | °C
1028 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1FUELOIL:AO202507.OUT | 1FUELOIL:AO202507.OUT | 10HJF60AA101XB11 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE CONTROL | AO | 0 | 100 | %
888 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:ZT200808.PNT | 1PDAS:ZT200808.PNT | 10HJF60AA101XB12 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE POSITION | AI | 0 | 100 | %
887 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1PDAS:FT200807.PNT | 1PDAS:FT200807.PNT | 10HJF60CF201 | RETURNED OIL FLOW | AI | 0 | 25 | t/h
222 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-17 | OPC.1ODAS:PT193202.PNT | 1ODAS:PT193202.PNT | 10HJF60CP201 | RETURN OIL PRESSURE | AI | 0 | 1 | MPa
1232 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-07 | OPC.1FULSTMDESUP:AO122205.OUT | 1FULSTMDESUP:AO122205.OUT | 10LCE13AA101XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATING DESUPERHEATING WATER MOTORIZE | AO | 0 | 100 | %
1178 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120605.PNT | 1IDAS:ZT120605.PNT | 10LCE13AA101XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATING DESUPERHEATING WATER MOTORIZE | AI | 0 | 100 | %
1233 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-07 | OPC.1CNCURT:AO122206.OUT | 1CNCURT:AO122206.OUT | 10LCE13AA102XB11 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE | AO | 0 | 100 | %
1179 | 2 | UJRBG #10 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120606.PNT | 1IDAS:ZT120606.PNT | 10LCE13AA102XB12 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE | AI | 0 | 100 | %
1162 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1IDAS:PT120404.PNT | 1IDAS:PT120404.PNT | 10(20)LBG10CP201 | AUXILIARY STEAM HEADER TEMP | AI | 0 | 1.1 | MPa
776 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1FDAS:TE087405.PNT | 1FDAS:TE087405.PNT | 10(20)LBG10CT001 | AUXILIARY STEAM HEADER TEMP | TC | 0 | 400 | °C
1225 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1AUXHDR:AO122104.OUT | 1AUXHDR:AO122104.OUT | 10(20)LBG13AA101XB11 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE CONTRO | AO | 0 | 100 | %
1163 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1IDAS:ZT120405.PNT | 1IDAS:ZT120405.PNT | 10(20)LBG13AA101XB12 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE POSITI | AI | 0 | 100 | %
1226 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1DAPRESS:AO122105.OUT | 1DAPRESS:AO122105.OUT | 10(20)LBG17AA101XB11 | AUXILIARY HEADER TO DEAERATOR SUPPLY STEAM CONTROL VALVE CONTROL C | AO | 0 | 100 | %
1164 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | 50-F290S-J0201-06 | OPC.1IDAS:ZT120406.PNT | 1IDAS:ZT120406.PNT | 10(20)LBG17AA101XB12 | AUXILIARY HEADER TO DEAERATOR SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | %
479 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | 50-F290S-J0201-11 | OPC.1FDAS:ZT086707.PNT | 1FDAS:ZT086707.PNT | 10MAW10AA001XB12 | REGULATING FLOW VALVE (RFV) POSITION | AI | 0 | 100 | %
478 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | 50-F290S-J0201-11 | OPC.1FDAS:PT086706.PNT | 1FDAS:PT086706.PNT | 10MAW10CP201 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX PRESS | AI | 0 | 20
791 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | 50-F290S-J0201-11 | OPC.1FDAS:TE087608.PNT | 1FDAS:TE087608.PNT | 10MAW10CT001 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX TEMP | TC | 0 | 800 | °C
1265 | 2 | UJRBG #10 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | 50-F290S-J0201-11 | OPC.1IDAS:TE121502.PNT | 1IDAS:TE121502.PNT | 10MAW10CT002 | IP CYLINDER START STEAM TEMP | TC | 0 | 400 | °C
6 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1JDAS:AI130606.PNT | 1JDAS:AI130606.PNT | 10HJF71CB201B | 1# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
22 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1KDAS:AI140606.PNT | 1KDAS:AI140606.PNT | 10HJF71CB202B | 1# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
45 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1LDAS:AI150606.PNT | 1LDAS:AI150606.PNT | 10HJF71CB203B | 1# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
7 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1JDAS:AI130607.PNT | 1JDAS:AI130607.PNT | 10HJF72CB201B | 2# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
23 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1KDAS:AI140607.PNT | 1KDAS:AI140607.PNT | 10HJF72CB202B | 2# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
46 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1LDAS:AI150607.PNT | 1LDAS:AI150607.PNT | 10HJF72CB203B | 2# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
14 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1JDAS:AI130706.PNT | 1JDAS:AI130706.PNT | 10HJF73CB201B | 3# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
30 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1KDAS:AI140706.PNT | 1KDAS:AI140706.PNT | 10HJF73CB202B | 3# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
49 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1LDAS:AI150706.PNT | 1LDAS:AI150706.PNT | 10HJF73CB203B | 3# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
15 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1JDAS:AI130707.PNT | 1JDAS:AI130707.PNT | 10HJF74CB201B | 4# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
31 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1KDAS:AI140707.PNT | 1KDAS:AI140707.PNT | 10HJF74CB202B | 4# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
50 | 2 | UJRBG #10 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F290S-J0201-17 | OPC.1LDAS:AI150707.PNT | 1LDAS:AI150707.PNT | 10HJF74CB203B | 4# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
1026 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1BLFLOW:AO202505.OUT | 1BLFLOW:AO202505.OUT | 10LCQ10AA101XB11 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE CONTROL | AO | 0 | 100 | %
879 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1PDAS:ZT200707.PNT | 1PDAS:ZT200707.PNT | 10LCQ10AA101XB12 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE POSITION | AI | 0 | 100 | %
877 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1PDAS:FT200705.PNT | 1PDAS:FT200705.PNT | 10LCQ10CF201 | DRUM CONTINUOUS BLOWDOWN FLOW | AI | 0 | 160 | KPa
878 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1PDAS:LT200706.PNT | 1PDAS:LT200706.PNT | 10LCQ10CL201 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL | AI | 0 | 10 | KPa
1027 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1BLLVL:AO202506.OUT | 1BLLVL:AO202506.OUT | 10LCQ11AA101XB11 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE CONTROL | AO | 0 | 100 | %
880 | 2 | UJRBG #10 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F290S-J0201-16 | OPC.1PDAS:ZT200708.PNT | 1PDAS:ZT200708.PNT | 10LCQ11AA101XB12 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE POSITIO | AI | 0 | 100 | %
409 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1FDAS:PT073102.PNT | 1FDAS:PT073102.PNT | 10LBW00CP201 | GLAND STEAM CONDENSER STEAM SIDE PRESS | AI | -99 | 99 | KPa
1214 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:PT121307.PNT | 1IDAS:PT121307.PNT | 10LBW10CP201 | GLAND MAIN PIPE PRESS | AI | 0 | 129 | Kpa
408 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1FDAS:PT073101.PNT | 1FDAS:PT073101.PNT | 10LBW10CP202 | BFP TURBINE GLAND MAIN PIPE PRESS | AI | 0 | 129 | MPa
783 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1FDAS:TE087507.PNT | 1FDAS:TE087507.PNT | 10LBW10CT001 | GLAND MAIN PIPE TEMP(BEFORE TEMPERATURE REDUCING DEVICE) | TC | 0 | 310 | °C
790 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1FDAS:TE087607.PNT | 1FDAS:TE087607.PNT | 10LBW10CT002 | BFP TURBINE GLAND MAIN PIPE TEMP | TC | 0 | 310 | °C
1262 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:RT121601.PNT | 1IDAS:RT121601.PNT | 10LBW10CT003 | GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | RTD | 0 | 150 | °C
1257 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1GLDHDRP:AO122602.OUT | 1GLDHDRP:AO122602.OUT | 10LBW12AA101XB11 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMA | AO | 0 | 100 | %
1216 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:ZT121401.PNT | 1IDAS:ZT121401.PNT | 10LBW12AA101XB12 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1256 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1GLDHDRP:AO122601.OUT | 1GLDHDRP:AO122601.OUT | 10LBW13AA002XB11 | HP STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1215 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:ZT121308.PNT | 1IDAS:ZT121308.PNT | 10LBW13AA002XB12 | HP STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1258 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1GLDHDRP:AO122603.OUT | 1GLDHDRP:AO122603.OUT | 10LBW14AA101XB11 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAN | AO | 0 | 100 | %
1217 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:ZT121402.PNT | 1IDAS:ZT121402.PNT | 10LBW14AA101XB12 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1259 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1GLDESUP:AO122604.OUT | 1GLDESUP:AO122604.OUT | 10LBW15AA101XB11 | LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1218 | 2 | UJRBG #10 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | TURBINE SEALING SYSTEM #1 | 50-F290S-J0201-10 | OPC.1IDAS:ZT121403.PNT | 1IDAS:ZT121403.PNT | 10LBW15AA101XB12 | LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
1231 | 2 | UJRBG #10 | 81 | TURBINE SEALING #1 | 3 | IP CYLINDER STARTUP STEAM PIPE #1 | 50-F290S-J0201-07 | OPC.1IPSTDESUP:AO122204.OUT | 1IPSTDESUP:AO122204.OUT | 10LCE12AA101XB11 | IP CYLINDER STARTUP STEAM DESUPERHEATING DESUPERHEATING WATER MOTO | AO | 0 | 100 | %
1177 | 2 | UJRBG #10 | 81 | TURBINE SEALING #1 | 3 | IP CYLINDER STARTUP STEAM PIPE #1 | 50-F290S-J0201-07 | OPC.1IDAS:ZT120604.PNT | 1IDAS:ZT120604.PNT | 10LCE12AA101XB12 | IP CYLINDER STARTUP STEAM DESUPERHEATING DESUPERHEATING WATER MOTO | AI | 0 | 100 | %
419 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.1FDAS:LT073205.PNT | 1FDAS:LT073205.PNT | 10MAV00CL201 | MAIN OIL TANK LEVEL | AI | 0 | 2000 | mm |  | 1330 | 1410 | 1910 | 2000
663 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.1FDAS:RT073701.PNT | 1FDAS:RT073701.PNT | 10MAV00CT001 | MAIN OIL TANK OIL TEMP | RTD | 0 | 400 | °C
663 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.1ATC:1BD116AIN.PNT_2 | 1ATC:1BD116AIN.PNT_2 | 10MAV00CT002 | MAIN OIL TANK OIL TEMP | RTD | 0 | 400 | °C
426 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-23 | OPC.1FDAS:CT073305.PNT | 1FDAS:CT073305.PNT | 10MAV20GC001AI02 | TURBINE LUBE OIL TANK ELECTRIC HEATER CURRENT | AI | 0 | 100 | %
418 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.1FDAS:PT073204.PNT | 1FDAS:PT073204.PNT | 10MAV00CP205 | OIL COOLER OUTLET MAIN PIPE OIL PRESS | AI | 0 | 0.6 | MPa
664 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.1FDAS:RT073702.PNT | 1FDAS:RT073702.PNT | 10MAV00CT003 | OIL COOLER INLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | °C
665 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.1FDAS:RT073703.PNT | 1FDAS:RT073703.PNT | 10MAV00CT004 | OIL COOLER OUTLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | °C
661 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-14 | OPC.1EDAS:RT067806.PNT | 1EDAS:RT067806.PNT | 10PGA34CT001 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
662 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-14 | OPC.1EDAS:RT067807.PNT | 1EDAS:RT067807.PNT | 10PGA34CT002 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
415 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 6 | MAIN OIL PUMP #1 | 50-F290S-J0201-19 | OPC.1FDAS:PT073201.PNT | 1FDAS:PT073201.PNT | 10MAV00CP201 | MAIN OIL PUMP INLET PRESS | AI | 0 | 2.5 | MPa
416 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 6 | MAIN OIL PUMP #1 | 50-F290S-J0201-19 | OPC.1FDAS:PT073202.PNT | 1FDAS:PT073202.PNT | 10MAV00CP202 | MAIN OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
413 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 7 | TURBINE AC OIL PUMP #10 | 50-F290S-J0201-19 | OPC.1FDAS:PT073106.PNT | 1FDAS:PT073106.PNT | 10MAV20CP201 | A.C. LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
421 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 7 | TURBINE AC OIL PUMP #10 | 50-F290S-J0201-19 | OPC.1FDAS:CT073207.PNT | 1FDAS:CT073207.PNT | 10MAV20GC001AI01 | TURBINE AC OIL PUMP CURRENT | AI | 0 | 100 | %
449 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 8 | TURBINE JACKING OIL PUMP #10A | 50-F290S-K0301-01 | OPC.1FDAS:PT073606.PNT | 1FDAS:PT073606.PNT | 10MAV00CP206 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa
425 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 8 | TURBINE JACKING OIL PUMP #10A | 50-F290S-K0301-01 | OPC.1FDAS:CT073304.PNT | 1FDAS:CT073304.PNT | 10MAV30AP101XB13 | TURBINE JACKING OIL PUMP A CURRENT | AI | 0 | 100 | %
432 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 9 | TURBINE JACKING OIL PUMP #10B | 50-F290S-K0301-01 | OPC.1FDAS:CT073404.PNT | 1FDAS:CT073404.PNT | 10MAV40AP101XB13 | TURBINE JACKING OIL PUMP B CURRENT | AI | 0 | 100 | %
1642 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 10 | LUBE OIL PIPE #1 | F296S-J0201-19 | OPC.1VALVE:1AD111AIN.PNT_2 | 1VALVE:1AD111AIN.PNT_2 | 10MAV00CP204 | LUBE OIL PRESS | AI | 0 | 0.6 | MPa
1643 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 10 | LUBE OIL PIPE #1 | F296S-J0201-19 | OPC.1ATC:1BD116AIN.PNT_1 | 1ATC:1BD116AIN.PNT_1 | 10MAV00CT042 | LUBE OIL TEMP | RTD | 0 | 120 | C
420 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 11 | TURBINE DC EMERGENCY OIL PUMP #10 | 50-F290S-J0201-19 | OPC.1FDAS:CT073206.PNT | 1FDAS:CT073206.PNT | 10MAV10AP101XB13 | TURBINE DC EMERGENCY OIL PUMP CURRENT | AI | 0 | 100 | %
412 | 2 | UJRBG #10 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 11 | TURBINE DC EMERGENCY OIL PUMP #10 | 50-F290S-J0201-19 | OPC.1FDAS:PT073105.PNT | 1FDAS:PT073105.PNT | 10MAV10CP201 | D.C. EMERGENCY LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
1646 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_1 | 1ATC:1BD115AIN.PNT_1 | 10MAV00CT005 | #1 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1647 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD116AIN.PNT_5 | 1ATC:1BD116AIN.PNT_5 | 10MAV00CT012 | #1 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1648 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD116AIN.PNT_6 | 1ATC:1BD116AIN.PNT_6 | 10MAV00CT013 | #1 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1649 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD103AIN.PNT_7 | 1ATC:1BD103AIN.PNT_7 | 10TSIDEH08 | SHAFT NO.1 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1650 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD103AIN.PNT_8 | 1ATC:1BD103AIN.PNT_8 | 10TSIDEH09 | SHAFT NO.1 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1651 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_3 | 1ATC:1BD105AIN.PNT_3 | 10TSIDEH20 | BEARING COVER NO.1 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1652 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_2 | 1ATC:1BD115AIN.PNT_2 | 10MAV00CT006 | #2 BEARING OIL DRAIN TEMP | RTD | 0 | 120 | C
1653 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD116AIN.PNT_7 | 1ATC:1BD116AIN.PNT_7 | 10MAV00CT014 | #2 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1654 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_1 | 1ATC:1BD117AIN.PNT_1 | 10MAV00CT015 | #2 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1655 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_1 | 1ATC:1BD104AIN.PNT_1 | 10TSIDEH10 | SHAFT NO.2 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1656 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_2 | 1ATC:1BD104AIN.PNT_2 | 10TSIDEH11 | SHAFT NO.2 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1657 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_4 | 1ATC:1BD105AIN.PNT_4 | 10TSIDEH21 | BEARING COVER NO.2 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1658 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_3 | 1ATC:1BD115AIN.PNT_3 | 10MAV00CT010 | #3 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1659 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_2 | 1ATC:1BD117AIN.PNT_2 | 10MAV00CT016 | #3 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1660 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_3 | 1ATC:1BD117AIN.PNT_3 | 10MAV00CT017 | #3 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1661 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_3 | 1ATC:1BD104AIN.PNT_3 | 10TSIDEH12 | SHAFT NO.3 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1662 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_4 | 1ATC:1BD104AIN.PNT_4 | 10TSIDEH13 | SHAFT NO.3 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1663 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_5 | 1ATC:1BD105AIN.PNT_5 | 10TSIDEH22 | BEARING COVER NO.3 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1664 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD115AIN.PNT_4 | 1ATC:1BD115AIN.PNT_4 | 10MAV00CT011 | #4 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1665 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_4 | 1ATC:1BD117AIN.PNT_4 | 10MAV00CT018 | #4 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1666 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD117AIN.PNT_5 | 1ATC:1BD117AIN.PNT_5 | 10MAV00CT019 | #4 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1667 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_5 | 1ATC:1BD104AIN.PNT_5 | 10TSIDEH14 | SHAFT NO.4 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1668 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD104AIN.PNT_6 | 1ATC:1BD104AIN.PNT_6 | 10TSIDEH15 | SHAFT NO.4 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1669 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.1ATC:1BD105AIN.PNT_6 | 1ATC:1BD105AIN.PNT_6 | 10TSIDEH23 | BEARING COVER NO.4 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
666 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | 50-F290S-J0201-19 | OPC.1FDAS:RT073704.PNT | 1FDAS:RT073704.PNT | 10MAV00CT007 | POSITION THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | °C
667 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | 50-F290S-J0201-19 | OPC.1FDAS:RT073705.PNT | 1FDAS:RT073705.PNT | 10MAV00CT008 | THRUST BEARING OIL DRAIN TEMP | RTD | -50 | 150 | °C
668 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | 50-F290S-J0201-19 | OPC.1FDAS:RT073706.PNT | 1FDAS:RT073706.PNT | 10MAV00CT009 | WORK THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | °C
1673 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_4 | 1ATC:1BD113AIN.PNT_4 | 10MAV00CT020 | #1 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1674 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_5 | 1ATC:1BD113AIN.PNT_5 | 10MAV00CT021 | #2 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1675 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_6 | 1ATC:1BD113AIN.PNT_6 | 10MAV00CT022 | #3 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1676 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_7 | 1ATC:1BD113AIN.PNT_7 | 10MAV00CT023 | #4 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1677 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_8 | 1ATC:1BD113AIN.PNT_8 | 10MAV00CT024 | #5 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1678 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_1 | 1ATC:1BD114AIN.PNT_1 | 10MAV00CT025 | #6 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1679 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_2 | 1ATC:1BD114AIN.PNT_2 | 10MAV00CT026 | #7 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1680 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_3 | 1ATC:1BD114AIN.PNT_3 | 10MAV00CT027 | #8 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1681 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_4 | 1ATC:1BD114AIN.PNT_4 | 10MAV00CT028 | #9 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1682 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_5 | 1ATC:1BD114AIN.PNT_5 | 10MAV00CT029 | #10 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1683 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD114AIN.PNT_6 | 1ATC:1BD114AIN.PNT_6 | 10MAV00CT030 | #11 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1684 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_1 | 1ATC:1BD112AIN.PNT_1 | 10MAV00CT031 | #1 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1685 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_2 | 1ATC:1BD112AIN.PNT_2 | 10MAV00CT032 | #2 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1686 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_3 | 1ATC:1BD112AIN.PNT_3 | 10MAV00CT033 | #3 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1687 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_4 | 1ATC:1BD112AIN.PNT_4 | 10MAV00CT034 | #4 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1688 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_5 | 1ATC:1BD112AIN.PNT_5 | 10MAV00CT035 | #5 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1689 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_6 | 1ATC:1BD112AIN.PNT_6 | 10MAV00CT036 | #6 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1690 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_7 | 1ATC:1BD112AIN.PNT_7 | 10MAV00CT037 | #7 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1691 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD112AIN.PNT_8 | 1ATC:1BD112AIN.PNT_8 | 10MAV00CT038 | #8 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1692 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_1 | 1ATC:1BD113AIN.PNT_1 | 10MAV00CT039 | #9 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1693 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_2 | 1ATC:1BD113AIN.PNT_2 | 10MAV00CT040 | #10 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1694 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD113AIN.PNT_3 | 1ATC:1BD113AIN.PNT_3 | 10MAV00CT041 | #11 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1695 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD124AIN.PNT_1 | 1ATC:1BD124AIN.PNT_1 | 10TSIDEH03 | AXIAL DISPLACEMENT NO.1 OUTPUT | AI | -2 | 2 | um
1696 | 2 | UJRBG #10 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.1ATC:1BD124AIN.PNT_2 | 1ATC:1BD124AIN.PNT_2 | 10TSIDEH04 | AXIAL DISPLACEMENT NO.2 OUTPUT (4~20mA) | AI | -2 | 2 | um
555 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-08 | OPC.1HBP:AO113706.OUT | 1HBP:AO113706.OUT | 10LAB21AA101XB11 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
528 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-08 | OPC.1HDAS:ZT113203.PNT | 1HDAS:ZT113203.PNT | 10LAB21AA101XB12 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
529 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113204.PNT | 1HDAS:PT113204.PNT | 10LBA30CP101 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 20 | MPa
530 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113205.PNT | 1HDAS:PT113205.PNT | 10LBA30CP102 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 20 | MPa
835 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:TE113603.PNT | 1HDAS:TE113603.PNT | 10LBA30CT001 | HP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | °C
531 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113206.PNT | 1HDAS:PT113206.PNT | 10LBC30CP101 | HP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 6 | MPa
836 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:TE113604.PNT | 1HDAS:TE113604.PNT | 10LBC30CT001 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 400 | °C
550 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HBP:AO113701.OUT | 1HBP:AO113701.OUT | 10LBF10AA101XB11 | HP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
526 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:ZT113201.PNT | 1HDAS:ZT113201.PNT | 10LBF10AA101XB12 | HP BYPASS PRESS CONTROL VALVE CONTROL POSITION | AI | 0 | 100 | %
1699 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS CONTROL VALVE #10 | F296S-J0201-08 | OPC.1HDAS:PT113208.PNT | 1HDAS:PT113208.PNT | 10LAB21CP201 | HP BYPASS DESUPERHEATING WATER PRESS | AI | 0 | 25 | MPa
521 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113104.PNT | 1HDAS:PT113104.PNT | 10LBB30CP101 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 6 | MPa
833 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:TE113601.PNT | 1HDAS:TE113601.PNT | 10LBB30CT001 | LP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | °C
522 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113105.PNT | 1HDAS:PT113105.PNT | 10LBB40CP101 | LP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 2 | MPa
834 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:TE113602.PNT | 1HDAS:TE113602.PNT | 10LBB40CT001 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 200 | °C
1266 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1IDAS:TE121503.PNT | 1IDAS:TE121503.PNT | 10LBB41CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CON | TC | 0 | 400 | °C
1267 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1IDAS:TE121504.PNT | 1IDAS:TE121504.PNT | 10LBB42CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CON | TC | 0 | 400 | °C
552 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1LBP:AO113703.OUT | 1LBP:AO113703.OUT | 10LCE16AA101XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AO | 0 | 100 | %
519 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1HDAS:ZT113102.PNT | 1HDAS:ZT113102.PNT | 10LCE16AA101XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AI | 0 | 100 | %
553 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1LBP:AO113704.OUT | 1LBP:AO113704.OUT | 10LCE16AA102XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AO | 0 | 100 | %
527 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1HDAS:ZT113202.PNT | 1HDAS:ZT113202.PNT | 10LCE16AA102XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AI | 0 | 100 | %
554 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1LBP:AO113705.OUT | 1LBP:AO113705.OUT | 10LCE17AA101XB11 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
520 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-07 | OPC.1HDAS:ZT113103.PNT | 1HDAS:ZT113103.PNT | 10LCE17AA101XB12 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
551 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1LBP:AO113702.OUT | 1LBP:AO113702.OUT | 10MAN10AA101XB11 | LP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
518 | 2 | UJRBG #10 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS CONTROL VALVE #10 | 50-F290S-J0201-04 | OPC.1HDAS:ZT113101.PNT | 1HDAS:ZT113101.PNT | 10MAN10AA101XB12 | LP BYPASS PRESS CONTROL VALVE POSITION | AI | 0 | 100 | %
1730 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 2 | HP TURBINE #1 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.1ATC:1BD12405AOUT.OUT | 1ATC:1BD12405AOUT.OUT | 10MAX20AA001XB11 | MSV2 CONTROL COMMAND | AO | 0 | 100 | %
1729 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 2 | HP TURBINE #1 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.1ATC:1BD124AIN.PNT_4 | 1ATC:1BD124AIN.PNT_4 | 10MAX20AA001XB12 | MSV2 POSITION | AI | 0 | 100 | %
1732 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 3 | HP TURBINE #1 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.1VALVE:1AD11105AOUT.OUT | 1VALVE:1AD11105AOUT.OUT | 10MAX10AA102XB11 | CV4 CONTROL COMMAND | AO | 0 | 100 | %
1731 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 3 | HP TURBINE #1 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.1VALVE:1AD111AIN.PNT_4 | 1VALVE:1AD111AIN.PNT_4 | 10MAX10AA102XB12 | CV4 POSITION | AI | 0 | 100 | %
1734 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 4 | HP TURBINE #1 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.1VALVE:1AD10605AOUT.OUT | 1VALVE:1AD10605AOUT.OUT | 10MAX10AA101XB11 | CV1 CONTROL COMMAND | AO | 0 | 100 | %
1733 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 4 | HP TURBINE #1 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.1VALVE:1AD106AIN.PNT_4 | 1VALVE:1AD106AIN.PNT_4 | 10MAX10AA101XB12 | CV1 POSITION | AI | 0 | 100 | %
1736 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 5 | HP TURBINE #1 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.1VALVE:1AD10705AOUT.OUT | 1VALVE:1AD10705AOUT.OUT | 10MAX20AA101XB11 | CV2 CONTROL COMMAND | AO | 0 | 100 | %
1735 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 5 | HP TURBINE #1 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.1VALVE:1AD107AIN.PNT_4 | 1VALVE:1AD107AIN.PNT_4 | 10MAX20AA101XB12 | CV2 POSITION | AI | 0 | 100 | %
1739 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 6 | HP TURBINE #1 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.1VALVE:1AD10805AOUT.OUT | 1VALVE:1AD10805AOUT.OUT | 10MAX20AA102XB11 | CV3 CONTROL COMMAND | AO | 0 | 100 | %
1738 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 6 | HP TURBINE #1 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.1VALVE:1AD108AIN.PNT_4 | 1VALVE:1AD108AIN.PNT_4 | 10MAX20AA102XB12 | CV3 POSITION | AI | 0 | 100 | %
476 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | 50-F290S-J0201-04 | OPC.1FDAS:PT086704.PNT | 1FDAS:PT086704.PNT | 10LBB11CP202 | IP GOV VALVE REAR STEAM PRESS (LEFT) | AI | 0 | 6 | MPa
1803 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296Z-J0201-04 | OPC.1ATC:1BD103AIN.PNT_1 | 1ATC:1BD103AIN.PNT_1 | 10LBB11CP201 | IP GOV VALVE FRONT STEAM PRESS (LEFT) | AI | 0 | 6 | MPa
1804 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296Z-J0201-04 | OPC.1ATC:1BD106AIN.PNT_3 | 1ATC:1BD106AIN.PNT_3 | 10LBB11CT001 | REHEAT STEAM TEMP(LEFT) | TC | 0 | 600 | C
1742 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296S-J0201-04 | OPC.1VALVE:1AD11205AOUT.OUT | 1VALVE:1AD11205AOUT.OUT | 10MAB10AA001XB11 | ICV1 CONTROL COMMAND | AO | 0 | 100 | %
1741 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296S-J0201-04 | OPC.1VALVE:1AD112AIN.PNT_4 | 1VALVE:1AD112AIN.PNT_4 | 10MAB10AA001XB12 | ICV1 POSITION | AI | 0 | 100 | %
483 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | 50-F290S-J0201-04 | OPC.1FDAS:PT086804.PNT | 1FDAS:PT086804.PNT | 10LBB12CP202 | IP GOV VALVE REAR STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa
1805 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296Z-J0201-04 | OPC.1ATC:1BD103AIN.PNT_2 | 1ATC:1BD103AIN.PNT_2 | 10LBB12CP201 | IP GOV VALVE FRONT STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa
1806 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296Z-J0201-04 | OPC.1ATC:1BD106AIN.PNT_4 | 1ATC:1BD106AIN.PNT_4 | 10LBB12CT001 | REHEAT STEAM TEMP(RIGHT) | TC | 0 | 600 | C
1745 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296S-J0201-04 | OPC.1VALVE:1AD11305AOUT.OUT | 1VALVE:1AD11305AOUT.OUT | 10MAB20AA001XB11 | ICV2 CONTROL COMMAND | AO | 0 | 100 | %
1744 | 2 | UJRBG #10 | 85 | TURBINE VALVE #1 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296S-J0201-04 | OPC.1VALVE:1AD113AIN.PNT_4 | 1VALVE:1AD113AIN.PNT_4 | 10MAB20AA001XB12 | ICV2 POSITION | AI | 0 | 100 | %
1220 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F289S-K0606-01 | OPC.1IDAS:ZT121405.PNT | 1IDAS:ZT121405.PNT | 10DEHDCS01 | TURBINE POSITION | AI | 0 | 100
480 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:PT086801.PNT | 1FDAS:PT086801.PNT | 10LBA12CP202 | HP GOV VALVE STEAM PRESS | AI | 0 | 20 | MPa
781 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087505.PNT | 1FDAS:TE087505.PNT | 10LBC11CT001 | HP EXHAUSTING PIPE(LEFT) TOP TEMP | TC | 0 | 800 | °C
788 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087605.PNT | 1FDAS:TE087605.PNT | 10LBC11CT002 | HP EXHAUSTING PIPE(LEFT) BOTTOM TEMP | TC | 0 | 400 | °C
782 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087506.PNT | 1FDAS:TE087506.PNT | 10LBC12CT001 | HP EXHAUSTING PIPE(RIGHT) TOP TEMP | TC | 0 | 400 | °C
789 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087606.PNT | 1FDAS:TE087606.PNT | 10LBC12CT002 | HP EXHAUSTING PIPE(RIGHT) BOTTOM TEMP | TC | 0 | 400 | °C
1136 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120102.PNT | 1IDAS:PT120102.PNT | 10MAA10CP202 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1144 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120202.PNT | 1IDAS:PT120202.PNT | 10MAA10CP203 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1152 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1IDAS:PT120302.PNT | 1IDAS:PT120302.PNT | 10MAA10CP204 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
532 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1HDAS:PT113207.PNT | 1HDAS:PT113207.PNT | 10MAA10CP205 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
481 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-J0201-04 | OPC.1FDAS:PT086802.PNT | 1FDAS:PT086802.PNT | 10MAA10CP206 | HP SIXTH STAGE STEAM PRESS | AI | 0 | 10 | MPa
1347 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244705.PNT | 1HDAS:TE244705.PNT | 10MAA10CT010 | HP INNER & OUTER CYLINDER INTERLAY BAFFLE PLATE FRONT TEMP | TC | 0 | 500 | °C
1317 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244301.PNT | 1HDAS:TE244301.PNT | 10MAA10CT011 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(LEFT) | TC | 0 | 500 | °C
1318 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244302.PNT | 1HDAS:TE244302.PNT | 10MAA10CT012 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(LEFT) | TC | 0 | 500 | °C
1319 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244303.PNT | 1HDAS:TE244303.PNT | 10MAA10CT013 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(LEFT) | TC | 0 | 500 | °C
1323 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244401.PNT | 1HDAS:TE244401.PNT | 10MAA10CT014 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1324 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244402.PNT | 1HDAS:TE244402.PNT | 10MAA10CT015 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1325 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244403.PNT | 1HDAS:TE244403.PNT | 10MAA10CT016 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1320 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244304.PNT | 1HDAS:TE244304.PNT | 10MAA10CT023 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 500 | °C
1321 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244305.PNT | 1HDAS:TE244305.PNT | 10MAA10CT024 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 500 | °C
1322 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244306.PNT | 1HDAS:TE244306.PNT | 10MAA10CT025 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 500 | °C
1326 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244404.PNT | 1HDAS:TE244404.PNT | 10MAA10CT026 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 500 | °C
1327 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244405.PNT | 1HDAS:TE244405.PNT | 10MAA10CT027 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 500 | °C
1328 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244406.PNT | 1HDAS:TE244406.PNT | 10MAA10CT028 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 500 | °C
1333 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244505.PNT | 1HDAS:TE244505.PNT | 10MAA10CT029 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 500 | °C
1334 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244506.PNT | 1HDAS:TE244506.PNT | 10MAA10CT030 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 500 | °C
1335 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244507.PNT | 1HDAS:TE244507.PNT | 10MAA10CT031 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 500 | °C
1340 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244605.PNT | 1HDAS:TE244605.PNT | 10MAA10CT032 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 500 | °C
1341 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244606.PNT | 1HDAS:TE244606.PNT | 10MAA10CT033 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 500 | °C
1342 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F290S-K0301-03 | OPC.1HDAS:TE244607.PNT | 1HDAS:TE244607.PNT | 10MAA10CT034 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 500 | °C
450 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | 50-F289S-K0302-03 | OPC.1FDAS:AI073607.PNT | 1FDAS:AI073607.PNT | 10TSIDCS21 | TURBINE SPEED (4~20mA) | AI | 0 | 5000 | rpm
1746 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296S-K0606 | OPC.1VALVE:1AD11106AOUT.OUT | 1VALVE:1AD11106AOUT.OUT | 10DEHDCSAO01 | TURBINE POSITION | AO | 0 | 100 | %
1748 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1VALVE:1AD111AIN.PNT_1 | 1VALVE:1AD111AIN.PNT_1 | 10LBA11CP201 | MAIN STEAM PRESS(LEFT) | AI | 0 | 18 | MPa
1749 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1ATC:1BD106AIN.PNT_1 | 1ATC:1BD106AIN.PNT_1 | 10LBA11CT001 | MAIN STEAM TEMPERATURE (LEFT) | TC | 0 | 600 | C
1750 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1VALVE:1AD112AIN.PNT_1 | 1VALVE:1AD112AIN.PNT_1 | 10LBA12CP201 | MAIN STEAM PRESS(RIGHT) | AI | 0 | 18 | MPa
1751 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1ATC:1BD106AIN.PNT_2 | 1ATC:1BD106AIN.PNT_2 | 10LBA12CT001 | MAIN STEAM TEMPERATURE (RIGHT) | TC | 0 | 600 | C
1756 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1VALVE:1AD107AIN.PNT_2 | 1VALVE:1AD107AIN.PNT_2 | 10MAA10CP201 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1763 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1VALVE:1AD108AIN.PNT_2 | 1VALVE:1AD108AIN.PNT_2 | 10MAA10CP207 | HP EXHAUSTING STEAM PRESS | AI | 0 | 5 | MPa
1764 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1ATC:1BD107AIN.PNT_2 | 1ATC:1BD107AIN.PNT_2 | 10MAA10CT001 | HP EXHAUSTING TEMP (UPPER) | TC | 0 | 600 | C
1765 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1ATC:1BD111AIN.PNT_1 | 1ATC:1BD111AIN.PNT_1 | 10MAA10CT002 | HP EXHAUSTING TEMP (LOWER) | TC | 0 | 600 | C
1766 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-04 | OPC.1ATC:1BD107AIN.PNT_1 | 1ATC:1BD107AIN.PNT_1 | 10MAA10CT003 | STEAM TEMP AFTER HP GOV STAGE | TC | 0 | 600 | C
1767 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_5 | 1ATC:1BD108AIN.PNT_5 | 10MAA10CT004 | HP EXHAUSTING UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C
1768 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_6 | 1ATC:1BD108AIN.PNT_6 | 10MAA10CT005 | HP EXHAUSTING BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C
1769 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD107AIN.PNT_4 | 1ATC:1BD107AIN.PNT_4 | 10MAA10CT006 | HP INNER CYLINDER UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C
1770 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD107AIN.PNT_6 | 1ATC:1BD107AIN.PNT_6 | 10MAA10CT007 | HP INNER CYLINDER UPPER HALF OUTER WALL TEMP | TC | 0 | 600 | C
1771 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD107AIN.PNT_5 | 1ATC:1BD107AIN.PNT_5 | 10MAA10CT008 | HP INNER CYLINDER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C
1772 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD107AIN.PNT_7 | 1ATC:1BD107AIN.PNT_7 | 10MAA10CT009 | HP INNER CYLINDER BOTTOM HALF OUTER WALL TEMP | TC | 0 | 600 | C
1780 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD106AIN.PNT_7 | 1ATC:1BD106AIN.PNT_7 | 10MAA10CT017 | HP MSV INNER WALL METAL TEMP (LEFT) | TC | 0 | 600 | C
1781 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD106AIN.PNT_5 | 1ATC:1BD106AIN.PNT_5 | 10MAA10CT018 | HP MSV OUTER WALL METAL TEMP | TC | 0 | 600 | C
1782 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD106AIN.PNT_8 | 1ATC:1BD106AIN.PNT_8 | 10MAA10CT019 | HP MSV INNER WALL METAL TEMP | TC | 0 | 600 | C
1783 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD106AIN.PNT_6 | 1ATC:1BD106AIN.PNT_6 | 10MAA10CT020 | HP MSV OUTER WALL METAL TEMP (RIGHT) | TC | 0 | 600 | C
1784 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD111AIN.PNT_4 | 1ATC:1BD111AIN.PNT_4 | 10MAA10CT021 | HP MSCV INNER WALL METAL TEMP | TC | 0 | 600 | C
1785 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296Z-J0201-46 | OPC.1ATC:1BD111AIN.PNT_5 | 1ATC:1BD111AIN.PNT_5 | 10MAA10CT022 | HP MSCV OUTER WALL METAL TEMP | TC | 0 | 600 | C
1799 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296S-J0201-19 | OPC.1VALVE:1AD113AIN.PNT_1 | 1VALVE:1AD113AIN.PNT_1 | 10TSIDEH01 | ECCENTRICITY OUTPUT (4~20mA) | AI | 0 | 100 | um
1800 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296S-J0201-19 | OPC.1VALVE:1AD111AIN.PNT_3 | 1VALVE:1AD111AIN.PNT_3 | 10TSIDEH02 | HP/IP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | -7 | 9 | um
1801 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296S-J0201-19 | OPC.1ATC:1BD103AIN.PNT_5 | 1ATC:1BD103AIN.PNT_5 | 10TSIDEH06 | HP CYLINDER(LEFT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm
1802 | 2 | UJRBG #10 | 86 | TURBINE #1 | 1 | HP TURBINE #10 | F296S-J0201-19 | OPC.1ATC:1BD103AIN.PNT_6 | 1ATC:1BD103AIN.PNT_6 | 10TSIDEH07 | HP CYLINDER(RIGHT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm
482 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:PT086803.PNT | 1FDAS:PT086803.PNT | 10MAB10CP202 | IP THIRD STAGE STEAM PRESS | AI | 0 | 2 | MPa
1807 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-04 | OPC.1VALVE:1AD108AIN.PNT_3 | 1VALVE:1AD108AIN.PNT_3 | 10MAB10CP201 | IP EXHAUSTING STEAM PRESS | AI | 0 | 1 | MPa
1809 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-04 | OPC.1ATC:1BD107AIN.PNT_3 | 1ATC:1BD107AIN.PNT_3 | 10MAB10CT001 | IP EXHAUSTING STEAM TEMP | TC | 0 | 600 | C
1810 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_2 | 1ATC:1BD108AIN.PNT_2 | 10MAB10CT002 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF INNER TEMP | TC | 0 | 600 | C
1811 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_4 | 1ATC:1BD108AIN.PNT_4 | 10MAB10CT003 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF OUTER TEMP | TC | 0 | 600 | C
1812 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_1 | 1ATC:1BD108AIN.PNT_1 | 10MAB10CT004 | HP/IP OUTER CYLINDER IP STEAM INLET UPPER HALF INNER TEMP | TC | 0 | 600 | C
1813 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_3 | 1ATC:1BD108AIN.PNT_3 | 10MAB10CT005 | HP/IP OUTER CYLINDER IP STEAM INLETA UPPER HALF OUTER TEMP | TC | 0 | 600 | C
1814 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_8 | 1ATC:1BD108AIN.PNT_8 | 10MAB10CT006 | IP EXHAUSTING BOTTOM HALF INNER METAL TEMP | TC | 0 | 600 | C
1815 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD108AIN.PNT_7 | 1ATC:1BD108AIN.PNT_7 | 10MAB10CT007 | IP EXHAUSTING UPPER HALF INNER METAL TEMP | TC | 0 | 600 | C
1816 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD111AIN.PNT_3 | 1ATC:1BD111AIN.PNT_3 | 10MAB10CT008 | CLAPBOARD BOTTOM HALF INNER TEMP | TC | 0 | 600 | C
1817 | 2 | UJRBG #10 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #10 | F296Z-J0201-46 | OPC.1ATC:1BD111AIN.PNT_2 | 1ATC:1BD111AIN.PNT_2 | 10MAB10CT009 | CLAPBOARD UPPER HALF INNER TEMP | TC | 0 | 600 | C
674 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:RT087701.PNT | 1FDAS:RT087701.PNT | 10MAC10CT001B | LP EXHAUSTING STEAM TEMP(FRONT & RIGHT) | RTD | 0 | 400 | °C
675 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:RT087702.PNT | 1FDAS:RT087702.PNT | 10MAC10CT002B | LP EXHAUSTING STEAM TEMP(REAR & LEFT) | RTD | 0 | 800 | °C
780 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087504.PNT | 1FDAS:TE087504.PNT | 10MAC10CT003 | BACKWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 800 | °C
787 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087604.PNT | 1FDAS:TE087604.PNT | 10MAC10CT004 | FORWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 800 | °C
777 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087501.PNT | 1FDAS:TE087501.PNT | 10MAC10CT005 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 800 | °C
784 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087601.PNT | 1FDAS:TE087601.PNT | 10MAC10CT006 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 800 | °C
778 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087502.PNT | 1FDAS:TE087502.PNT | 10MAC10CT007 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 800 | °C
785 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1FDAS:TE087602.PNT | 1FDAS:TE087602.PNT | 10MAC10CT008 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 800 | °C
1818 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1ATC:1BD116AIN.PNT_3 | 1ATC:1BD116AIN.PNT_3 | 10MAC10CT001A | LP EXHAUSTING STEAM TEMP（FRONT & RIGHT） | RTD | 0 | 120 | C
1820 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1ATC:1BD116AIN.PNT_4 | 1ATC:1BD116AIN.PNT_4 | 10MAC10CT002A | LP EXHAUSTING STEAM TEMP（BACK & LEFT） | RTD | 0 | 120 | C
1828 | 2 | UJRBG #10 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #10 | 50-F290S-J0201-04 | OPC.1ATC:1BD124AIN.PNT_3 | 1ATC:1BD124AIN.PNT_3 | 10TSIDEH05 | LP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | 0 | 16 | um
1830 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060401.PNT | 0EDAS:LT060401.PNT | 10PAA10CL001XR01 | UPSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 1A | AI | 0 | 10 | m
1831 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060402.PNT | 0EDAS:LT060402.PNT | 10PAA10CL002XR01 | DOWNSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 1A | AI | 0 | 10 | m
1832 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060403.PNT | 0EDAS:LT060403.PNT | 10PAA10CL003XR01 | UPSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 1A | AI | 0 | 12 | m
1833 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060404.PNT | 0EDAS:LT060404.PNT | 10PAA10CL004XR01 | DOWNSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 1A | AI | 0 | 12 | m
1831 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060101.PNT | 0EDAS:LT060101.PNT | 10PAC10CL001XR01 | SEAWATER INTAKE WATER PIT 1A LEVEL TRANSMITTER A | AI | 0 | 10 | m
1832 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060201.PNT | 0EDAS:LT060201.PNT | 10PAC10CL002XR01 | SEAWATER INTAKE WATER PIT 1A LEVEL TRANSMITTER B | AI | 0 | 10 | m
1833 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:LT060301.PNT | 0EDAS:LT060301.PNT | 10PAC10CL003XR01 | SEAWATER INTAKE WATER PIT 1A LEVEL TRANSMITTER C | AI | 0 | 10 | m
1835 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:AI060601.PNT | 0EDAS:AI060601.PNT | 10PAC10GC001XR01 | #0 CWP 1A DISCHAREG VALVE OPENING | AI | 0 | 100 | %
1829 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:CT060305.PNT | 0EDAS:CT060305.PNT | 00BCC12CE001XQ01 | CIRCULATING WATER PUMP 1A MOTOR CURRENT | AI | 0 | 300 | A
1837 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061101.PNT | 0EDAS:RT061101.PNT | 10PAC10CT001XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE #1 (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1838 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061201.PNT | 0EDAS:RT061201.PNT | 10PAC10CT002XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE#2 (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1839 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061102.PNT | 0EDAS:RT061102.PNT | 10PAC10CT003XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE #1(S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1840 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061202.PNT | 0EDAS:RT061202.PNT | 10PAC10CT004XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE #2 (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1841 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061103.PNT | 0EDAS:RT061103.PNT | 10PAC10CT005XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE #1 (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1842 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061203.PNT | 0EDAS:RT061203.PNT | 10PAC10CT006XR01 | CIRC.WATER PUMP 1A WINDING TEMPERATURE #2(T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1843 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061104.PNT | 0EDAS:RT061104.PNT | 10PAC10CT007XR01 | CIRC.WATER PUMP 1A GUIDE BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1844 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061204.PNT | 0EDAS:RT061204.PNT | 10PAC10CT008XR01 | CIRC.WATER PUMP 1A GUIDE BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1845 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061105.PNT | 0EDAS:RT061105.PNT | 10PAC10CT009XR01 | CIRC.WATER PUMP 1A THRUST BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1846 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061205.PNT | 0EDAS:RT061205.PNT | 10PAC10CT010XR01 | CIRC.WATER PUMP 1A THRUST BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1847 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:RT061106.PNT | 0EDAS:RT061106.PNT | 10PAC10CT011XR01 | CIRC.WATER PUMP 1A LOWER MOTOR BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1848 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:AI060605.PNT | 0EDAS:AI060605.PNT | 10PAC10CY001XR01 | CIRC. WATER PUMP 1A HORIZONTAL VIBRATION 1 | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:AI060701.PNT | 0EDAS:AI060701.PNT | 10PAC10CY002XR01 | CIRC. WATER PUMP 1A HORIZONTAL VIBRATION 2 | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:AI060606.PNT | 0EDAS:AI060606.PNT | 10PAC10CY003XR01 | CIRC.WATER PUMP 1A VERTICAL VIBRATION | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.0EDAS:PT060108.PNT | 0EDAS:PT060108.PNT | 10PAB30CP001XR01 | CIRCULATING WATER DISCHARGE HEADER PRESSURE | AI | 0 | 0.6 | MPa
1851 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060405.PNT | 0EDAS:LT060405.PNT | 10PAA20CL001XR01 | UPSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 1B | AI | 0 | 10 | m
1852 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060406.PNT | 0EDAS:LT060406.PNT | 10PAA20CL002XR01 | DOWNSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 1B | AI | 0 | 10 | m
1853 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060407.PNT | 0EDAS:LT060407.PNT | 10PAA20CL003XR01 | UPSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 1B | AI | 0 | 12 | m
1854 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060408.PNT | 0EDAS:LT060408.PNT | 10PAA20CL004XR01 | DOWNSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 1B | AI | 0 | 12 | m
1852 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060102.PNT | 0EDAS:LT060102.PNT | 10PAC20CL001XR01 | SEAWATER INTAKE WATER PIT 1B LEVEL TRANSMITTER A | AI | 0 | 10 | m
1853 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060202.PNT | 0EDAS:LT060202.PNT | 10PAC20CL002XR01 | SEAWATER INTAKE WATER PIT 1B LEVEL TRANSMITTER B | AI | 0 | 10 | m
1854 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:LT060302.PNT | 0EDAS:LT060302.PNT | 10PAC20CL003XR01 | SEAWATER INTAKE WATER PIT 1B LEVEL TRANSMITTER C | AI | 0 | 10 | m
1855 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:AI060602.PNT | 0EDAS:AI060602.PNT | 10PAC20GC001XR01 | #0 CWP 1B DISCHAREG VALVE OPENING | AI | 0 | 100 | %
1850 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:CT060306.PNT | 0EDAS:CT060306.PNT | 00BCC13CE001XQ01 | CIRCULATING WATER PUMP 1B MOTOR CURRENT | AI | 0 | 300 | A
1857 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061301.PNT | 0EDAS:RT061301.PNT | 10PAC20CT001XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1858 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061401.PNT | 0EDAS:RT061401.PNT | 10PAC20CT002XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1859 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061302.PNT | 0EDAS:RT061302.PNT | 10PAC20CT003XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1860 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061402.PNT | 0EDAS:RT061402.PNT | 10PAC20CT004XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1861 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061303.PNT | 0EDAS:RT061303.PNT | 10PAC20CT005XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1862 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061403.PNT | 0EDAS:RT061403.PNT | 10PAC20CT006XR01 | CIRC.WATER PUMP 1B WINDING TEMPERATURE (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1863 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061304.PNT | 0EDAS:RT061304.PNT | 10PAC20CT007XR01 | CIRC.WATER PUMP 1B GUIDE BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1864 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061404.PNT | 0EDAS:RT061404.PNT | 10PAC20CT008XR01 | CIRC.WATER PUMP 1B GUIDE BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1865 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061305.PNT | 0EDAS:RT061305.PNT | 10PAC20CT009XR01 | CIRC.WATER PUMP 1B THRUST BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1866 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061405.PNT | 0EDAS:RT061405.PNT | 10PAC20CT010XR01 | CIRC.WATER PUMP 1B THRUST BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1867 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:RT061306.PNT | 0EDAS:RT061306.PNT | 10PAC20CT011XR01 | CIRC.WATER PUMP 1B LOWER MOTOR BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1868 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:AI060607.PNT | 0EDAS:AI060607.PNT | 10PAC20CY001XR01 | CIRC. WATER PUMP 1B HORIZONTAL VIBRATION 1 | AI | 0 | 7 | mm/s
1869 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:AI060608.PNT | 0EDAS:AI060608.PNT | 10PAC20CY003XR01 | CIRC.WATER PUMP 1B VERTICAL VIBRATION | AI | 0 | 7 | mm/s
1869 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.0EDAS:AI060702.PNT | 0EDAS:AI060702.PNT | 10PAC20CY002XR01 | CIRC. WATER PUMP 1B HORIZONTAL VIBRATION 2 | AI | 0 | 7 | mm/s

## UJRBG20 (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS
1137 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.2IDAS:LT120103.PNT | 2IDAS:LT120103.PNT | 20MAG10CL201 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
1145 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.2IDAS:LT120203.PNT | 2IDAS:LT120203.PNT | 20MAG10CL202 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
1153 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-07 | OPC.2IDAS:LT120303.PNT | 2IDAS:LT120303.PNT | 20MAG10CL203 | CONDENSER LEVEL | AI | -680 | 420 | mm |  |  | -260 | 220
539 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:AI113307.PNT | 2HDAS:AI113307.PNT | 20PAH11GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM A SIDE DIFF.PRESS | AI | -1 | 9
540 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:AI113308.PNT | 2HDAS:AI113308.PNT | 20PAH12GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM B SIDE DIFF.PRESS | AI | -1 | 9
533 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:PT113301.PNT | 2HDAS:PT113301.PNT | 20PAH21CP201 | CONDENSER SIDE A CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa
741 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:RT113401.PNT | 2HDAS:RT113401.PNT | 20PAH21CT001 | CONDENSER SIDE A CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | °C
535 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:PT113303.PNT | 2HDAS:PT113303.PNT | 20PAH22CP201 | CONDENSER SIDE B CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa
743 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:RT113403.PNT | 2HDAS:RT113403.PNT | 20PAH22CT001 | CONDENSER SIDE B CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | °C
537 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:ZT113305.PNT | 2HDAS:ZT113305.PNT | 20PAH31AA001XB12 | CONDENSER A SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITIO | AI | 0 | 100 | %
534 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:PT113302.PNT | 2HDAS:PT113302.PNT | 20PAH31CP201 | CONDENSER SIDE A CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa
742 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:RT113402.PNT | 2HDAS:RT113402.PNT | 20PAH31CT001 | CONDENSER SIDE A CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | °C
538 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:ZT113306.PNT | 2HDAS:ZT113306.PNT | 20PAH32AA001XB12 | CONDENSER B SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITIO | AI | 0 | 100 | %
536 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:PT113304.PNT | 2HDAS:PT113304.PNT | 20PAH32CP201 | CONDENSER SIDE B CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa
744 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) | 50-F290S-J0201-13 | OPC.2HDAS:RT113404.PNT | 2HDAS:RT113404.PNT | 20PAH32CT001 | CONDENSER SIDE B CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | °C
744 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #20 (CONDENSING SYSTEM/CONDENSER) |  | OPC.2VALVE:1AD106AIN.PNT_3 | 2VALVE:1AD106AIN.PNT_3 | 20MAG10CP201 | #20 COND VACUUM | AI | 103 | -103 | kPa |  | -80 | -85
607 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053805.PNT | 2EDAS:RT053805.PNT | 20LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 100 | °C
358 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:PT050508.PNT | 2EDAS:PT050508.PNT | 20LCA12CP201 | CONDENSATE PUMP A OUTLET PRESS | AI | 0 | 4 | MPa
368 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:PT050702.PNT | 2EDAS:PT050702.PNT | 20LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa
375 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50- | OPC.2EDAS:ZT050801.PNT | 2EDAS:ZT050801.PNT | 20LCB12AP001XB13 | CONDENSER PUMP A CURRENT | AI | 0 | 100 | %
579 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053404.PNT | 2EDAS:RT053404.PNT | 20LCB12CT001 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
586 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053504.PNT | 2EDAS:RT053504.PNT | 20LCB12CT002 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
580 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053405.PNT | 2EDAS:RT053405.PNT | 20LCB12CT003 | CONDENSATE PUMP A MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
587 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053505.PNT | 2EDAS:RT053505.PNT | 20LCB12CT004 | CONDENSATE PUMP A MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
576 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053401.PNT | 2EDAS:RT053401.PNT | 20LCB12CT005 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
583 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053501.PNT | 2EDAS:RT053501.PNT | 20LCB12CT006 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
577 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053402.PNT | 2EDAS:RT053402.PNT | 20LCB12CT007 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
584 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053502.PNT | 2EDAS:RT053502.PNT | 20LCB12CT008 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
578 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053403.PNT | 2EDAS:RT053403.PNT | 20LCB12CT009 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
585 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053503.PNT | 2EDAS:RT053503.PNT | 20LCB12CT010 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
585 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM |  | OPC.2VMS2:AIN1.PNT | 2VMS2:AIN1.PNT | 20LCB12CY201X | #20 CEP A DRIVE END VIB X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
585 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 2 | MAIN CONDESATE A PUMP SYSTEM |  | OPC.2VMS2:AIN2.PNT | 2VMS2:AIN2.PNT | 20LCB12CY201Y | #20 CEP A DRIVE END VIB Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
366 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:PT050608.PNT | 2EDAS:PT050608.PNT | 20LCA13CP201 | CONDENSATE PUMP B OUTLET PRESS | AI | 0 | 4 | MPa
376 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50- | OPC.2EDAS:ZT050802.PNT | 2EDAS:ZT050802.PNT | 20LCB13AP001XB13 | CONDENSER PUMP B CURRENT | AI | 0 | 100 | %
593 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053604.PNT | 2EDAS:RT053604.PNT | 20LCB13CT001 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
600 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053704.PNT | 2EDAS:RT053704.PNT | 20LCB13CT002 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | °C |  |  |  | 70 | 80
594 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053605.PNT | 2EDAS:RT053605.PNT | 20LCB13CT003 | CONDENSATE PUMP B MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
601 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053705.PNT | 2EDAS:RT053705.PNT | 20LCB13CT004 | CONDENSATE PUMP B MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 70 | 80
590 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053601.PNT | 2EDAS:RT053601.PNT | 20LCB13CT005 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
597 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053701.PNT | 2EDAS:RT053701.PNT | 20LCB13CT006 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
591 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053602.PNT | 2EDAS:RT053602.PNT | 20LCB13CT007 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
598 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053702.PNT | 2EDAS:RT053702.PNT | 20LCB13CT008 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
592 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053603.PNT | 2EDAS:RT053603.PNT | 20LCB13CT009 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
599 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM | 50-F290S-J0201-07 | OPC.2EDAS:RT053703.PNT | 2EDAS:RT053703.PNT | 20LCB13CT010 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | °C |  |  |  | 130 | 140
599 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM |  | OPC.2VMS2:AIN3.PNT | 2VMS2:AIN3.PNT | 20LCB13CY201X | #20 CEP B DRIVE END VIB X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
599 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 3 | MAIN CONDESATE B PUMP SYSTEM |  | OPC.2VMS2:AIN4.PNT | 2VMS2:AIN4.PNT | 20LCB13CY201Y | #20 CEP B DRIVE END VIB Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2
493 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:CT092701.PNT | 2GDAS:CT092701.PNT | 20MAJ21AP001XB13 | VACUUM PUMP A CURRENT | AI | 0 | 100 | %
705 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093501.PNT | 2GDAS:RT093501.PNT | 20MAJ21CT001 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
713 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093601.PNT | 2GDAS:RT093601.PNT | 20MAJ21CT002 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
706 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093502.PNT | 2GDAS:RT093502.PNT | 20MAJ21CT003 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
714 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093602.PNT | 2GDAS:RT093602.PNT | 20MAJ21CT004 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
707 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093503.PNT | 2GDAS:RT093503.PNT | 20MAJ21CT005 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
715 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093603.PNT | 2GDAS:RT093603.PNT | 20MAJ21CT006 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
708 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093504.PNT | 2GDAS:RT093504.PNT | 20MAJ21CT007 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
716 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-15 | OPC.2GDAS:RT093604.PNT | 2GDAS:RT093604.PNT | 20MAJ21CT008 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
655 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 4 | VACUUM PUMP 20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067707.PNT | 2EDAS:RT067707.PNT | 20PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 50 | °C
709 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093505.PNT | 2GDAS:RT093505.PNT | 20MAJ21CT009 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
717 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093605.PNT | 2GDAS:RT093605.PNT | 20MAJ21CT010 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
710 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093506.PNT | 2GDAS:RT093506.PNT | 20MAJ21CT011 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
718 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093606.PNT | 2GDAS:RT093606.PNT | 20MAJ21CT012 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
711 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093507.PNT | 2GDAS:RT093507.PNT | 20MAJ21CT013 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
719 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093607.PNT | 2GDAS:RT093607.PNT | 20MAJ21CT014 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | °C |  | 0 | 0 | 140 | 150
712 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093508.PNT | 2GDAS:RT093508.PNT | 20MAJ21CT015 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
720 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:RT093608.PNT | 2GDAS:RT093608.PNT | 20MAJ21CT016 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 100 | °C |  | 0 | 0 | 80 | 85
494 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 5 | VACUUM PUMP 20B | 50-F290S-J0201-15 | OPC.2GDAS:CT092702.PNT | 2GDAS:CT092702.PNT | 20MAJ22AP001XB13 | VACUUM PUMP B CURRENT | AI | 0 | 100 | %
410 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #20 | 50-F290S-J0201-10 | OPC.2FDAS:CT073103.PNT | 2FDAS:CT073103.PNT | 20LBW20AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN A CURRENT | AI | 0 | 100 | %
411 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #20 | 50-F290S-J0201-10 | OPC.2FDAS:CT073104.PNT | 2FDAS:CT073104.PNT | 20LBW21AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN B CURRENT | AI | 0 | 100 | %
581 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #20 | 50-F290S-J0201-07 | OPC.2EDAS:RT053406.PNT | 2EDAS:RT053406.PNT | 20LCA10CT001 | GLAND STEAM CONDENSER INLET TEMP | RTD | 0 | 100 | °C
582 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #20 | 50-F290S-J0201-07 | OPC.2EDAS:RT053407.PNT | 2EDAS:RT053407.PNT | 20LCA10CT002 | GLAND STEAM CONDENSER OUTLET MAIN PIPE TEMP | RTD | 0 | 100 | °C
462 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-05 | OPC.2FDAS:PT086504.PNT | 2FDAS:PT086504.PNT | 20LBS80CP201 | #8 EXTRACTION STEAM PRESS(LEFT) | AI | 0 | 0.1 | MPa
467 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-05 | OPC.2FDAS:PT086602.PNT | 2FDAS:PT086602.PNT | 20LBS80CP202 | #8 EXTRACTION STEAM PRESS(RIGHT) | AI | 0 | 0.1 | MPa
771 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-05 | OPC.2FDAS:TE087308.PNT | 2FDAS:TE087308.PNT | 20LBS80CT001 | #8 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 150 | °C
775 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-05 | OPC.2FDAS:TE087404.PNT | 2FDAS:TE087404.PNT | 20LBS80CT002 | #8 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 150 | °C
369 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-07 | OPC.2EDAS:PT050703.PNT | 2EDAS:PT050703.PNT | 20LCA10CP201 | #8 LP HEATER INLET PRESS | AI | 0 | 4 | MPa
588 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-07 | OPC.2EDAS:RT053506.PNT | 2EDAS:RT053506.PNT | 20LCA10CT003 | #8 LP HEATER INLET WATER TEMP | RTD | 0 | 100 | °C
1161 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120403.PNT | 2IDAS:LT120403.PNT | 20LCC80CL201 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1168 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120503.PNT | 2IDAS:LT120503.PNT | 20LCC80CL202 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1176 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120603.PNT | 2IDAS:LT120603.PNT | 20LCC80CL203 | #8 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1253 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2LP8LVL:AO122505.OUT | 2LP8LVL:AO122505.OUT | 20LCJ80AA101XB11 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1212 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121305.PNT | 2IDAS:ZT121305.PNT | 20LCJ80AA101XB12 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
606 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2EDAS:RT053804.PNT | 2EDAS:RT053804.PNT | 20LCJ80CT001 | #8 LP HEATER DRAIN WATER TEMP | RTD | 0 | 50 | °C
1254 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2LP8LVL:AO122506.OUT | 2LP8LVL:AO122506.OUT | 20LCJ81AA101XB11 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1213 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 9 | LP FEED WATER HEATER 8 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121306.PNT | 2IDAS:ZT121306.PNT | 20LCJ81AA101XB12 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
461 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-05 | OPC.2FDAS:PT086503.PNT | 2FDAS:PT086503.PNT | 20LBS70CP201 | #7 EXTRACTION STEAM PRESS(LEFT) | AI | 0 | 0.15 | MPa
466 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-05 | OPC.2FDAS:PT086601.PNT | 2FDAS:PT086601.PNT | 20LBS70CP202 | #7 EXTRACTION STEAM PRESS(RIGHT) | AI | 0 | 0.15 | MPa
770 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-05 | OPC.2FDAS:TE087307.PNT | 2FDAS:TE087307.PNT | 20LBS70CT001 | #7 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 200 | °C
774 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-05 | OPC.2FDAS:TE087403.PNT | 2FDAS:TE087403.PNT | 20LBS70CT002 | #7 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 200 | °C
589 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-07 | OPC.2EDAS:RT053507.PNT | 2EDAS:RT053507.PNT | 20LCA20CT001 | #7 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1160 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120402.PNT | 2IDAS:LT120402.PNT | 20LCC70CL201 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1167 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120502.PNT | 2IDAS:LT120502.PNT | 20LCC70CL202 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1175 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120602.PNT | 2IDAS:LT120602.PNT | 20LCC70CL203 | #7 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1251 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2LP7LVL:AO122503.OUT | 2LP7LVL:AO122503.OUT | 20LCJ70AA101XB11 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1210 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121303.PNT | 2IDAS:ZT121303.PNT | 20LCJ70AA101XB12 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
605 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2EDAS:RT053803.PNT | 2EDAS:RT053803.PNT | 20LCJ70CT001 | #7 LP HEATER DRAIN WATER TEMP | RTD | 0 | 100 | °C
1252 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2LP7LVL:AO122504.OUT | 2LP7LVL:AO122504.OUT | 20LCJ71AA101XB11 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1211 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 10 | LP FEED WATER HEATER 7 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121304.PNT | 2IDAS:ZT121304.PNT | 20LCJ71AA101XB12 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
460 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2FDAS:PT086502.PNT | 2FDAS:PT086502.PNT | 20LBS60CP201 | #6 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.4 | MPa
505 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2GDAS:PT104106.PNT | 2GDAS:PT104106.PNT | 20LBS60CP202 | #6 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.4 | MPa
767 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2FDAS:TE087304.PNT | 2FDAS:TE087304.PNT | 20LBS60CT001 | #6 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 250 | °C
768 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2FDAS:TE087305.PNT | 2FDAS:TE087305.PNT | 20LBS60CT002 | #6 EXTRACTION PIPE TOP TEMP | TC | 0 | 250 | °C
769 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2FDAS:TE087306.PNT | 2FDAS:TE087306.PNT | 20LBS60CT003 | #6 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 250 | °C
825 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-05 | OPC.2GDAS:TE107402.PNT | 2GDAS:TE107402.PNT | 20LBS60CT004 | #6 EXTRACTION STEAM TEMP (LP HEATER SIDE) | TC | 0 | 250 | °C
595 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-07 | OPC.2EDAS:RT053606.PNT | 2EDAS:RT053606.PNT | 20LCA30CT001 | #6 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1159 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120401.PNT | 2IDAS:LT120401.PNT | 20LCC60CL201 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1166 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120501.PNT | 2IDAS:LT120501.PNT | 20LCC60CL202 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1174 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120601.PNT | 2IDAS:LT120601.PNT | 20LCC60CL203 | #6 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1249 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2LP6LVL:AO122501.OUT | 2LP6LVL:AO122501.OUT | 20LCJ60AA101XB11 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1208 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121301.PNT | 2IDAS:ZT121301.PNT | 20LCJ60AA101XB12 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
604 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2EDAS:RT053802.PNT | 2EDAS:RT053802.PNT | 20LCJ60CT001 | #6 LP HEATER DRAIN WATER TEMP | RTD | 0 | 110 | °C
1250 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2LP6LVL:AO122502.OUT | 2LP6LVL:AO122502.OUT | 20LCJ61AA101XB11 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1209 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 12 | LP FEED WATER HEATER 6 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121302.PNT | 2IDAS:ZT121302.PNT | 20LCJ61AA101XB12 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
459 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2FDAS:PT086501.PNT | 2FDAS:PT086501.PNT | 20LBS50CP201 | #5 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.6 | MPa
504 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2GDAS:PT104105.PNT | 2GDAS:PT104105.PNT | 20LBS50CP202 | #5 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.6 | MPa
764 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2FDAS:TE087301.PNT | 2FDAS:TE087301.PNT | 20LBS50CT001 | #5 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 300 | °C
765 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2FDAS:TE087302.PNT | 2FDAS:TE087302.PNT | 20LBS50CT002 | #5 EXTRACTION PIPE TOP TEMP | TC | 0 | 300 | °C
766 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2FDAS:TE087303.PNT | 2FDAS:TE087303.PNT | 20LBS50CT003 | #5 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 300 | °C
824 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-05 | OPC.2GDAS:TE107401.PNT | 2GDAS:TE107401.PNT | 20LBS50CT004 | #5 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 300 | °C
596 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-07 | OPC.2EDAS:RT053607.PNT | 2EDAS:RT053607.PNT | 20LCA40CT001 | #5 LP HEATER OUTLET WATER TEMP | RTD | 0 | 150 | °C
1142 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120108.PNT | 2IDAS:LT120108.PNT | 20LCC50CL201 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1150 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120208.PNT | 2IDAS:LT120208.PNT | 20LCC50CL202 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1158 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:LT120308.PNT | 2IDAS:LT120308.PNT | 20LCC50CL203 | #5 LP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -40 | 40
1247 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2LP5LVL:AO122406.OUT | 2LP5LVL:AO122406.OUT | 20LCJ50AA101XB11 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1206 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121206.PNT | 2IDAS:ZT121206.PNT | 20LCJ50AA101XB12 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
603 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2EDAS:RT053801.PNT | 2EDAS:RT053801.PNT | 20LCJ50CT001 | #5 LP HEATER DRAIN WATER TEMP | RTD | 0 | 150 | °C
1248 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2LP5LVL:AO122407.OUT | 2LP5LVL:AO122407.OUT | 20LCJ51AA101XB11 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1207 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 14 | LP FEED WATER HEATER 5 | 50-F290S-J0201-09(2/2) | OPC.2IDAS:ZT121207.PNT | 2IDAS:ZT121207.PNT | 20LCJ51AA101XB12 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
491 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-09(1/2) | OPC.2GDAS:ZT092606.PNT | 2GDAS:ZT092606.PNT | 20LAA40AA501XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | %
495 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50- | OPC.2GDAS:ZT092703.PNT | 2GDAS:ZT092703.PNT | 20LAA40AA502XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 101 | %
496 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50- | OPC.2GDAS:ZT092704.PNT | 2GDAS:ZT092704.PNT | 20LAA40AA503XB12 | DEAERATOR EXHAUST MOTORIZED VALVE 3 POSITION | AI | 0 | 102 | %
1138 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2IDAS:LT120104.PNT | 2IDAS:LT120104.PNT | 20LAA40CL201 | DEAERATOR TANK LEVEL | AI | -1950 | 550 | mm |  |  | -200 | 200
1146 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2IDAS:LT120204.PNT | 2IDAS:LT120204.PNT | 20LAA40CL202 | DEAERATOR TANK LEVEL | AI | -195 | 550 | mm |  |  | -200 | 200
1154 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2IDAS:LT120304.PNT | 2IDAS:LT120304.PNT | 20LAA40CL203 | DEAERATOR TANK LEVEL | AI | -195 | 550 | mm |  |  | -200 | 200
602 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2EDAS:RT053706.PNT | 2EDAS:RT053706.PNT | 20LAA40CT001 | DEAERATOR TANK TEMP | RTD | 0 | 200 | °C
473 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:ZT086701.PNT | 2FDAS:ZT086701.PNT | 20LBS40AA005XB12 | AUXILIARY STEAM HEADER TO DEAERATOR INCHING MOTORIZED VALVE POSITI | AI | 0 | 100 | %
455 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:PT086404.PNT | 2FDAS:PT086404.PNT | 20LBS40CP201 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (TURBINE SIDE) | AI | 0 | 1 | MPa
463 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:PT086505.PNT | 2FDAS:PT086505.PNT | 20LBS40CP202 | #4 EXTRACTION STEAM PIPE 1 PRESS 2 (TURBINE SIDE) | AI | 0 | 1 | MPa
1181 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2IDAS:PT120701.PNT | 2IDAS:PT120701.PNT | 20LBS40CP203 | DEAERATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa
1186 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2IDAS:PT120801.PNT | 2IDAS:PT120801.PNT | 20LBS40CP204 | DEAERATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa
503 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2GDAS:PT104104.PNT | 2GDAS:PT104104.PNT | 20LBS40CP205 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (DEAERATOR SIDE) | AI | 0 | 1 | MPa
761 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087204.PNT | 2FDAS:TE087204.PNT | 20LBS40CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 400 | °C
762 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087205.PNT | 2FDAS:TE087205.PNT | 20LBS40CT002 | #4 EXTRACTION STEAM PIPE 1 TOP TEMP | TC | 0 | 400 | °C
756 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087107.PNT | 2FDAS:TE087107.PNT | 20LBS40CT003 | #4 EXTRACTION STEAM PIPE 1 BOTTOM TEMP | TC | 0 | 400 | °C
822 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2GDAS:TE107306.PNT | 2GDAS:TE107306.PNT | 20LBS40CT004 | #4 EXTRACTION STEAM PIPE 1 TEMP (DEAERATOR SIDE) | TC | 0 | 400 | °C
474 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-05 | OPC.2FDAS:ZT086702.PNT | 2FDAS:ZT086702.PNT | 20LBS43AA001XB12 | OPEN #4 EXTRACTION STEAM PIPE TO DEAERATOR INCHING MOTORIZED VALVE | AI | 0 | 100 | %
373 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2EDAS:ZT050707.PNT | 2EDAS:ZT050707.PNT | 20LCA10AA004XB12 | DEAERATOR LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | %
1224 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2DALVL:AO122103.OUT | 2DALVL:AO122103.OUT | 20LCA10AA101XB11 | DEAERATOR WATER LEVEL CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1172 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120507.PNT | 2IDAS:ZT120507.PNT | 20LCA10AA101XB12 | DEAERATOR WATER LEVEL CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1230 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2DALVL:AO122203.OUT | 2DALVL:AO122203.OUT | 20LCA10AA102XB11 | DEAERATOR WATER LEVEL CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1173 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120508.PNT | 2IDAS:ZT120508.PNT | 20LCA10AA102XB12 | DEAERATOR WATER LEVEL CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
541 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50- | OPC.2GHH:AO092801.OUT | 2GHH:AO092801.OUT | 20LAA40AA501XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
542 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50- | OPC.2GHH:AO092802.OUT | 2GHH:AO092802.OUT | 20LAA40AA502XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
543 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #20 | 50- | OPC.2GHH:AO092803.OUT | 2GHH:AO092803.OUT | 20LAA40AA503XB11 | DEAERATOR EXHAUST MOTORIZED VALVE 3 CONTROL COMMAND | AO | 0 | 100 | %
1182 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2IDAS:FT120702.PNT | 2IDAS:FT120702.PNT | 20LCA40CF201 | CONDENSATE WATER FLOW | AI | 0 | 1000 | T/H
1187 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2IDAS:FT120802.PNT | 2IDAS:FT120802.PNT | 20LCA40CF202 | CONDENSATE WATER FLOW | AI | 0 | 1000 | T/H
372 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2EDAS:ZT050706.PNT | 2EDAS:ZT050706.PNT | 20LCA42AA001XB12 | OPEN CONDENSATE RECIRCULATING CONTROL VALVE BYPASS MOTORIZED VALV | AI | 0 | 100 | %
1228 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2CNREC:AO122107.OUT | 2CNREC:AO122107.OUT | 20LCA42AA101XB11 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1171 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120506.PNT | 2IDAS:ZT120506.PNT | 20LCA42AA101XB12 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE POSITION | AI | 0 | 100 | %
1165 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | 50-F290S-J0201-07 | OPC.2IDAS:FT120407.PNT | 2IDAS:FT120407.PNT | 20LCA42CF201 | CONDENSATE WATER RECIRCULATING FLOW | AI | 0 | 1000 | T/H
1227 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2CNMKUP:AO122106.OUT | 2CNMKUP:AO122106.OUT | 20LCA21AA101XB91 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE CONTROL COMM | AO | 0 | 100 | %
1170 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2IDAS:ZT120505.PNT | 2IDAS:ZT120505.PNT | 20LCA21AA101XB92 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | %
1235 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2CNMKUP:AO122301.OUT | 2CNMKUP:AO122301.OUT | 20LCD10AA101XB11 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1193 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2IDAS:ZT121101.PNT | 2IDAS:ZT121101.PNT | 20LCD10AA101XB12 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1236 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2CNLVL:AO122302.OUT | 2CNLVL:AO122302.OUT | 20LCP10AA101XB11 | CONDENSER WATER LEVEL CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1194 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2IDAS:ZT121102.PNT | 2IDAS:ZT121102.PNT | 20LCP10AA101XB12 | SHUI | AI | 0 | 100 | %
367 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2EDAS:CT050701.PNT | 2EDAS:CT050701.PNT | 20LCP10AP001XB13 | CONDENSATE MAKE-UP WATER PUMP CURRENT | AI | 0 | 100 | %
371 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2EDAS:FT050705.PNT | 2EDAS:FT050705.PNT | 20LCP10CF201 | CONDENSATE MAKE-UP WATER FLOW | AI | 0 | 80 | T/H
1169 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2IDAS:LT120504.PNT | 2IDAS:LT120504.PNT | 20LCP10CL201 | CONDENSATE MAKE-UP TANK LEVEL | AI | 0 | 4500 | mm
370 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2EDAS:PT050704.PNT | 2EDAS:PT050704.PNT | 20LCP10CP201 | CONDENSATE MAKE-UP WATER PUMP OUTLET PRESS | AI | 0 | 2.5 | MPa
374 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2EDAS:ZT050708.PNT | 2EDAS:ZT050708.PNT | 20LCP11AA001XB12 | CONDENSER WATER LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITI | AI | 0 | 100 | %
365 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE UP WATER TANK | 50-F290S-J0201-07 | OPC.2EDAS:CT050607.PNT | 2EDAS:CT050607.PNT | 20LCP20AP001XB13 | BOILER FEEDWATER PUMP CURRENT | AI | 0 | 100 | %
544 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50- | OPC.2GDAS:AO092804.OUT | 2GDAS:AO092804.OUT | 20LCE14AA001XB11 | DRAIN FLASH TANK DESUPERHEATING WATER VALVE CONTROL | AO | 0 | 100 | %
545 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50- | OPC.2GDAS:AO092805.OUT | 2GDAS:AO092805.OUT | 20LCE19AA001XB11 | DRAIN FLASH TANK DESUPERHEATING WATER VALVE CONTROL | AO | 0 | 100 | %
826 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113501.PNT | 2HDAS:TE113501.PNT | 20LCT10CT001 | NO.1 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 560 | °C
827 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113502.PNT | 2HDAS:TE113502.PNT | 20LCT10CT002 | NO.2 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 560 | °C
828 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113503.PNT | 2HDAS:TE113503.PNT | 20LCT10CT003 | NO.3 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 420 | °C
829 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113504.PNT | 2HDAS:TE113504.PNT | 20LCT10CT004 | NO.4 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 550 | °C
830 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113505.PNT | 2HDAS:TE113505.PNT | 20LCT10CT005 | NO.5 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 360 | °C
831 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113506.PNT | 2HDAS:TE113506.PNT | 20LCT10CT006 | NO.6 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 100 | °C
832 | 1 | UJRBG #20 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | 50-F290S-J0201-12 | OPC.2HDAS:TE113507.PNT | 2HDAS:TE113507.PNT | 20LCT10CT007 | NO.7 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 360 | °C
400 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 1 | CIRCULATING-WATER BOOSTER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:PT066701.PNT | 2EDAS:PT066701.PNT | 20PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.25 | MPa
654 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 1 | CIRCULATING-WATER BOOSTER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067706.PNT | 2EDAS:RT067706.PNT | 20PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 50 | °C
390 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 1 | CIRCULATING-WATER BOOSTER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:CT064705.PNT | 2EDAS:CT064705.PNT | 20PCC21AP001XB13 | CIRCULATING-WATER BOOSTER PUMP A CURRENT | AI | 0 | 100 | %
397 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 2 | CIRCULATING-WATER BOOSTER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:CT064805.PNT | 2EDAS:CT064805.PNT | 20PCC22AP001XB13 | CIRCULATING-WATER BOOSTER PUMP B CURRENT | AI | 0 | 100 | %
387 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 20A | 50-F290S-J0201-14 | OPC.2EDAS:ZT064702.PNT | 2EDAS:ZT064702.PNT | 20PCB31AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A SEA WATER SIDE OUTL | AI | 0 | 100 | %
388 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 20A | 50-F290S-J0201-14 | OPC.2EDAS:ZT064703.PNT | 2EDAS:ZT064703.PNT | 20PGA21AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A COOLING WATER INLET | AI | 0 | 100 | %
386 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 20A | 50-F290S-J0201-14 | OPC.2EDAS:PT064701.PNT | 2EDAS:PT064701.PNT | 20PGA21CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET PRESS | AI | 0 | 0.8 | MPa
633 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CLOSED COOLING WATER HEAT EXCHANGER 20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067406.PNT | 2EDAS:RT067406.PNT | 20PGA21CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET TEMP | RTD | 0 | 50 | °C
394 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 20B | 50-F290S-J0201-14 | OPC.2EDAS:ZT064802.PNT | 2EDAS:ZT064802.PNT | 20PCB32AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B SEA WATER SIDE OUTL | AI | 0 | 100 | %
395 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 20B | 50-F290S-J0201-14 | OPC.2EDAS:ZT064803.PNT | 2EDAS:ZT064803.PNT | 20PGA22AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B COOLING WATER INLET | AI | 0 | 100 | %
393 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 20B | 50-F290S-J0201-14 | OPC.2EDAS:PT064801.PNT | 2EDAS:PT064801.PNT | 20PGA22CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET PRESS | AI | 0 | 0.8 | MPa
640 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CLOSED COOLING WATER HEAT EXCHANGER 20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067506.PNT | 2EDAS:RT067506.PNT | 20PGA22CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET TEMP | RTD | 0 | 50 | °C
405 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:ZT066706.PNT | 2EDAS:ZT066706.PNT | 20PGA11AA001XB12 | CLOSED CIRCULATING-WATER PUMP A OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | %
391 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:CT064706.PNT | 2EDAS:CT064706.PNT | 20PGA11AP001XB13 | CLOSED CIRCULATING-WATER PUMP A CURRENT | AI | 0 | 100 | %
631 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067404.PNT | 2EDAS:RT067404.PNT | 20PGA11CT001 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
638 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067504.PNT | 2EDAS:RT067504.PNT | 20PGA11CT002 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
632 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067405.PNT | 2EDAS:RT067405.PNT | 20PGA11CT003 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
639 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067505.PNT | 2EDAS:RT067505.PNT | 20PGA11CT004 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
628 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067401.PNT | 2EDAS:RT067401.PNT | 20PGA11CT005 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
635 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067501.PNT | 2EDAS:RT067501.PNT | 20PGA11CT006 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
629 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067402.PNT | 2EDAS:RT067402.PNT | 20PGA11CT007 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
636 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067502.PNT | 2EDAS:RT067502.PNT | 20PGA11CT008 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
630 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067403.PNT | 2EDAS:RT067403.PNT | 20PGA11CT009 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
637 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067503.PNT | 2EDAS:RT067503.PNT | 20PGA11CT010 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
401 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CLOSED CIRCULATING-WATER PUMP #20A | 50-F290S-J0201-14 | OPC.2EDAS:PT066702.PNT | 2EDAS:PT066702.PNT | 20PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 1.6 | MPa
398 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:CT064806.PNT | 2EDAS:CT064806.PNT | 20PGA12AP001XB13 | CLOSED CIRCULATING-WATER PUMP B CURRENT | AI | 0 | 100 | %
645 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067604.PNT | 2EDAS:RT067604.PNT | 20PGA12CT001 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
652 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067704.PNT | 2EDAS:RT067704.PNT | 20PGA12CT002 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 400 | °C |  | 0 | 0 | 80 | 85
646 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067605.PNT | 2EDAS:RT067605.PNT | 20PGA12CT003 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
653 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067705.PNT | 2EDAS:RT067705.PNT | 20PGA12CT004 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 400 | °C |  | 0 | 0 | 90 | 95
642 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067601.PNT | 2EDAS:RT067601.PNT | 20PGA12CT005 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
649 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067701.PNT | 2EDAS:RT067701.PNT | 20PGA12CT006 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
643 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067602.PNT | 2EDAS:RT067602.PNT | 20PGA12CT007 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
650 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067702.PNT | 2EDAS:RT067702.PNT | 20PGA12CT008 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
644 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067603.PNT | 2EDAS:RT067603.PNT | 20PGA12CT009 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
651 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CLOSED CIRCULATING-WATER PUMP #20B | 50-F290S-J0201-14 | OPC.2EDAS:RT067703.PNT | 2EDAS:RT067703.PNT | 20PGA12CT010 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE N | RTD | 0 | 400 | °C |  | 0 | 0 | 125 | 130
389 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:ZT064704.PNT | 2EDAS:ZT064704.PNT | 20PGA31AA002XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | %
403 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:PT066704.PNT | 2EDAS:PT066704.PNT | 20PGA31CP201 | BOOSTER PUMP FOR T-BFP DRIVEN BOILER FEED WATER PUMP BEARING COOL | AI | 0 | 0.8 | MPa
647 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067606.PNT | 2EDAS:RT067606.PNT | 20PGA31CT001 | TURBINE HOUSE COOLING WATER INLET TEMP | RTD | 0 | 50 | °C
634 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067407.PNT | 2EDAS:RT067407.PNT | 20PGA31CT002 | TURBINE HOUSER COOLING RETURN WATER TEMP 1 | RTD | 0 | 50 | °C
641 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067507.PNT | 2EDAS:RT067507.PNT | 20PGA31CT004 | TURBINE HOUSER COOLING RETURN WATER TEMP 2 | RTD | 0 | 50 | °C
396 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:ZT064804.PNT | 2EDAS:ZT064804.PNT | 20PGA33AA001XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | %
402 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:PT066703.PNT | 2EDAS:PT066703.PNT | 20PGA40CP201 | FUEL OIL COOLER INLET PRESS | AI | 0 | 0.8 | MPa
656 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067801.PNT | 2EDAS:RT067801.PNT | 20PGA40CT001 | BOILER HOUSE COOLING WATER MAIN PIPE INLET TEMP | RTD | 0 | 50 | °C
392 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:ZT064707.PNT | 2EDAS:ZT064707.PNT | 20PGA50AA001XB12 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE MOTORIZED VALVE POSIT | AI | 0 | 100 | %
657 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067802.PNT | 2EDAS:RT067802.PNT | 20PGA50CT001 | BOILER HOUSE COOLING RENTURN WATER TEMP | RTD | 0 | 50 | °C
658 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | 50-F290S-J0201-14 | OPC.2EDAS:RT067803.PNT | 2EDAS:RT067803.PNT | 20PGA50CT002 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE TEMP | RTD | 0 | 50 | °C
1234 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | 50-F290S-J0201-07 | OPC.2CWEXTNK:AO122207.OUT | 2CWEXTNK:AO122207.OUT | 20LCE18AA101XB11 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER | AO | 0 | 100 | %
1180 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120607.PNT | 2IDAS:ZT120607.PNT | 20LCE18AA101XB12 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER | AI | 0 | 100 | %
404 | 1 | UJRBG #20 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | 50-F290S-J0201-14 | OPC.2EDAS:LT066705.PNT | 2EDAS:LT066705.PNT | 20PGA10CL201 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK LEVEL | AI | 0 | 2.5 | m
353 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50-F290S-J0201-08 | OPC.2EDAS:CT050503.PNT | 2EDAS:CT050503.PNT | 20LAC11AP001XB13 | BOOSTER PUMP FOR T-BFP A CURRENT | AI | 0 | 100 | %
556 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50-F290S-K0301-05 | OPC.2EDAS:RT053101.PNT | 2EDAS:RT053101.PNT | 20LAC11CT001 | BOOSTER PUMP FOR T-BFP A DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
557 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50-F290S-K0301-05 | OPC.2EDAS:RT053102.PNT | 2EDAS:RT053102.PNT | 20LAC11CT002 | BOOSTER PUMP FOR T-BFP A FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
721 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093701.PNT | 2GDAS:RT093701.PNT | 20LAC11CT013 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 1 | RTD | 0 | 100 | °C
722 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093702.PNT | 2GDAS:RT093702.PNT | 20LAC11CT014 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 2 | RTD | 0 | 100 | °C
723 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093703.PNT | 2GDAS:RT093703.PNT | 20LAC11CT015 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 3 | RTD | 0 | 100 | °C
724 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093704.PNT | 2GDAS:RT093704.PNT | 20LAC11CT016 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 4 | RTD | 0 | 100 | °C
725 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093705.PNT | 2GDAS:RT093705.PNT | 20LAC11CT017 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 5 | RTD | 0 | 100 | °C
726 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093706.PNT | 2GDAS:RT093706.PNT | 20LAC11CT018 | MOTOR OF BOOSTER PUMP FOR T-BFP A STATOR WINDING TEMP 6 | RTD | 0 | 100 | °C
727 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093707.PNT | 2GDAS:RT093707.PNT | 20LAC11CT019 | MOTOR OF BOOSTER PUMP FOR T-BFP A BEARING TEMP 1 | RTD | 0 | 100 | °C
728 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #20A - BOOSTER PUMP | 50- | OPC.2GDAS:RT093708.PNT | 2GDAS:RT093708.PNT | 20LAC11CT020 | MOTOR OF BOOSTER PUMP FOR T-BFP A BEARING TEMP 2 | RTD | 0 | 100 | °C
1223 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-08 | OPC.2TFPAREC:AO122101.OUT | 2TFPAREC:AO122101.OUT | 20LAB11AA101XB11 | T-BFP A MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1184 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-08 | OPC.2IDAS:ZT120704.PNT | 2IDAS:ZT120704.PNT | 20LAB11AA101XB12 | T-BFP A MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1183 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-08 | OPC.2IDAS:FT120703.PNT | 2IDAS:FT120703.PNT | 20LAB11CF201 | T-BFP A INLET WATER FLOW | AI | 0 | 1000
351 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-08 | OPC.2EDAS:PT050501.PNT | 2EDAS:PT050501.PNT | 20LAB11CP201 | T-BFP A INLET WATER PRESS | AI | 0 | 4 | MPa
352 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-08 | OPC.2EDAS:PT050502.PNT | 2EDAS:PT050502.PNT | 20LAB11CP202 | T-BFP A OUTLET WATER PRESS | AI | 0 | 25 | MPa
558 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053103.PNT | 2EDAS:RT053103.PNT | 20LAC11CT003 | T-BFP A INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
559 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053104.PNT | 2EDAS:RT053104.PNT | 20LAC11CT004 | T-BFP A OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
560 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053105.PNT | 2EDAS:RT053105.PNT | 20LAC11CT005 | T-BFP A THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
561 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053106.PNT | 2EDAS:RT053106.PNT | 20LAC11CT006 | T-BFP A THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
563 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053201.PNT | 2EDAS:RT053201.PNT | 20LAC11CT007 | T-BFP A INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
564 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053202.PNT | 2EDAS:RT053202.PNT | 20LAC11CT008 | T-BFP A OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
565 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053203.PNT | 2EDAS:RT053203.PNT | 20LAC11CT009 | T-BFP A WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
566 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053204.PNT | 2EDAS:RT053204.PNT | 20LAC11CT010 | T-BFP A WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
567 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053205.PNT | 2EDAS:RT053205.PNT | 20LAC11CT011 | T-BFP A WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
568 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-K0301-05 | OPC.2EDAS:RT053206.PNT | 2EDAS:RT053206.PNT | 20LAC11CT012 | T-BFP A WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
485 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-04 | OPC.2FDAS:FT086806.PNT | 2FDAS:FT086806.PNT | 20LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | Mpa
779 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-04 | OPC.2FDAS:TE087503.PNT | 2FDAS:TE087503.PNT | 20LBR11CT001 | BFP TURBINE A INLET STEAM TEMP | TC | 0 | 400 | °C
477 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-04 | OPC.2FDAS:ZT086705.PNT | 2FDAS:ZT086705.PNT | 20LBR11GC001AI01 | BFP TURBINE A INLET STEAM SWITCHING VALVE POSITION INDICATION | AI
546 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50- | OPC.2GDAS:AO092806.OUT | 2GDAS:AO092806.OUT | 20LBR11GC001AO01 | CONTROL BFP TURBINE A INLET STEAM SWITCHING VALVE | AO | 0 | 100 | %
468 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:FT086603.PNT | 2FDAS:FT086603.PNT | 20LBR21CF201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30
457 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:PT086406.PNT | 2FDAS:PT086406.PNT | 20LBR21CP201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa
772 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:TE087401.PNT | 2FDAS:TE087401.PNT | 20LBR21CT001 | BFP TURBINE A INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 400 | °C
458 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:PT086407.PNT | 2FDAS:PT086407.PNT | 20LBR31CP201 | BFP TURBINE A EXHAUST STEAM PRESS | AI | -0.1 | 0.15 | MPa
562 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2EDAS:RT053107.PNT | 2EDAS:RT053107.PNT | 20LBR31CT001 | BFP TURBINE A EXHAUST STEAM TEMP 1 | RTD | 0 | 100 | °C
569 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2EDAS:RT053207.PNT | 2EDAS:RT053207.PNT | 20LBR31CT002 | BFP TURBINE A EXHAUST STEAM TEMP 2 | RTD | 0 | 100 | °C
575 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2EDAS:RT053307.PNT | 2EDAS:RT053307.PNT | 20LBR31CT003 | BFP TURBINE A EXHAUST STEAM TEMP 3 | RTD | 0 | 100 | °C
456 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:PT086405.PNT | 2FDAS:PT086405.PNT | 20LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa
763 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:TE087206.PNT | 2FDAS:TE087206.PNT | 20LBS41CT001 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 400 | °C
757 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2FDAS:TE087108.PNT | 2FDAS:TE087108.PNT | 20LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 400 | °C
823 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-05 | OPC.2GDAS:TE107307.PNT | 2GDAS:TE107307.PNT | 20LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 TEMP (TURBINE SIDE) | TC | 0 | 400 | °C
497 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50- | OPC.2GDAS:CT092705.PNT | 2GDAS:CT092705.PNT | 20MAV50AP103XB13 | BFP TURBINE A LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURREN | AI | 0 | 103 | %
354 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:LT050504.PNT | 2EDAS:LT050504.PNT | 20MAV50CL201 | BFP TURBINE A LUBE-OIL TANK LEVEL | AI | 0 | 750 | mm
570 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:RT053301.PNT | 2EDAS:RT053301.PNT | 20MAV50CT001 | BFP TURBINE A LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | °C
571 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:RT053302.PNT | 2EDAS:RT053302.PNT | 20MAV50CT002 | BFP TURBINE A LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | °C
572 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:RT053303.PNT | 2EDAS:RT053303.PNT | 20MAV50CT003 | BFP TURBINE A LUBE-OIL TANK TEMP. | RTD | 0 | 100 | °C
573 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:RT053304.PNT | 2EDAS:RT053304.PNT | 20MAV50CT004 | BFP TURBINE A FRONT BEARING BOX RETURN OIL TEMP | RTD | 0 | 100 | °C
574 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2EDAS:RT053305.PNT | 2EDAS:RT053305.PNT | 20MAV50CT005 | BFP TURBINE A #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | °C
1190 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0608-01 | OPC.2IDAS:AI120805.PNT | 2IDAS:AI120805.PNT | 20MEHADCS01 | BFP TURBINE A SPEED SET POINT SIGNAL | AI | 0 | 10000 | rpm |  |  | 2840 | 5945
356 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050506.PNT | 2EDAS:AI050506.PNT | 20MTSIADCS01 | BFP TURBINE A SPEED (4~20mA) | AI | 0 | 10000 | rpm
359 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050601.PNT | 2EDAS:AI050601.PNT | 20MTSIADCS03 | BFP TURBINE A NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
360 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050602.PNT | 2EDAS:AI050602.PNT | 20MTSIADCS04 | BFP TURBINE A NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
361 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050603.PNT | 2EDAS:AI050603.PNT | 20MTSIADCS05 | BFP TURBINE A NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
362 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050604.PNT | 2EDAS:AI050604.PNT | 20MTSIADCS06 | BFP TURBINE A NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
363 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050605.PNT | 2EDAS:AI050605.PNT | 20MTSIADCS07 | BFP TURBINE A NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
364 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050606.PNT | 2EDAS:AI050606.PNT | 20MTSIADCS08 | BFP TURBINE A NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
355 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI050505.PNT | 2EDAS:AI050505.PNT | 20MTSIADCS09 | BFP TURBINE A NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
383 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI064505.PNT | 2EDAS:AI064505.PNT | 20MTSIADCS10 | BFP TURBINE A AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
384 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI064506.PNT | 2EDAS:AI064506.PNT | 20MTSIADCS11 | BFP TURBINE A AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
385 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F289S-K0302-05 | OPC.2EDAS:AI064507.PNT | 2EDAS:AI064507.PNT | 20MTSIADCS12 | BFP TURBINE A ECCENTRICTIY (4~20mA) | AI | 0 | 100 | %
399 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-14 | OPC.2EDAS:ZT064807.PNT | 2EDAS:ZT064807.PNT | 20PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | %
659 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-14 | OPC.2EDAS:RT067804.PNT | 2EDAS:RT067804.PNT | 20PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
803 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107101.PNT | 2GDAS:TE107101.PNT | 20XAC11CT001 | BFP TURBINE A POSITION THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
804 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107102.PNT | 2GDAS:TE107102.PNT | 20XAC11CT002 | BFP TURBINE A POSITION THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
805 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107103.PNT | 2GDAS:TE107103.PNT | 20XAC11CT003 | BFP TURBINE A WORK THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
806 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107104.PNT | 2GDAS:TE107104.PNT | 20XAC11CT004 | BFP TURBINE A WORK THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
807 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107105.PNT | 2GDAS:TE107105.PNT | 20XAC11CT005 | BFP TURBINE A SUPPORT PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
808 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107106.PNT | 2GDAS:TE107106.PNT | 20XAC11CT006 | BFP TURBINE A SUPPORT PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
809 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107107.PNT | 2GDAS:TE107107.PNT | 20XAC11CT007 | BFP TURBINE A #2 BEARING PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
810 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:TE107201.PNT | 2GDAS:TE107201.PNT | 20XAC11CT008 | BFP TURBINE A #2 BEARING PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
737 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:RT104501.PNT | 2GDAS:RT104501.PNT | 20XAC11CT009 | BFP TURBINE A SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | °C |  | 0 | 0 | 65 | 75
738 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50-F290S-J0201-20 | OPC.2GDAS:RT104502.PNT | 2GDAS:RT104502.PNT | 20XAC11CT010 | BFP TURBINE A THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
406 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | 50- | OPC.2FDAS:CT072801.PNT | 2FDAS:CT072801.PNT | 210MAV50GC001AI01 | BFP TURBINE A TURNING GEAR MOTOR CURRENT | AI | 0 | 50 | A
381 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50-F290S-J0201-08 | OPC.2EDAS:CT064503.PNT | 2EDAS:CT064503.PNT | 20LAC12AP001XB13 | BOOSTER PUMP FOR T-BFP B CURRENT | AI | 0 | 100 | %
608 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50-F290S-K0301-06 | OPC.2EDAS:RT067101.PNT | 2EDAS:RT067101.PNT | 20LAC12CT001 | BOOSTER PUMP FOR T-BFP B DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
609 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50-F290S-K0301-06 | OPC.2EDAS:RT067102.PNT | 2EDAS:RT067102.PNT | 20LAC12CT002 | BOOSTER PUMP FOR T-BFP B FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
729 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093801.PNT | 2GDAS:RT093801.PNT | 20LAC12CT013 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 1 | RTD | 0 | 100 | °C
730 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093802.PNT | 2GDAS:RT093802.PNT | 20LAC12CT014 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 2 | RTD | 0 | 100 | °C
731 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093803.PNT | 2GDAS:RT093803.PNT | 20LAC12CT015 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 3 | RTD | 0 | 100 | °C
732 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093804.PNT | 2GDAS:RT093804.PNT | 20LAC12CT016 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 4 | RTD | 0 | 100 | °C
733 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093805.PNT | 2GDAS:RT093805.PNT | 20LAC12CT017 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 5 | RTD | 0 | 100 | °C
734 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093806.PNT | 2GDAS:RT093806.PNT | 20LAC12CT018 | MOTOR OF BOOSTER PUMP FOR T-BFP B STATOR WINDING TEMP 6 | RTD | 0 | 100 | °C
735 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093807.PNT | 2GDAS:RT093807.PNT | 20LAC12CT019 | MOTOR OF BOOSTER PUMP FOR T-BFP B BEARING TEMP 1 | RTD | 0 | 100 | °C
736 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #20B - BOOSTER PUMP | 50- | OPC.2GDAS:RT093808.PNT | 2GDAS:RT093808.PNT | 20LAC12CT020 | MOTOR OF BOOSTER PUMP FOR T-BFP B BEARING TEMP 2 | RTD | 0 | 100 | °C
1229 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-08 | OPC.2TFPBREC:AO122201.OUT | 2TFPBREC:AO122201.OUT | 20LAB12AA101XB11 | T-BFP B MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1189 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-08 | OPC.2IDAS:ZT120804.PNT | 2IDAS:ZT120804.PNT | 20LAB12AA101XB12 | T-BFP B MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1188 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-08 | OPC.2IDAS:FT120803.PNT | 2IDAS:FT120803.PNT | 20LAB12CF201 | T-BFP B INLET WATER FLOW | AI | 0 | 1000
379 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-08 | OPC.2EDAS:PT064501.PNT | 2EDAS:PT064501.PNT | 20LAB12CP201 | T-BFP B INLET WATER PRESS | AI | 0 | 4 | MPa
380 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-08 | OPC.2EDAS:PT064502.PNT | 2EDAS:PT064502.PNT | 20LAB12CP202 | T-BFP B OUTLET WATER PRESS | AI | 0 | 25 | MPa
610 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067103.PNT | 2EDAS:RT067103.PNT | 20LAC12CT003 | T-BFP B INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
611 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067104.PNT | 2EDAS:RT067104.PNT | 20LAC12CT004 | T-BFP B OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
612 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067105.PNT | 2EDAS:RT067105.PNT | 20LAC12CT005 | T-BFP B THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
613 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067106.PNT | 2EDAS:RT067106.PNT | 20LAC12CT006 | T-BFP B THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
615 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067201.PNT | 2EDAS:RT067201.PNT | 20LAC12CT007 | T-BFP B INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
616 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067202.PNT | 2EDAS:RT067202.PNT | 20LAC12CT008 | T-BFP B OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
617 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067203.PNT | 2EDAS:RT067203.PNT | 20LAC12CT009 | T-BFP B WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
618 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067204.PNT | 2EDAS:RT067204.PNT | 20LAC12CT010 | T-BFP B WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
619 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067205.PNT | 2EDAS:RT067205.PNT | 20LAC12CT011 | T-BFP B WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | °C |  |  | 25
620 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0301-06 | OPC.2EDAS:RT067206.PNT | 2EDAS:RT067206.PNT | 20LAC12CT012 | T-BFP B WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | °C |  |  | 25
786 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-04 | OPC.2FDAS:TE087603.PNT | 2FDAS:TE087603.PNT | 20LBR12CT001 | BFP TURBINE B INLET STEAM TEMP | TC | 0 | 400 | °C
484 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-04 | OPC.2FDAS:ZT086805.PNT | 2FDAS:ZT086805.PNT | 20LBR12GC001AI01 | BFP TURBINE B INLET STEAM SWITCHING VALVE POSITION INDICATION | AI | 0 | 20 | MPa
547 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50- | OPC.2GDAS:AO092807.OUT | 2GDAS:AO092807.OUT | 20LBR12GC001AO01 | CONTROL BFP TURBINE B INLET STEAM SWITCHING VALVE | AO | 0 | 100 | %
469 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2FDAS:FT086604.PNT | 2FDAS:FT086604.PNT | 20LBR22CF201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30
464 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2FDAS:PT086506.PNT | 2FDAS:PT086506.PNT | 20LBR22CP201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa
773 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2FDAS:TE087402.PNT | 2FDAS:TE087402.PNT | 20LBR22CT001 | BFP TURBINE B INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 400 | °C
465 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2FDAS:PT086507.PNT | 2FDAS:PT086507.PNT | 20LBR32CP201 | BFP TURBINE B EXHAUST STEAM PRESS | AI | -0.1 | 0.15 | MPa
614 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2EDAS:RT067107.PNT | 2EDAS:RT067107.PNT | 20LBR32CT001 | BFP TURBINE B EXHAUST STEAM TEMP 1 | RTD | 0 | 100 | °C
621 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2EDAS:RT067207.PNT | 2EDAS:RT067207.PNT | 20LBR32CT002 | BFP TURBINE B EXHAUST STEAM TEMP 2 | RTD | 0 | 100 | °C
627 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-05 | OPC.2EDAS:RT067307.PNT | 2EDAS:RT067307.PNT | 20LBR32CT003 | BFP TURBINE B EXHAUST STEAM TEMP 3 | RTD | 0 | 100 | °C
498 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50- | OPC.2GDAS:CT092706.PNT | 2GDAS:CT092706.PNT | 20MAV60AP103XB13 | BFP TURBINE B LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURREN | AI | 0 | 104 | %
382 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:LT064504.PNT | 2EDAS:LT064504.PNT | 20MAV60CL201 | BFP TURBINE B LUBE-OIL TANK LEVEL | AI | 0 | 750 | mm |  | 145 | 272 | 475 | 750
622 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:RT067301.PNT | 2EDAS:RT067301.PNT | 20MAV60CT001 | BFP TURBINE B LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | °C
623 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:RT067302.PNT | 2EDAS:RT067302.PNT | 20MAV60CT002 | BFP TURBINE B LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | °C
624 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:RT067303.PNT | 2EDAS:RT067303.PNT | 20MAV60CT003 | BFP TURBINE B LUBE-OIL TANK TEMP. | RTD | 0 | 100 | °C
625 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:RT067304.PNT | 2EDAS:RT067304.PNT | 20MAV60CT004 | BFP TURBINE B FRONT BEARING BOX RETURN OIL TEMP | RTD | 0 | 100 | °C
626 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2EDAS:RT067305.PNT | 2EDAS:RT067305.PNT | 20MAV60CT005 | BFP TURBINE B #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | °C
1191 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F289S-K0608-01 | OPC.2IDAS:AI120806.PNT | 2IDAS:AI120806.PNT | 20MEHBDCS01 | BFP TURBINE B SPEED SET POINT SIGNAL | AI | 0 | 10000 | rpm |  |  | 2840 | 5945
506 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104107.PNT | 2GDAS:AI104107.PNT | 20MTSIBDCS01 | BFP TURBINE B SPEED (4~20mA) | AI | 0 | 10000 | rpm
507 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104201.PNT | 2GDAS:AI104201.PNT | 20MTSIBDCS02 | BFP TURBINE B NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
508 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104202.PNT | 2GDAS:AI104202.PNT | 20MTSIBDCS03 | BFP TURBINE B NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
509 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104203.PNT | 2GDAS:AI104203.PNT | 20MTSIBDCS04 | BFP TURBINE B NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
510 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104204.PNT | 2GDAS:AI104204.PNT | 20MTSIBDCS05 | BFP TURBINE B NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
511 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104205.PNT | 2GDAS:AI104205.PNT | 20MTSIBDCS06 | BFP TURBINE B NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
512 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104206.PNT | 2GDAS:AI104206.PNT | 20MTSIBDCS07 | BFP TURBINE B NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
513 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104207.PNT | 2GDAS:AI104207.PNT | 20MTSIBDCS08 | BFP TURBINE B NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
514 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104301.PNT | 2GDAS:AI104301.PNT | 20MTSIBDCS09 | BFP TURBINE B NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | µm |  | 0 | 0 | 80 | 125
515 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104302.PNT | 2GDAS:AI104302.PNT | 20MTSIBDCS10 | BFP TURBINE B AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
516 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104303.PNT | 2GDAS:AI104303.PNT | 20MTSIBDCS11 | BFP TURBINE B AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm |  | -0.6 | -0.5 | 0.3 | 0.4
517 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-K0604-07 | OPC.2GDAS:AI104304.PNT | 2GDAS:AI104304.PNT | 20MTSIBDCS12 | BFP TURBINE B ECCENTRICTIY (4~20mA) | AI | 0 | 100 | %
811 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107202.PNT | 2GDAS:TE107202.PNT | 20XAC12CT001 | BFP TURBINE B POSITION THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
812 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107203.PNT | 2GDAS:TE107203.PNT | 20XAC12CT002 | BFP TURBINE B POSITION THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
813 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107204.PNT | 2GDAS:TE107204.PNT | 20XAC12CT003 | BFP TURBINE B WORK THRUST PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
814 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107205.PNT | 2GDAS:TE107205.PNT | 20XAC12CT004 | BFP TURBINE B WORK THRUST PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
815 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107206.PNT | 2GDAS:TE107206.PNT | 20XAC12CT005 | BFP TURBINE B SUPPORT PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
816 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107207.PNT | 2GDAS:TE107207.PNT | 20XAC12CT006 | BFP TURBINE B SUPPORT PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
817 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107301.PNT | 2GDAS:TE107301.PNT | 20XAC12CT007 | BFP TURBINE B #2 BEARING PAD TEMP 1 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
818 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:TE107302.PNT | 2GDAS:TE107302.PNT | 20XAC12CT008 | BFP TURBINE B #2 BEARING PAD TEMP 2 | TC | 0 | 400 | °C |  | 0 | 0 | 100 | 110
739 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:RT104503.PNT | 2GDAS:RT104503.PNT | 20XAC12CT009 | BFP TURBINE B SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
740 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50-F290S-J0201-20 | OPC.2GDAS:RT104504.PNT | 2GDAS:RT104504.PNT | 20XAC12CT010 | BFP TURBINE B THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 400 | °C
407 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #20B | 50- | OPC.2FDAS:CT072802.PNT | 2FDAS:CT072802.PNT | 210MAV60GC001AI01 | BFP TURBINE B TURNING GEAR MOTOR CURRENT | AI | 0 | 50 | A
1237 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2BFPREC:AO122303.OUT | 2BFPREC:AO122303.OUT | 20LAH10AA101XB11 | M-BFP MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | %
1196 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2IDAS:ZT121104.PNT | 2IDAS:ZT121104.PNT | 20LAH10AA101XB12 | M-BFP MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | %
1195 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2IDAS:FT121103.PNT | 2IDAS:FT121103.PNT | 20LAH10CF201 | M-BFP INLET WATER FLOW | AI | 0 | 400 |  |  |  | 0 | 367.2158
486 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2GDAS:PT092601.PNT | 2GDAS:PT092601.PNT | 20LAH10CP201 | M-BFP INLET PRESS | AI | 0 | 2.5 | MPa
487 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2GDAS:PT092602.PNT | 2GDAS:PT092602.PNT | 20LAH10CP202 | M-BFP OUTLET WATER PRESS | AI | 0 | 25 | MPa
802 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092504.PNT | 2GDAS:TE092504.PNT | 20LAH10CT001 | M-BFP OUTLET TEMPERATURE | TC | 0 | 200 | °C
1238 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2FWCNTL:AO122304.OUT | 2FWCNTL:AO122304.OUT | 20LAJ10AA101XB11 | M-BFP HYDRAULIC CUOPLE ACTUATOR CONTROL COMMAND | AO | 0 | 100 | %
1197 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2IDAS:ZT121105.PNT | 2IDAS:ZT121105.PNT | 20LAJ10AA101XB12 | M-BFP HYDRAULIC CUOPLE ACTUATOR POSITION | AI | 0 | 100 | %
490 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-08 | OPC.2GDAS:CT092605.PNT | 2GDAS:CT092605.PNT | 20LAJ10AP001XB13 | M-BFP GROUP CURRENT | AI | 0 | 100 | %
492 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:AI092607.PNT | 2GDAS:AI092607.PNT | 20LAJ10CS201 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min
687 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093205.PNT | 2GDAS:RT093205.PNT | 20LAJ10CT001 | BOOSTER PUMP FOR M-BFP FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
688 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093206.PNT | 2GDAS:RT093206.PNT | 20LAJ10CT002 | BOOSTER PUMP FOR M-BFP DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | °C |  |  |  | 90 | 100
696 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093306.PNT | 2GDAS:RT093306.PNT | 20LAJ10CT003 | M-BFP INLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
703 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093406.PNT | 2GDAS:RT093406.PNT | 20LAJ10CT004 | M-BFP OUTET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
697 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093307.PNT | 2GDAS:RT093307.PNT | 20LAJ10CT005 | M-BFP THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
704 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093407.PNT | 2GDAS:RT093407.PNT | 20LAJ10CT006 | M-BFP THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | °C |  |  |  | 90 | 100
689 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093207.PNT | 2GDAS:RT093207.PNT | 20LAJ10CT007 | M-BFP INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
690 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093208.PNT | 2GDAS:RT093208.PNT | 20LAJ10CT008 | M-BFP OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | °C |  |  |  | 80 | 90
691 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093301.PNT | 2GDAS:RT093301.PNT | 20LAJ10CT009 | M-BFP HYDRAULIC COUPLER B1 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
692 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093302.PNT | 2GDAS:RT093302.PNT | 20LAJ10CT010 | M-BFP HYDRAULIC COUPLER B2 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
693 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093303.PNT | 2GDAS:RT093303.PNT | 20LAJ10CT011 | M-BFP HYDRAULIC COUPLER B3 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
694 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093304.PNT | 2GDAS:RT093304.PNT | 20LAJ10CT012 | M-BFP HYDRAULIC COUPLER B4 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
695 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093305.PNT | 2GDAS:RT093305.PNT | 20LAJ10CT013 | M-BFP HYDRAULIC COUPLER B5 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
698 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093401.PNT | 2GDAS:RT093401.PNT | 20LAJ10CT014 | M-BFP HYDRAULIC COUPLER B6 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
699 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093402.PNT | 2GDAS:RT093402.PNT | 20LAJ10CT015 | M-BFP HYDRAULIC COUPLER B7 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
700 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093403.PNT | 2GDAS:RT093403.PNT | 20LAJ10CT016 | M-BFP HYDRAULIC COUPLER B8 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
701 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093404.PNT | 2GDAS:RT093404.PNT | 20LAJ10CT017 | M-BFP HYDRAULIC COUPLER B9 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
702 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093405.PNT | 2GDAS:RT093405.PNT | 20LAJ10CT018 | M-BFP HYDRAULIC COUPLER B10 RADIAL BEARING TEMP | RTD | -50 | 180 | °C |  |  |  | 90 | 95
679 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093104.PNT | 2GDAS:RT093104.PNT | 20LAJ10CT019 | M-BFP LUBE-OIL COOLER OUTLET TEMP | RTD | -50 | 180 | °C |  |  |  | 55 | 60
680 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093105.PNT | 2GDAS:RT093105.PNT | 20LAJ10CT020 | M-BFP WORKING OIL COOLER INLET TEMP | RTD | -50 | 180 | °C |  |  |  | 110 | 130
681 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093106.PNT | 2GDAS:RT093106.PNT | 20LAJ10CT021 | M-BFP WORKING OIL COOLER OUTLET TEMP | RTD | -50 | 180 | °C |  |  | 35 | 75 | 85
686 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093204.PNT | 2GDAS:RT093204.PNT | 20LAJ10CT022 | M-BFP HYDRAULIC COUPLER MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | °C |  |  |  | 80 | 90
682 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093107.PNT | 2GDAS:RT093107.PNT | 20LAJ10CT023 | BOOSTER PUMP FOR M-BFP MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | °C |  |  |  | 80 | 90
676 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093101.PNT | 2GDAS:RT093101.PNT | 20LAJ10CT024 | M-BFP MOTOR STATOR WINDING TEMP 1 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
677 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093102.PNT | 2GDAS:RT093102.PNT | 20LAJ10CT025 | M-BFP MOTOR STATOR WINDING TEMP 2 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
678 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093103.PNT | 2GDAS:RT093103.PNT | 20LAJ10CT026 | M-BFP MOTOR STATOR WINDING TEMP 3 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
683 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093201.PNT | 2GDAS:RT093201.PNT | 20LAJ10CT027 | M-BFP MOTOR STATOR WINDING TEMP 4 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
684 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093202.PNT | 2GDAS:RT093202.PNT | 20LAJ10CT028 | M-BFP MOTOR STATOR WINDING TEMP 5 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
685 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 5 | MOTOR DRIVEN BOILER FEED WATER PUMP #20 | 50-F290S-J0201-21 | OPC.2GDAS:RT093203.PNT | 2GDAS:RT093203.PNT | 20LAJ10CT029 | M-BFP MOTOR STATOR WINDING TEMP 6 | RTD | 0 | 200 | °C |  |  |  | 140 | 150
488 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-08 | OPC.2GDAS:PT092603.PNT | 2GDAS:PT092603.PNT | 20LAB30CP201 | HP HEATER MAIN PIPE INLET WATER PRESS | AI | 0 | 25 | MPa
792 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092401.PNT | 2GDAS:TE092401.PNT | 20LAB30CT001 | HP HEATER INLET WATER TEMP | TC | 0 | 200 | °C
794 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092403.PNT | 2GDAS:TE092403.PNT | 20LAB30CT002 | #3 HP HEATER OUTLET MAIN PIPE WATER TEMP | TC | 0 | 210 | °C
1141 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120107.PNT | 2IDAS:LT120107.PNT | 20LAD30CL201 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1149 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120207.PNT | 2IDAS:LT120207.PNT | 20LAD30CL202 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1157 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120307.PNT | 2IDAS:LT120307.PNT | 20LAD30CL203 | #3 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
472 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2FDAS:ZT086607.PNT | 2FDAS:ZT086607.PNT | 20LBQ30AA001XB12 | #3 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
454 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2FDAS:PT086403.PNT | 2FDAS:PT086403.PNT | 20LBQ30CP201 | #3 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 2 | MPa
502 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2GDAS:PT104103.PNT | 2GDAS:PT104103.PNT | 20LBQ30CP202 | #3 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 2 | MPa
758 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087201.PNT | 2FDAS:TE087201.PNT | 20LBQ30CT001 | #3 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | °C
759 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087202.PNT | 2FDAS:TE087202.PNT | 20LBQ30CT002 | #3 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | °C
760 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087203.PNT | 2FDAS:TE087203.PNT | 20LBQ30CT003 | #3 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | °C
821 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-05 | OPC.2GDAS:TE107305.PNT | 2GDAS:TE107305.PNT | 20LBQ30CT004 | #3 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | °C
1245 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP3LVL:AO122404.OUT | 2HP3LVL:AO122404.OUT | 20LCH30AA101XB11 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1204 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121204.PNT | 2IDAS:ZT121204.PNT | 20LCH30AA101XB12 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1246 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP3LVL:AO122405.OUT | 2HP3LVL:AO122405.OUT | 20LCH30AA102XB11 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1205 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121205.PNT | 2IDAS:ZT121205.PNT | 20LCH30AA102XB12 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
801 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #20 | 50-F290S-J0201-09(1/2) | OPC.2GDAS:TE092503.PNT | 2GDAS:TE092503.PNT | 20LCH30CT001 | #3 HP HEATER DRAIN WATER TEMP | TC | 0 | 190 | °C
796 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092405.PNT | 2GDAS:TE092405.PNT | 20LAB30CT003 | #2 HP HEATER OUTLET WATER TEMP | TC | 0 | 250 | °C
795 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092404.PNT | 2GDAS:TE092404.PNT | 20LAB30CT004 | #2 HP HEATER INLET WATER TEMP | TC | 0 | 210 | °C
1140 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120106.PNT | 2IDAS:LT120106.PNT | 20LAD20CL201 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1148 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120206.PNT | 2IDAS:LT120206.PNT | 20LAD20CL202 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1156 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120306.PNT | 2IDAS:LT120306.PNT | 20LAD20CL203 | #2 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
471 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2FDAS:ZT086606.PNT | 2FDAS:ZT086606.PNT | 20LBQ20AA001XB12 | #2 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
453 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2FDAS:PT086402.PNT | 2FDAS:PT086402.PNT | 20LBQ20CP201 | #2 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 4 | MPa
501 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2GDAS:PT104102.PNT | 2GDAS:PT104102.PNT | 20LBQ20CP202 | #2 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 4 | MPa
753 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087104.PNT | 2FDAS:TE087104.PNT | 20LBQ20CT001 | #2 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 600 | °C
754 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087105.PNT | 2FDAS:TE087105.PNT | 20LBQ20CT002 | #2 EXTRACTION PIPE TOP TEMP | TC | 0 | 600 | °C
755 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087106.PNT | 2FDAS:TE087106.PNT | 20LBQ20CT003 | #2 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 600 | °C
820 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-05 | OPC.2GDAS:TE107304.PNT | 2GDAS:TE107304.PNT | 20LBQ20CT004 | #2 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | °C
1242 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP2LVL:AO122401.OUT | 2HP2LVL:AO122401.OUT | 20LCH20AA101XB11 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1201 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121201.PNT | 2IDAS:ZT121201.PNT | 20LCH20AA101XB12 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1243 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP2LVL:AO122402.OUT | 2HP2LVL:AO122402.OUT | 20LCH20AA102XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1202 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121202.PNT | 2IDAS:ZT121202.PNT | 20LCH20AA102XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1244 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP2LVL:AO122403.OUT | 2HP2LVL:AO122403.OUT | 20LCH20AA103XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1203 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121203.PNT | 2IDAS:ZT121203.PNT | 20LCH20AA103XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
800 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #20 | 50-F290S-J0201-09(1/2) | OPC.2GDAS:TE092502.PNT | 2GDAS:TE092502.PNT | 20LCH20CT001 | #2 HP HEATER DRAIN WATER TEMP | TC | 0 | 210 | °C
798 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092407.PNT | 2GDAS:TE092407.PNT | 20LAB30CT004 | #1 HP HEATER OUTLET WATER TEMP | TC | 0 | 300 | °C
797 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-08 | OPC.2GDAS:TE092406.PNT | 2GDAS:TE092406.PNT | 20LAB30CT006 | #1 HP HEATER INLET WATER TEMP | TC | 0 | 250 | °C
489 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-08 | OPC.2GDAS:PT092604.PNT | 2GDAS:PT092604.PNT | 20LAB40CP201 | HP HEATER OUTLET WATER PRESS | AI | 0 | 25 | MPa
1139 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120105.PNT | 2IDAS:LT120105.PNT | 20LAD10CL201 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1147 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120205.PNT | 2IDAS:LT120205.PNT | 20LAD10CL202 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
1155 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:LT120305.PNT | 2IDAS:LT120305.PNT | 20LAD10CL203 | #1 HP HEATER LEVEL | AI | -100 | 150 | mm |  |  | -50 | 50
470 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2FDAS:ZT086605.PNT | 2FDAS:ZT086605.PNT | 20LBQ10AA001XB12 | #1 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | %
452 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2FDAS:PT086401.PNT | 2FDAS:PT086401.PNT | 20LBQ10CP201 | #1 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 6.5 | MPa
500 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2GDAS:PT104101.PNT | 2GDAS:PT104101.PNT | 20LBQ10CP202 | #1 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 6.5 | MPa
750 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087101.PNT | 2FDAS:TE087101.PNT | 20LBQ10CT001 | #1 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 450 | °C
751 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087102.PNT | 2FDAS:TE087102.PNT | 20LBQ10CT002 | #1 EXTRACTION PIPE TOP TEMP | TC | 0 | 450 | °C
752 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2FDAS:TE087103.PNT | 2FDAS:TE087103.PNT | 20LBQ10CT003 | #1 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 450 | °C
819 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-05 | OPC.2GDAS:TE107303.PNT | 2GDAS:TE107303.PNT | 20LBQ10CT004 | #1 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 450 | °C
1239 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP1LVL:AO122305.OUT | 2HP1LVL:AO122305.OUT | 20LCH10AA101XB11 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1198 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121106.PNT | 2IDAS:ZT121106.PNT | 20LCH10AA101XB12 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | %
1240 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP1LVL:AO122306.OUT | 2HP1LVL:AO122306.OUT | 20LCH10AA102XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | %
1199 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121107.PNT | 2IDAS:ZT121107.PNT | 20LCH10AA102XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | %
1241 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2HP1LVL:AO122307.OUT | 2HP1LVL:AO122307.OUT | 20LCH10AA103XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | %
1200 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2IDAS:ZT121108.PNT | 2IDAS:ZT121108.PNT | 20LCH10AA103XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | %
799 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #20 | 50-F290S-J0201-09(1/2) | OPC.2GDAS:TE092501.PNT | 2GDAS:TE092501.PNT | 20LCH10CT001 | #1 HP HEATER DRAIN WATER TEMP | TC | 0 | 260 | °C
548 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-K0601-03 | OPC.2GDAS:AO104701.OUT | 2GDAS:AO104701.OUT | 20DCSMEHA01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | %
549 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-K0601-03 | OPC.2GDAS:AO104702.OUT | 2GDAS:AO104702.OUT | 20DCSMEHB01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | %
228 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.2ODAS:ZT193301.PNT | 2ODAS:ZT193301.PNT | 20LAB40AA002XB12 | BOILER FEED WATER MOTORIZED ORIFICE VALVE POSITION | AI | 0 | 100 | %
870 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.PDAS:FT200604.PNT | PDAS:FT200604C.PNT | 20LAB40CF201 | FEED WATER FLOW | AI | 0 | 1500 | T/H
876 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.PDAS:FT200704.PNT | PDAS:FT200704C.PNT | 20LAB40CF202 | FEED WATER FLOW | AI | 0 | 1500 | T/H
884 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.PDAS:FT200804.PNT | PDAS:FT200804C.PNT | 20LAB40CF203 | FEED WATER FLOW | AI | 0 | 1500 | T/H
221 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.2ODAS:PT193201.PNT | 2ODAS:PT193201.PNT | 20LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa
1119 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.2PDAS:TE202808.PNT | 2PDAS:TE202808.PNT | 20LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | °C
240 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.2ODAS:AO193601.OUT | 2ODAS:AO193601.OUT | 20LAB41AA101XB11 | BOILER FEED WATER BYPASS CONTROL VALVE CONTROL | AO | 0 | 100 | %
229 | 1 | UJRBG #20 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F290S-J0201-08 | OPC.2ODAS:ZT193303.PNT | 2ODAS:ZT193303.PNT | 20LAB41AA101XB12 | BOILER FEED WATER BYPASS CONTROL VALVE POSITION | AI | 0 | 100 | %
997 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #20A | 50-F290S-J0201-02 | OPC.2SAFVANE:AO202106.OUT | 2SAFVANE:AO202106.OUT | 20HFW11AA101XB11 | SAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
893 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT201106.PNT | 2PDAS:ZT201106.PNT | 20HFW11AA101XB12 | SAF A INLET VANE POSITION | AI | 0 | 100 | %
33 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #20A | 50-F290S-J0201-02 | OPC.2LDAS:CT150301.PNT | 2LDAS:CT150301.PNT | 20HFW11AN001XB13 | SAF A CURRENT | AI | 0 | 250 | A
1005 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #20B | 50-F290S-J0201-02 | OPC.2SAFVANE:AO202206.OUT | 2SAFVANE:AO202206.OUT | 20HFW12AA101XB11 | SAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
900 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT201206.PNT | 2PDAS:ZT201206.PNT | 20HFW12AA101XB12 | SAF B INLET VANE POSITION | AI | 0 | 100 | %
48 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #20B | 50-F290S-J0201-02 | OPC.2LDAS:CT150701.PNT | 2LDAS:CT150701.PNT | 20HFW12AN001XB13 | SAF B CURRENT | AI | 0 | 250 | A
153 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2MDAS:PT163107.PNT | 2MDAS:PT163107.PNT | 20HFW10CP201 | SAF OUTLET AIR PRESSURE | AI | 0 | 25 | KPa
872 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2PDAS:PT200606.PNT | 2PDAS:PT200606.PNT | 20HFW10CP301 | DIFFERENTIAL PRESSURE BETWEEN SAF OUTLET AND PRIMARY AIR PIPE | AI | 0 | 6.5 | KPa
317 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2MDAS:TE162606.PNT | 2MDAS:TE162606.PNT | 20HFW10CT001 | SAF OUTLET AIR TEMP. | TC | 0 | 400 | °C
1025 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2SAFASH:AO202504.OUT | 2SAFASH:AO202504.OUT | 20HFW13AA101XB11 | SAF EXHAUST ASH VAVLE CONTROL COMMAND | AO | 0 | 100 | %
895 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2PDAS:ZT201108.PNT | 2PDAS:ZT201108.PNT | 20HFW13AA101XB12 | SAF EXHAUST ASH VAVLE POSITION | AI | 0 | 100 | %
871 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F290S-J0201-02 | OPC.2PDAS:PT200605.PNT | 2PDAS:PT200605.PNT | 20HFW13DP201 | SAF DIFFERENTIAL PRESSURE BETWEEN FILTER AND DISCHARGE ASH OUTLET | AI | 0 | 1.37 | KPa
34 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 4 | COAL FEEDER #20A | 50-F290S-J0201-03 | OPC.2LDAS:FT150302.PNT | 2LDAS:FT150302.PNT | 20HFB10GC001AI01 | ECF A INSTANTANEOUS FEED RATE | AI | 0 | 60
56 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 4 | COAL FEEDER #20A | 50-F290S-J0201-03 | OPC.2LDAS:AO150402.OUT | 2LDAS:AO150402.OUT | 20HFB10GC001AO01 | ECF A FEED RATE COMMAND | AO | 0 | 60
8 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-03 | OPC.2JDAS:CT130608.PNT | 2JDAS:CT130608.PNT | 20HFC10AJ001XB13 | MSM A CURRENT | AI | 0 | 75 | A
61 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130101.PNT | 2JDAS:RT130101.PNT | 20HFC10CT001 | MSM A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
68 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130201.PNT | 2JDAS:RT130201.PNT | 20HFC10CT002 | MSM A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
62 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130102.PNT | 2JDAS:RT130102.PNT | 20HFC10CT003 | MSM A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
69 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130202.PNT | 2JDAS:RT130202.PNT | 20HFC10CT004 | MSM A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
63 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130103.PNT | 2JDAS:RT130103.PNT | 20HFC10CT005 | MSM A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
70 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130203.PNT | 2JDAS:RT130203.PNT | 20HFC10CT006 | MSM A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
64 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130104.PNT | 2JDAS:RT130104.PNT | 20HFC10CT007 | MSM A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
71 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130204.PNT | 2JDAS:RT130204.PNT | 20HFC10CT008 | MSM A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
65 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130105.PNT | 2JDAS:RT130105.PNT | 20HFC10CT009 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
66 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130106.PNT | 2JDAS:RT130106.PNT | 20HFC10CT010 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
72 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130205.PNT | 2JDAS:RT130205.PNT | 20HFC10CT011 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
73 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130206.PNT | 2JDAS:RT130206.PNT | 20HFC10CT012 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
67 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130107.PNT | 2JDAS:RT130107.PNT | 20HFC10CT013 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
74 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130207.PNT | 2JDAS:RT130207.PNT | 20HFC10CT014 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130501.PNT | 2JDAS:RT130501.PNT | 20HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1090 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2PDAS:RT201701.PNT | 2PDAS:RT201701.PNT | 20HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1095 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2PDAS:RT201801.PNT | 2PDAS:RT201801.PNT | 20HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
90 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130502.PNT | 2JDAS:RT130502.PNT | 20HFC10CT018 | MSM A LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
91 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2JDAS:RT130503.PNT | 2JDAS:RT130503.PNT | 20HFC10CT019 | MSM A LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
170 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2MDAS:PT163403.PNT | 2MDAS:PT163403.PNT | 20HFC10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4 | %
51 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-35 | OPC.2LDAS:AI150702.PNT | 2LDAS:AI150702.PNT | 20HFC10GC003AI01 | MSM A OUTLET CO CONTENT | AI | 0 | 100 | %
1 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2JDAS:PT130601.PNT | 2JDAS:PT130601.PNT | 20HFE10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
993 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2MILLAHCAD:AO202102.OUT | 2MILLAHCAD:AO202102.OUT | 20HFE41AA101XB11 | MSM A INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
841 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT200105.PNT | 2PDAS:ZT200105.PNT | 20HFE41AA101XB12 | MSM A INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
992 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2MILLAHCAD:AO202101.OUT | 2MILLAHCAD:AO202101.OUT | 20HFE51AA101XB11 | MSM A INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
840 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT200104.PNT | 2PDAS:ZT200104.PNT | 20HFE51AA101XB12 | MSM A INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
994 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2MILLAPAD:AO202103.OUT | 2MILLAPAD:AO202103.OUT | 20HFE51AA102XB11 | MSM A INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
842 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT200106.PNT | 2PDAS:ZT200106.PNT | 20HFE51AA102XB12 | MSM A INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
838 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:FT200102.PNT | 2PDAS:FT200102.PNT | 20HFE51CF201 | MSM A INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
839 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:FT200103.PNT | 2PDAS:FT200103.PNT | 20HFE51CF202 | MSM A INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
837 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:PT200101.PNT | 2PDAS:PT200101.PNT | 20HFE51CP201 | MSM A INLET AIR PRESSURE | AI | 0 | 20 | KPa
1100 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-02 | OPC.2PDAS:TE202601.PNT | 2PDAS:TE202601.PNT | 20HFE51CT001 | MSM A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
1100 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-34 | OPC.2VMS2:AIN5.PNT | 2VMS2:AIN5.PNT | 20HFC10CY001X | #20 MSM A BEARING VIBRATION X | AI | 0 | 20 | µm
1100 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #20A | 50-F290S-J0201-34 | OPC.2VMS2:AIN6.PNT | 2VMS2:AIN6.PNT | 20HFC10CY001Y | #20 MSM A BEARING VIBRATION Y | AI | 0 | 20 | µm
172 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163501.PNT | 2MDAS:FT163501.PNT | 20HFF11CF201 | 1# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
1081 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211705.OUT | 2RHTTEM:AO211705.OUT | 20HHA10KV001XB11 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
984 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210705.PNT | 2QDAS:ZT210705.PNT | 20HHA10KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1082 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211706.OUT | 2RHTTEM:AO211706.OUT | 20HHA10KV002XB11 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
985 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210706.PNT | 2QDAS:ZT210706.PNT | 20HHA10KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
2 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130602.PNT | 2JDAS:AI130602.PNT | 20HHA11CB201B | 1# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1029 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAA:AO211101.OUT | 2AUXDAMPAA:AO211101.OUT | 20HLA11AA001XB11 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
932 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210101.PNT | 2QDAS:ZT210101.PNT | 20HLA11AA001XB12 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1030 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPA:AO211102.OUT | 2CYCDAMPA:AO211102.OUT | 20HLA11AA002XB11 | 1# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
933 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210102.PNT | 2QDAS:ZT210102.PNT | 20HLA11AA002XB12 | 1# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1031 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAB:AO211103.OUT | 2AUXDAMPAB:AO211103.OUT | 20HLA11AA003XB11 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
934 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 6 | MSM A PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210103.PNT | 2QDAS:ZT210103.PNT | 20HLA11AA003XB12 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
173 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163502.PNT | 2MDAS:FT163502.PNT | 20HFF12CF201 | 2# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
3 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130603.PNT | 2JDAS:AI130603.PNT | 20HHA12CB201B | 2# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1083 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211707.OUT | 2RHTTEM:AO211707.OUT | 20HHA20KV001XB11 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
986 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210707.PNT | 2QDAS:ZT210707.PNT | 20HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1084 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211708.OUT | 2RHTTEM:AO211708.OUT | 20HHA20KV002XB11 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
987 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210708.PNT | 2QDAS:ZT210708.PNT | 20HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1042 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAA:AO211206.OUT | 2AUXDAMPAA:AO211206.OUT | 20HLA21AA001XB11 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
945 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210206.PNT | 2QDAS:ZT210206.PNT | 20HLA21AA001XB12 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1043 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPA:AO211207.OUT | 2CYCDAMPA:AO211207.OUT | 20HLA21AA002XB11 | 2# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
946 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210207.PNT | 2QDAS:ZT210207.PNT | 20HLA21AA002XB12 | 2# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1044 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAB:AO211208.OUT | 2AUXDAMPAB:AO211208.OUT | 20HLA21AA003XB11 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
947 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 7 | MSM A PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210208.PNT | 2QDAS:ZT210208.PNT | 20HLA21AA003XB12 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
174 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163503.PNT | 2MDAS:FT163503.PNT | 20HFF13CF201 | 3# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
4 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130604.PNT | 2JDAS:AI130604.PNT | 20HHA13CB201B | 3# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1085 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211801.OUT | 2RHTTEM:AO211801.OUT | 20HHA30KV001XB11 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
988 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210801.PNT | 2QDAS:ZT210801.PNT | 20HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1086 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211802.OUT | 2RHTTEM:AO211802.OUT | 20HHA30KV002XB11 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
989 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210802.PNT | 2QDAS:ZT210802.PNT | 20HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1055 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAA:AO211403.OUT | 2AUXDAMPAA:AO211403.OUT | 20HLA31AA001XB11 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
958 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210403.PNT | 2QDAS:ZT210403.PNT | 20HLA31AA001XB12 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1056 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPA:AO211404.OUT | 2CYCDAMPA:AO211404.OUT | 20HLA31AA002XB11 | 3# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
959 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210404.PNT | 2QDAS:ZT210404.PNT | 20HLA31AA002XB12 | 3# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1057 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAB:AO211405.OUT | 2AUXDAMPAB:AO211405.OUT | 20HLA31AA003XB11 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
960 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 8 | MSM A PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210405.PNT | 2QDAS:ZT210405.PNT | 20HLA31AA003XB12 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
175 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163504.PNT | 2MDAS:FT163504.PNT | 20HFF14CF201 | 4# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
5 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130605.PNT | 2JDAS:AI130605.PNT | 20HHA14CB201B | 4# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1087 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211803.OUT | 2RHTTEM:AO211803.OUT | 20HHA40KV001XB11 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
990 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210803.PNT | 2QDAS:ZT210803.PNT | 20HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1088 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2RHTTEM:AO211804.OUT | 2RHTTEM:AO211804.OUT | 20HHA40KV002XB11 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | %
991 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-34 | OPC.2QDAS:ZT210804.PNT | 2QDAS:ZT210804.PNT | 20HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
1068 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAA:AO211508.OUT | 2AUXDAMPAA:AO211508.OUT | 20HLA41AA001XB11 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
971 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210508.PNT | 2QDAS:ZT210508.PNT | 20HLA41AA001XB12 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1069 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPA:AO211601.OUT | 2CYCDAMPA:AO211601.OUT | 20HLA41AA002XB11 | 4# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
972 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210601.PNT | 2QDAS:ZT210601.PNT | 20HLA41AA002XB12 | 4# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | %
1070 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPAB:AO211602.OUT | 2AUXDAMPAB:AO211602.OUT | 20HLA41AA003XB11 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
973 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 9 | MSM A PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210602.PNT | 2QDAS:ZT210602.PNT | 20HLA41AA003XB12 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
35 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 11 | COAL FEEDER #20B | 50-F290S-J0201-03 | OPC.2LDAS:FT150303.PNT | 2LDAS:FT150303.PNT | 20HFB20GC001AI01 | ECF B INSTANTANEOUS FEED RATE | AI | 0 | 60
57 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 11 | COAL FEEDER #20B | 50-F290S-J0201-03 | OPC.2LDAS:AO150403.OUT | 2LDAS:AO150403.OUT | 20HFB20GC001AO01 | ECF B FEED RATE COMMAND | AO | 0 | 60
52 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2LDAS:AI150703.PNT | 2LDAS:AI150703.PNT | 20HFC10GC003AI02 | MSM B OUTLET CO CONTENT | AI | 0 | 100 | %
16 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-03 | OPC.2JDAS:CT130708.PNT | 2JDAS:CT130708.PNT | 20HFC20AJ001XB13 | MSM B CURRENT | AI | 0 | 75 | A
75 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130301.PNT | 2JDAS:RT130301.PNT | 20HFC20CT001 | MSM B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
82 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130401.PNT | 2JDAS:RT130401.PNT | 20HFC20CT002 | MSM B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
76 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130302.PNT | 2JDAS:RT130302.PNT | 20HFC20CT003 | MSM B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
83 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130402.PNT | 2JDAS:RT130402.PNT | 20HFC20CT004 | MSM B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
77 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130303.PNT | 2JDAS:RT130303.PNT | 20HFC20CT005 | MSM B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
84 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130403.PNT | 2JDAS:RT130403.PNT | 20HFC20CT006 | MSM B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
78 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130304.PNT | 2JDAS:RT130304.PNT | 20HFC20CT007 | MSM B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
85 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130404.PNT | 2JDAS:RT130404.PNT | 20HFC20CT008 | MSM B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
79 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130305.PNT | 2JDAS:RT130305.PNT | 20HFC20CT009 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
80 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130306.PNT | 2JDAS:RT130306.PNT | 20HFC20CT010 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
86 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130405.PNT | 2JDAS:RT130405.PNT | 20HFC20CT011 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
87 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130406.PNT | 2JDAS:RT130406.PNT | 20HFC20CT012 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
81 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130307.PNT | 2JDAS:RT130307.PNT | 20HFC20CT013 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
88 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130407.PNT | 2JDAS:RT130407.PNT | 20HFC20CT014 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
92 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130504.PNT | 2JDAS:RT130504.PNT | 20HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1091 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2PDAS:RT201702.PNT | 2PDAS:RT201702.PNT | 20HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1096 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2PDAS:RT201802.PNT | 2PDAS:RT201802.PNT | 20HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
93 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130505.PNT | 2JDAS:RT130505.PNT | 20HFC20CT018 | MSM B LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
94 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2JDAS:RT130506.PNT | 2JDAS:RT130506.PNT | 20HFC20CT019 | MSM B LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
171 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2MDAS:PT163404.PNT | 2MDAS:PT163404.PNT | 20HFC20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4 | %
9 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2JDAS:PT130701.PNT | 2JDAS:PT130701.PNT | 20HFE20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1001 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2MILLBHCAD:AO202202.OUT | 2MILLBHCAD:AO202202.OUT | 20HFE42AA101XB11 | MSM B INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
847 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT200205.PNT | 2PDAS:ZT200205.PNT | 20HFE42AA101XB12 | MSM B INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1000 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2MILLBHCAD:AO202201.OUT | 2MILLBHCAD:AO202201.OUT | 20HFE52AA101XB11 | MSM B INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
846 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT200204.PNT | 2PDAS:ZT200204.PNT | 20HFE52AA101XB12 | MSM B INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1002 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2MILLBPAD:AO202203.OUT | 2MILLBPAD:AO202203.OUT | 20HFE52AA102XB11 | MSM B INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
848 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT200206.PNT | 2PDAS:ZT200206.PNT | 20HFE52AA102XB12 | MSM B INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
844 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:FT200202.PNT | 2PDAS:FT200202.PNT | 20HFE52CF201 | MSM B INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
845 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:FT200203.PNT | 2PDAS:FT200203.PNT | 20HFE52CF202 | MSM B INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
843 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:PT200201.PNT | 2PDAS:PT200201.PNT | 20HFE52CP201 | MSM B INLET AIR PRESSURE | AI | 0 | 20 | KPa
1101 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-02 | OPC.2PDAS:TE202602.PNT | 2PDAS:TE202602.PNT | 20HFE52CT001 | MSM B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2VMS2:AIN7.PNT | 2VMS2:AIN7.PNT | 20HFC20CY001X | #20 MSM B BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #20B | 50-F290S-J0201-35 | OPC.2VMS2:AIN8.PNT | 2VMS2:AIN8.PNT | 20HFC20CY001Y | #20 MSM B BEARING VIBRATION Y | AI | 0 | 20 | µm
176 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163505.PNT | 2MDAS:FT163505.PNT | 20HFF21CF201 | 1# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
10 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130702.PNT | 2JDAS:AI130702.PNT | 20HHA21CB201B | 1# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1032 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPB:AO211104.OUT | 2CYCDAMPB:AO211104.OUT | 20HLA11AA004XB11 | 1# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
935 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210104.PNT | 2QDAS:ZT210104.PNT | 20HLA11AA004XB12 | 1# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1033 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPBC:AO211105.OUT | 2AUXDAMPBC:AO211105.OUT | 20HLA11AA005XB11 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
936 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 13 | MSM B PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210105.PNT | 2QDAS:ZT210105.PNT | 20HLA11AA005XB12 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
177 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163506.PNT | 2MDAS:FT163506.PNT | 20HFF22CF201 | 2# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
11 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130703.PNT | 2JDAS:AI130703.PNT | 20HHA22CB201B | 2# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1045 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPB:AO211301.OUT | 2CYCDAMPB:AO211301.OUT | 20HLA21AA004XB11 | 2# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
948 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210301.PNT | 2QDAS:ZT210301.PNT | 20HLA21AA004XB12 | 2# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1046 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPBC:AO211302.OUT | 2AUXDAMPBC:AO211302.OUT | 20HLA21AA005XB11 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
949 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 14 | MSM B PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210302.PNT | 2QDAS:ZT210302.PNT | 20HLA21AA005XB12 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
178 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163507.PNT | 2MDAS:FT163507.PNT | 20HFF23CF201 | 3# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
12 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130704.PNT | 2JDAS:AI130704.PNT | 20HHA23CB201B | 3# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1058 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPB:AO211406.OUT | 2CYCDAMPB:AO211406.OUT | 20HLA31AA004XB11 | 3# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
961 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210406.PNT | 2QDAS:ZT210406.PNT | 20HLA31AA004XB12 | 3# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1059 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPBC:AO211407.OUT | 2AUXDAMPBC:AO211407.OUT | 20HLA31AA005XB11 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
962 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 15 | MSM B PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210407.PNT | 2QDAS:ZT210407.PNT | 20HLA31AA005XB12 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
179 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2MDAS:FT163508.PNT | 2MDAS:FT163508.PNT | 20HFF24CF201 | 4# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1 | %
13 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2JDAS:AI130705.PNT | 2JDAS:AI130705.PNT | 20HHA24CB201B | 4# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1071 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPB:AO211603.OUT | 2CYCDAMPB:AO211603.OUT | 20HLA41AA004XB11 | 4# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
974 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210603.PNT | 2QDAS:ZT210603.PNT | 20HLA41AA004XB12 | 4# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1072 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPBC:AO211604.OUT | 2AUXDAMPBC:AO211604.OUT | 20HLA41AA005XB11 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
975 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 16 | MSM B PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210604.PNT | 2QDAS:ZT210604.PNT | 20HLA41AA005XB12 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
36 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 18 | COAL FEEDER #20C | 50-F290S-J0201-03 | OPC.2LDAS:FT150304.PNT | 2LDAS:FT150304.PNT | 20HFB30GC001AI01 | ECF C INSTANTANEOUS FEED RATE | AI | 0 | 60
58 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 18 | COAL FEEDER #20C | 50-F290S-J0201-03 | OPC.2LDAS:AO150404.OUT | 2LDAS:AO150404.OUT | 20HFB30GC001AO01 | ECF C FEED RATE COMMAND | AO | 0 | 60
53 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2LDAS:AI150704.PNT | 2LDAS:AI150704.PNT | 20HFC10GC003AI03 | MSM C OUTLET CO CONTENT | AI | 0 | 100 | %
24 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-03 | OPC.2KDAS:CT140608.PNT | 2KDAS:CT140608.PNT | 20HFC30AJ001XB13 | MSM C CURRENT | AI | 0 | 75 | A
95 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140101.PNT | 2KDAS:RT140101.PNT | 20HFC30CT001 | MSM C MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
102 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140201.PNT | 2KDAS:RT140201.PNT | 20HFC30CT002 | MSM C MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
96 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140102.PNT | 2KDAS:RT140102.PNT | 20HFC30CT003 | MSM C MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
103 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140202.PNT | 2KDAS:RT140202.PNT | 20HFC30CT004 | MSM C MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
97 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140103.PNT | 2KDAS:RT140103.PNT | 20HFC30CT005 | MSM C MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
104 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140203.PNT | 2KDAS:RT140203.PNT | 20HFC30CT006 | MSM C MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
98 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140104.PNT | 2KDAS:RT140104.PNT | 20HFC30CT007 | MSM C MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
105 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140204.PNT | 2KDAS:RT140204.PNT | 20HFC30CT008 | MSM C MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
99 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140105.PNT | 2KDAS:RT140105.PNT | 20HFC30CT009 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
100 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140106.PNT | 2KDAS:RT140106.PNT | 20HFC30CT010 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
106 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140205.PNT | 2KDAS:RT140205.PNT | 20HFC30CT011 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
107 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140206.PNT | 2KDAS:RT140206.PNT | 20HFC30CT012 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
101 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140107.PNT | 2KDAS:RT140107.PNT | 20HFC30CT013 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
108 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140207.PNT | 2KDAS:RT140207.PNT | 20HFC30CT014 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
123 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140501.PNT | 2KDAS:RT140501.PNT | 20HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1092 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2PDAS:RT201703.PNT | 2PDAS:RT201703.PNT | 20HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1097 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2PDAS:RT201803.PNT | 2PDAS:RT201803.PNT | 20HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
124 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140502.PNT | 2KDAS:RT140502.PNT | 20HFC30CT018 | MSM C LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
125 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2KDAS:RT140503.PNT | 2KDAS:RT140503.PNT | 20HFC30CT019 | MSM C LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
202 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2NDAS:PT183403.PNT | 2NDAS:PT183403.PNT | 20HFC30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
17 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2KDAS:PT140601.PNT | 2KDAS:PT140601.PNT | 20HFE30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1009 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2MILLCHCAD:AO202302.OUT | 2MILLCHCAD:AO202302.OUT | 20HFE43AA101XB11 | MSM C INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
853 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:ZT200305.PNT | 2PDAS:ZT200305.PNT | 20HFE43AA101XB12 | MSM C INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1008 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2MILLCHCAD:AO202301.OUT | 2MILLCHCAD:AO202301.OUT | 20HFE53AA101XB11 | MSM C INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
852 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:ZT200304.PNT | 2PDAS:ZT200304.PNT | 20HFE53AA101XB12 | MSM C INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1010 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2MILLCPAD:AO202303.OUT | 2MILLCPAD:AO202303.OUT | 20HFE53AA102XB11 | MSM C INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
854 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:ZT200306.PNT | 2PDAS:ZT200306.PNT | 20HFE53AA102XB12 | MSM C INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
850 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:FT200302.PNT | 2PDAS:FT200302.PNT | 20HFE53CF201 | MSM C INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
851 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:FT200303.PNT | 2PDAS:FT200303.PNT | 20HFE53CF202 | MSM C INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
849 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:PT200301.PNT | 2PDAS:PT200301.PNT | 20HFE53CP201 | MSM C INLET AIR PRESSURE | AI | 0 | 20 | KPa
1102 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-02 | OPC.2PDAS:TE202603.PNT | 2PDAS:TE202603.PNT | 20HFE53CT001 | MSM C INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2VMS2:AIN9.PNT | 2VMS2:AIN9.PNT | 20HFC30CY001X | #20 MSM C BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #20C | 50-F290S-J0201-35 | OPC.2VMS2:AIN10.PNT | 2VMS2:AIN10.PNT | 20HFC30CY001Y | #20 MSM C BEARING VIBRATION Y | AI | 0 | 20 | µm
206 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183501.PNT | 2NDAS:FT183501.PNT | 20HFF31CF201 | 1# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
18 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140602.PNT | 2KDAS:AI140602.PNT | 20HHA31CB201B | 1# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1034 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPC:AO211106.OUT | 2CYCDAMPC:AO211106.OUT | 20HLA11AA006XB11 | 1# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
937 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210106.PNT | 2QDAS:ZT210106.PNT | 20HLA11AA006XB12 | 1# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1035 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPCC:AO211107.OUT | 2AUXDAMPCC:AO211107.OUT | 20HLA11AA007XB11 | 1#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
938 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 20 | MSM C PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210107.PNT | 2QDAS:ZT210107.PNT | 20HLA11AA007XB12 | 1# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
207 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183502.PNT | 2NDAS:FT183502.PNT | 20HFF32CF201 | 2# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
19 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140603.PNT | 2KDAS:AI140603.PNT | 20HHA32CB201B | 2# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1047 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPC:AO211303.OUT | 2CYCDAMPC:AO211303.OUT | 20HLA21AA006XB11 | 2# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
950 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210303.PNT | 2QDAS:ZT210303.PNT | 20HLA21AA006XB12 | 2# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1048 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPCC:AO211304.OUT | 2AUXDAMPCC:AO211304.OUT | 20HLA21AA007XB11 | 2#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
951 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 21 | MSM C PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210304.PNT | 2QDAS:ZT210304.PNT | 20HLA21AA007XB12 | 2# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
208 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183503.PNT | 2NDAS:FT183503.PNT | 20HFF33CF201 | 3# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
20 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140604.PNT | 2KDAS:AI140604.PNT | 20HHA33CB201B | 3# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1060 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPC:AO211408.OUT | 2CYCDAMPC:AO211408.OUT | 20HLA31AA006XB11 | 3# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
963 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210408.PNT | 2QDAS:ZT210408.PNT | 20HLA31AA006XB12 | 3# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1061 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPCC:AO211501.OUT | 2AUXDAMPCC:AO211501.OUT | 20HLA31AA007XB11 | 3#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
964 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 22 | MSM C PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210501.PNT | 2QDAS:ZT210501.PNT | 20HLA31AA007XB12 | 3# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
209 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183504.PNT | 2NDAS:FT183504.PNT | 20HFF34CF201 | 4# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
21 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140605.PNT | 2KDAS:AI140605.PNT | 20HHA34CB201B | 4# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1073 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPC:AO211605.OUT | 2CYCDAMPC:AO211605.OUT | 20HLA41AA006XB11 | 4# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
976 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210605.PNT | 2QDAS:ZT210605.PNT | 20HLA41AA006XB12 | 4# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1074 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPCC:AO211606.OUT | 2AUXDAMPCC:AO211606.OUT | 20HLA41AA007XB11 | 4#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
977 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 23 | MSM C PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210606.PNT | 2QDAS:ZT210606.PNT | 20HLA41AA007XB12 | 4# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
37 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 25 | COAL FEEDER #20D | 50-F290S-J0201-03 | OPC.2LDAS:FT150305.PNT | 2LDAS:FT150305.PNT | 20HFB40GC001AI01 | ECF D INSTANTANEOUS FEED RATE | AI | 0 | 60
59 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 25 | COAL FEEDER #20D | 50-F290S-J0201-03 | OPC.2LDAS:AO150405.OUT | 2LDAS:AO150405.OUT | 20HFB40GC001AO01 | ECF D FEED RATE COMMAND | AO | 0 | 60
54 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2LDAS:AI150705.PNT | 2LDAS:AI150705.PNT | 20HFC10GC003AI04 | MSM D OUTLET CO CONTENT | AI | 0 | 100 | %
32 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-03 | OPC.2KDAS:CT140708.PNT | 2KDAS:CT140708.PNT | 20HFC40AJ001XB13 | MSM D CURRENT | AI | 0 | 75 | A
109 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140301.PNT | 2KDAS:RT140301.PNT | 20HFC40CT001 | MSM D MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
116 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140401.PNT | 2KDAS:RT140401.PNT | 20HFC40CT002 | MSM D MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
110 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140302.PNT | 2KDAS:RT140302.PNT | 20HFC40CT003 | MSM D MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
117 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140402.PNT | 2KDAS:RT140402.PNT | 20HFC40CT004 | MSM D MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
111 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140303.PNT | 2KDAS:RT140303.PNT | 20HFC40CT005 | MSM D MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
118 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140403.PNT | 2KDAS:RT140403.PNT | 20HFC40CT006 | MSM D MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
112 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140304.PNT | 2KDAS:RT140304.PNT | 20HFC40CT007 | MSM D MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
119 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140404.PNT | 2KDAS:RT140404.PNT | 20HFC40CT008 | MSM D MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
113 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140305.PNT | 2KDAS:RT140305.PNT | 20HFC40CT009 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
114 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140306.PNT | 2KDAS:RT140306.PNT | 20HFC40CT010 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
120 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140405.PNT | 2KDAS:RT140405.PNT | 20HFC40CT011 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
121 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140406.PNT | 2KDAS:RT140406.PNT | 20HFC40CT012 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
115 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140307.PNT | 2KDAS:RT140307.PNT | 20HFC40CT013 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
122 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140407.PNT | 2KDAS:RT140407.PNT | 20HFC40CT014 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
126 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140504.PNT | 2KDAS:RT140504.PNT | 20HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1093 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2PDAS:RT201704.PNT | 2PDAS:RT201704.PNT | 20HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1098 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2PDAS:RT201804.PNT | 2PDAS:RT201804.PNT | 20HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
127 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140505.PNT | 2KDAS:RT140505.PNT | 20HFC40CT018 | MSM D LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
128 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2KDAS:RT140506.PNT | 2KDAS:RT140506.PNT | 20HFC40CT019 | MSM D LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
203 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2NDAS:PT183404.PNT | 2NDAS:PT183404.PNT | 20HFC40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
25 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2KDAS:PT140701.PNT | 2KDAS:PT140701.PNT | 20HFE40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1016 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2MILLDHCAD:AO202402.OUT | 2MILLDHCAD:AO202402.OUT | 20HFE44AA101XB11 | MSM D INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
859 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:ZT200405.PNT | 2PDAS:ZT200405.PNT | 20HFE44AA101XB12 | MSM D INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1015 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2MILLDHCAD:AO202401.OUT | 2MILLDHCAD:AO202401.OUT | 20HFE54AA101XB11 | MSM D INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
858 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:ZT200404.PNT | 2PDAS:ZT200404.PNT | 20HFE54AA101XB12 | MSM D INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1017 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2MILLDPAD:AO202403.OUT | 2MILLDPAD:AO202403.OUT | 20HFE54AA102XB11 | MSM D INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
860 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:ZT200406.PNT | 2PDAS:ZT200406.PNT | 20HFE54AA102XB12 | MSM D INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
856 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:FT200402.PNT | 2PDAS:FT200402.PNT | 20HFE54CF201 | MSM D INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
857 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:FT200403.PNT | 2PDAS:FT200403.PNT | 20HFE54CF202 | MSM D INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
855 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:PT200401.PNT | 2PDAS:PT200401.PNT | 20HFE54CP201 | MSM D INLET AIR PRESSURE | AI | 0 | 20 | KPa
1103 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-02 | OPC.2PDAS:TE202604.PNT | 2PDAS:TE202604.PNT | 20HFE54CT001 | MSM D INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2VMS2:AIN11.PNT | 2VMS2:AIN11.PNT | 20HFC40CY001X | #20 MSM D BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #20D | 50-F290S-J0201-35 | OPC.2VMS2:AIN12.PNT | 2VMS2:AIN12.PNT | 20HFC40CY001Y | #20 MSM D BEARING VIBRATION Y | AI | 0 | 20 | µm
210 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183505.PNT | 2NDAS:FT183505.PNT | 20HFF41CF201 | 1# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
26 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140702.PNT | 2KDAS:AI140702.PNT | 20HHA41CB201B | 1# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1036 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDD:AO211108.OUT | 2AUXDAMPDD:AO211108.OUT | 20HLA11AA008XB11 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
939 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210108.PNT | 2QDAS:ZT210108.PNT | 20HLA11AA008XB12 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1037 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPD:AO211201.OUT | 2CYCDAMPD:AO211201.OUT | 20HLA11AA009XB11 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
940 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210201.PNT | 2QDAS:ZT210201.PNT | 20HLA11AA009XB12 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1038 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDE:AO211202.OUT | 2AUXDAMPDE:AO211202.OUT | 20HLA11AA010XB11 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
941 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 27 | MSM D PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210202.PNT | 2QDAS:ZT210202.PNT | 20HLA11AA010XB12 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
211 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183506.PNT | 2NDAS:FT183506.PNT | 20HFF42CF201 | 2# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
27 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140703.PNT | 2KDAS:AI140703.PNT | 20HHA42CB201B | 2# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1049 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDD:AO211305.OUT | 2AUXDAMPDD:AO211305.OUT | 20HLA21AA008XB11 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
952 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210305.PNT | 2QDAS:ZT210305.PNT | 20HLA21AA008XB12 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1050 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPD:AO211306.OUT | 2CYCDAMPD:AO211306.OUT | 20HLA21AA009XB11 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
953 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210306.PNT | 2QDAS:ZT210306.PNT | 20HLA21AA009XB12 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1051 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDE:AO211307.OUT | 2AUXDAMPDE:AO211307.OUT | 20HLA21AA010XB11 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
954 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 28 | MSM D PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210307.PNT | 2QDAS:ZT210307.PNT | 20HLA21AA010XB12 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
212 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183507.PNT | 2NDAS:FT183507.PNT | 20HFF43CF201 | 3# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
28 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140704.PNT | 2KDAS:AI140704.PNT | 20HHA43CB201B | 3# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1062 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDD:AO211502.OUT | 2AUXDAMPDD:AO211502.OUT | 20HLA31AA008XB11 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
965 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210502.PNT | 2QDAS:ZT210502.PNT | 20HLA31AA008XB12 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1063 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPD:AO211503.OUT | 2CYCDAMPD:AO211503.OUT | 20HLA31AA009XB11 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
966 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210503.PNT | 2QDAS:ZT210503.PNT | 20HLA31AA009XB12 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | %
1064 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDE:AO211504.OUT | 2AUXDAMPDE:AO211504.OUT | 20HLA31AA010XB11 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
967 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 29 | MSM D PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210504.PNT | 2QDAS:ZT210504.PNT | 20HLA31AA010XB12 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
213 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2NDAS:FT183508.PNT | 2NDAS:FT183508.PNT | 20HFF44CF201 | 4# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
29 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2KDAS:AI140705.PNT | 2KDAS:AI140705.PNT | 20HHA44CB201B | 4# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1075 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDD:AO211607.OUT | 2AUXDAMPDD:AO211607.OUT | 20HLA41AA008XB11 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
978 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210607.PNT | 2QDAS:ZT210607.PNT | 20HLA41AA008XB12 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1076 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPD:AO211608.OUT | 2CYCDAMPD:AO211608.OUT | 20HLA41AA009XB11 | 4# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
979 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210608.PNT | 2QDAS:ZT210608.PNT | 20HLA41AA009XB12 | 4# CORNER D LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1077 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPDE:AO211701.OUT | 2AUXDAMPDE:AO211701.OUT | 20HLA41AA010XB11 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
980 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 30 | MSM D PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210701.PNT | 2QDAS:ZT210701.PNT | 20HLA41AA010XB12 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
38 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 32 | COAL FEEDER #20E | 50-F290S-J0201-03 | OPC.2LDAS:FT150306.PNT | 2LDAS:FT150306.PNT | 20HFB50GC001AI01 | ECF E INSTANTANEOUS FEED RATE | AI | 0 | 60
60 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 32 | COAL FEEDER #20E | 50-F290S-J0201-03 | OPC.2LDAS:AO150406.OUT | 2LDAS:AO150406.OUT | 20HFB50GC001AO01 | ECF E FEED RATE COMMAND | AO | 0 | 60
55 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:AI150708.PNT | 2LDAS:AI150708.PNT | 20HFC10GC003AI05 | MSM E OUTLET CO CONTENT | AI | 0 | 100 | %
47 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-03 | OPC.2LDAS:CT150608.PNT | 2LDAS:CT150608.PNT | 20HFC50AJ001XB13 | MSM E CURRENT | AI | 0 | 75 | A
129 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150101.PNT | 2LDAS:RT150101.PNT | 20HFC50CT001 | MSM E MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
136 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150201.PNT | 2LDAS:RT150201.PNT | 20HFC50CT002 | MSM E MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C |  |  |  | 85 | 95
130 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150102.PNT | 2LDAS:RT150102.PNT | 20HFC50CT003 | MSM E MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
137 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150202.PNT | 2LDAS:RT150202.PNT | 20HFC50CT004 | MSM E MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
131 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150103.PNT | 2LDAS:RT150103.PNT | 20HFC50CT005 | MSM E MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
138 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150203.PNT | 2LDAS:RT150203.PNT | 20HFC50CT006 | MSM E MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
132 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150104.PNT | 2LDAS:RT150104.PNT | 20HFC50CT007 | MSM E MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
139 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150204.PNT | 2LDAS:RT150204.PNT | 20HFC50CT008 | MSM E MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 135 | 145
133 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150105.PNT | 2LDAS:RT150105.PNT | 20HFC50CT009 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
134 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150106.PNT | 2LDAS:RT150106.PNT | 20HFC50CT010 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
140 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150205.PNT | 2LDAS:RT150205.PNT | 20HFC50CT011 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
141 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150206.PNT | 2LDAS:RT150206.PNT | 20HFC50CT012 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 75 | 80
135 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150107.PNT | 2LDAS:RT150107.PNT | 20HFC50CT013 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
142 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150207.PNT | 2LDAS:RT150207.PNT | 20HFC50CT014 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 85 | 90
143 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150501.PNT | 2LDAS:RT150501.PNT | 20HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | °C
1094 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2PDAS:RT201705.PNT | 2PDAS:RT201705.PNT | 20HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | °C
1099 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2PDAS:RT201805.PNT | 2PDAS:RT201805.PNT | 20HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | °C
144 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150502.PNT | 2LDAS:RT150502.PNT | 20HFC50CT018 | MSM E LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 25 | 40
145 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2LDAS:RT150503.PNT | 2LDAS:RT150503.PNT | 20HFC50CT019 | MSM E LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | °C |  |  | 30
230 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2ODAS:PT193304.PNT | 2ODAS:PT193304.PNT | 20HFC50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 4
1023 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2MILLEHCAD:AO202502.OUT | 2MILLEHCAD:AO202502.OUT | 20HFE45AA101XB11 | MSM E INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
865 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:ZT200505.PNT | 2PDAS:ZT200505.PNT | 20HFE45AA101XB12 | MSM E INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
40 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2LDAS:PT150601.PNT | 2LDAS:PT150601.PNT | 20HFE50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa
1022 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2MILLEHCAD:AO202501.OUT | 2MILLEHCAD:AO202501.OUT | 20HFE55AA101XB11 | MSM E INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | %
864 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:ZT200504.PNT | 2PDAS:ZT200504.PNT | 20HFE55AA101XB12 | MSM E INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | %
1024 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2MILLEPAD:AO202503.OUT | 2MILLEPAD:AO202503.OUT | 20HFE55AA102XB11 | MSM E INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
866 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:ZT200506.PNT | 2PDAS:ZT200506.PNT | 20HFE55AA102XB12 | MSM E INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | %
862 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:FT200502.PNT | 2PDAS:FT200502.PNT | 20HFE55CF201 | MSM E INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
863 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:FT200503.PNT | 2PDAS:FT200503.PNT | 20HFE55CF202 | MSM E INLET PRIMARY AIR FLOW | AI | 0 | 1.231 | KPa
861 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:PT200501.PNT | 2PDAS:PT200501.PNT | 20HFE55CP201 | MSM E INLET AIR PRESSURE | AI | 0 | 20 | KPa
1104 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-02 | OPC.2PDAS:TE202605.PNT | 2PDAS:TE202605.PNT | 20HFE55CT001 | MSM E INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2VMS2:AIN13.PNT | 2VMS2:AIN13.PNT | 20HFC50CY001X | #20 MSM E BEARING VIBRATION X | AI | 0 | 20 | µm
89 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #20E | 50-F290S-J0201-35 | OPC.2VMS2:AIN14.PNT | 2VMS2:AIN14.PNT | 20HFC50CY001Y | #20 MSM E BEARING VIBRATION Y | AI | 0 | 20 | µm
231 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2ODAS:FT193305.PNT | 2ODAS:FT193305.PNT | 20HFF51CF201 | 1# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
41 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2LDAS:AI150602.PNT | 2LDAS:AI150602.PNT | 20HHA51CB201B | 1# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1039 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPE:AO211203.OUT | 2CYCDAMPE:AO211203.OUT | 20HLA11AA011XB11 | 1# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
942 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210203.PNT | 2QDAS:ZT210203.PNT | 20HLA11AA011XB12 | 1# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1040 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPEF:AO211204.OUT | 2AUXDAMPEF:AO211204.OUT | 20HLA11AA012XB11 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
943 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210204.PNT | 2QDAS:ZT210204.PNT | 20HLA11AA012XB12 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1041 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2BUTDAMEFF:AO211205.OUT | 2BUTDAMEFF:AO211205.OUT | 20HLA11AA013XB11 | 1# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
944 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 34 | MSM E PULVERIZED COAL CORNER 1 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210205.PNT | 2QDAS:ZT210205.PNT | 20HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
232 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2ODAS:FT193306.PNT | 2ODAS:FT193306.PNT | 20HFF52CF201 | 2# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
42 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2LDAS:AI150603.PNT | 2LDAS:AI150603.PNT | 20HHA52CB201B | 2# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1052 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPE:AO211308.OUT | 2CYCDAMPE:AO211308.OUT | 20HLA21AA011XB11 | 2# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
955 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210308.PNT | 2QDAS:ZT210308.PNT | 20HLA21AA011XB12 | 2# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1053 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPEF:AO211401.OUT | 2AUXDAMPEF:AO211401.OUT | 20HLA21AA012XB11 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
956 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210401.PNT | 2QDAS:ZT210401.PNT | 20HLA21AA012XB12 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1054 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2BUTDAMEFF:AO211402.OUT | 2BUTDAMEFF:AO211402.OUT | 20HLA21AA013XB11 | 2# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
957 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 35 | MSM E PULVERIZED COAL CORNER 2 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210402.PNT | 2QDAS:ZT210402.PNT | 20HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
233 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2ODAS:FT193307.PNT | 2ODAS:FT193307.PNT | 20HFF53CF201 | 3# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
43 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2LDAS:AI150604.PNT | 2LDAS:AI150604.PNT | 20HHA53CB201B | 3# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1065 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPE:AO211505.OUT | 2CYCDAMPE:AO211505.OUT | 20HLA31AA011XB11 | 3# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
968 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210505.PNT | 2QDAS:ZT210505.PNT | 20HLA31AA011XB12 | 3# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1066 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPEF:AO211506.OUT | 2AUXDAMPEF:AO211506.OUT | 20HLA31AA012XB11 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
969 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210506.PNT | 2QDAS:ZT210506.PNT | 20HLA31AA012XB12 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1067 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2BUTDAMEFF:AO211507.OUT | 2BUTDAMEFF:AO211507.OUT | 20HLA31AA013XB11 | 3# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
970 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 36 | MSM E PULVERIZED COAL CORNER 3 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210507.PNT | 2QDAS:ZT210507.PNT | 20HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
234 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2ODAS:FT193308.PNT | 2ODAS:FT193308.PNT | 20HFF54CF201 | 4# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 1.1
44 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2LDAS:AI150605.PNT | 2LDAS:AI150605.PNT | 20HHA54CB201B | 4# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | %
1078 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2CYCDAMPE:AO211702.OUT | 2CYCDAMPE:AO211702.OUT | 20HLA41AA011XB11 | 4# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
981 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210702.PNT | 2QDAS:ZT210702.PNT | 20HLA41AA011XB12 | 4# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | %
1079 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2AUXDAMPEF:AO211703.OUT | 2AUXDAMPEF:AO211703.OUT | 20HLA41AA012XB11 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
982 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210703.PNT | 2QDAS:ZT210703.PNT | 20HLA41AA012XB12 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | %
1080 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2BUTDAMEFF:AO211704.OUT | 2BUTDAMEFF:AO211704.OUT | 20HLA41AA013XB11 | 4# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | %
983 | 1 | UJRBG #20 | 5 | PULVERIZER SYSTEM#2 | 37 | MSM E PULVERIZED COAL CORNER 4 SYSTEM #20 | 50-F290S-J0201-03 | OPC.2QDAS:ZT210704.PNT | 2QDAS:ZT210704.PNT | 20HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
154 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER TUBE #20 | 50-F290S-J0201-02 | OPC.2MDAS:PT163201.PNT | 2MDAS:PT163201.PNT | 20HNA10CP201 | A SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa
314 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER TUBE #20 | 50-F290S-J0201-02 | OPC.2MDAS:TE162603.PNT | 2MDAS:TE162603.PNT | 20HNA10CT001 | A SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | °C
186 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER TUBE #20 | 50-F290S-J0201-02 | OPC.2NDAS:PT183201.PNT | 2NDAS:PT183201.PNT | 20HNA20CP201 | B SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa
328 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER TUBE #20 | 50-F290S-J0201-02 | OPC.2NDAS:TE182603.PNT | 2NDAS:TE182603.PNT | 20HNA20CT001 | B SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
869 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:LT200603.PNT | 2PDAS:LT200603.PNT | 20HAG10CL201 | DRUM LEVEL | AI | -300 | 300 | mm
875 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:LT200703.PNT | 2PDAS:LT200703.PNT | 20HAG10CL202 | DRUM LEVEL | AI | -300 | 300 | mm
883 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:LT200803.PNT | 2PDAS:LT200803.PNT | 20HAG10CL203 | DRUM LEVEL | AI | -300 | 300 | mm
868 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:PT200602.PNT | 2PDAS:PT200602.PNT | 20HAG10CP201 | DRUM PRESSURE | AI | 0 | 20 | MPa
874 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:PT200702.PNT | 2PDAS:PT200702.PNT | 20HAG10CP202 | DRUM PRESSURE | AI | 0 | 20 | MPa
882 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #20 | 50-F290S-J0201-04 | OPC.2PDAS:PT200802.PNT | 2PDAS:PT200802.PNT | 20HAG10CP203 | DRUM PRESSURE | AI | 0 | 20 | MPa
1268 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254301.PNT | 2ODAS:TE254301.PNT | 20HAG10CT001 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1276 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254401.PNT | 2ODAS:TE254401.PNT | 20HAG10CT002 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1284 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254501.PNT | 2ODAS:TE254501.PNT | 20HAG10CT003 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1291 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254601.PNT | 2ODAS:TE254601.PNT | 20HAG10CT004 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1298 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254701.PNT | 2ODAS:TE254701.PNT | 20HAG10CT005 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1305 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254801.PNT | 2ODAS:TE254801.PNT | 20HAG10CT006 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1311 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255101.PNT | 2ODAS:TE255101.PNT | 20HAG10CT007 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | °C
1269 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254302.PNT | 2ODAS:TE254302.PNT | 20HAG10CT008 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1270 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254303.PNT | 2ODAS:TE254303.PNT | 20HAG10CT009 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1277 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254402.PNT | 2ODAS:TE254402.PNT | 20HAG10CT010 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1278 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254403.PNT | 2ODAS:TE254403.PNT | 20HAG10CT011 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | °C
1271 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254304.PNT | 2ODAS:TE254304.PNT | 20HAG10CT012 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 5th TUBE | TC | 0 | 600 | °C
1279 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WATER WALL TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254404.PNT | 2ODAS:TE254404.PNT | 20HAG10CT013 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 12th TUBE | TC | 0 | 600 | °C
167 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2MDAS:PT163307.PNT | 2MDAS:PT163307.PNT | 20H10CP205 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa
923 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2PDAS:AI201506.PNT | 2PDAS:AI201506.PNT | 20H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
930 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2PDAS:AI201606.PNT | 2PDAS:AI201606.PNT | 20H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
325 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2MDAS:TE162707.PNT | 2MDAS:TE162707.PNT | 20H10CT009 | A SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | °C
199 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2NDAS:PT183307.PNT | 2NDAS:PT183307.PNT | 20H20CP205 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa
924 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2PDAS:AI201507.PNT | 2PDAS:AI201507.PNT | 20H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
931 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-34 | OPC.2PDAS:AI201607.PNT | 2PDAS:AI201607.PNT | 20H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
1272 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254305.PNT | 2ODAS:TE254305.PNT | 20HAH10CT001 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1273 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254306.PNT | 2ODAS:TE254306.PNT | 20HAH10CT002 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1280 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254405.PNT | 2ODAS:TE254405.PNT | 20HAH10CT003 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1281 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254406.PNT | 2ODAS:TE254406.PNT | 20HAH10CT004 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADE | TC | 0 | 600 | °C
1285 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254502.PNT | 2ODAS:TE254502.PNT | 20HAH10CT005 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 4th | TC | 0 | 600 | °C
1286 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254503.PNT | 2ODAS:TE254503.PNT | 20HAH10CT006 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 7th | TC | 0 | 600 | °C
1292 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254602.PNT | 2ODAS:TE254602.PNT | 20HAH10CT007 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 10th | TC | 0 | 600 | °C
1293 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254603.PNT | 2ODAS:TE254603.PNT | 20HAH10CT008 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 12th | TC | 0 | 600 | °C
1299 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254702.PNT | 2ODAS:TE254702.PNT | 20HAH10CT009 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FEOM LEFT 15th | TC | 0 | 600 | °C
1300 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254703.PNT | 2ODAS:TE254703.PNT | 20HAH10CT010 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 18th | TC | 0 | 600 | °C
1287 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254504.PNT | 2ODAS:TE254504.PNT | 20HAH10CT011 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1288 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254505.PNT | 2ODAS:TE254505.PNT | 20HAH10CT012 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1294 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254604.PNT | 2ODAS:TE254604.PNT | 20HAH10CT013 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1295 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254605.PNT | 2ODAS:TE254605.PNT | 20HAH10CT014 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT | TC | 0 | 600 | °C
1301 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254704.PNT | 2ODAS:TE254704.PNT | 20HAH10CT015 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1302 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254705.PNT | 2ODAS:TE254705.PNT | 20HAH10CT016 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1274 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254307.PNT | 2ODAS:TE254307.PNT | 20HAH10CT017 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LE | TC | 0 | 600 | °C
1275 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254308.PNT | 2ODAS:TE254308.PNT | 20HAH10CT018 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LE | TC | 0 | 600 | °C
1282 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254407.PNT | 2ODAS:TE254407.PNT | 20HAH10CT019 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
1283 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254408.PNT | 2ODAS:TE254408.PNT | 20HAH10CT020 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEF | TC | 0 | 600 | °C
339 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193401.PNT | 2ODAS:TE193401.PNT | 20HAH11CT001 | SUPERHEATER 1st STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1107 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202704.PNT | 2PDAS:TE202704.PNT | 20HAH11CT002 | SUPERHEATER 1st STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1108 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202705.PNT | 2PDAS:TE202705.PNT | 20HAH11CT003 | SUPERHEATER 1st STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
340 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193402.PNT | 2ODAS:TE193402.PNT | 20HAH21CT001 | SUPERHEATER 2nd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1109 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202706.PNT | 2PDAS:TE202706.PNT | 20HAH21CT002 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1110 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202707.PNT | 2PDAS:TE202707.PNT | 20HAH21CT003 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1112 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202801.PNT | 2PDAS:TE202801.PNT | 20HAH21CT004 | SUPERHEATER 3rd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1113 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202802.PNT | 2PDAS:TE202802.PNT | 20HAH21CT005 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1114 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202803.PNT | 2PDAS:TE202803.PNT | 20HAH21CT006 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
341 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193403.PNT | 2ODAS:TE193403.PNT | 20HAH22CT001 | SUPERHEATER 2nd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1111 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202708.PNT | 2PDAS:TE202708.PNT | 20HAH22CT002 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
342 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193404.PNT | 2ODAS:TE193404.PNT | 20HAH22CT003 | SUPERHEATER 2nd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
343 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193405.PNT | 2ODAS:TE193405.PNT | 20HAH22CT004 | SUPERHEATER 3rd STAGE DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1115 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202804.PNT | 2PDAS:TE202804.PNT | 20HAH22CT005 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1116 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202805.PNT | 2PDAS:TE202805.PNT | 20HAH22CT006 | SUPERHEATER 3rd STAGE DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
219 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2ODAS:PT193106.PNT | 2ODAS:PT193106.PNT | 20LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa
350 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2ODAS:TE193505.PNT | 2ODAS:TE193505.PNT | 20LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | °C
1021 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2SHTDESUP1:AO202407.OUT | 2SHTDESUP1:AO202407.OUT | 20LAE41AA101XB11 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
917 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201408.PNT | 2PDAS:ZT201408.PNT | 20LAE41AA101XB12 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
916 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201407.PNT | 2PDAS:FT201407.PNT | 20LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1012 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2SHTDESUP2A:AO202305.OUT | 2SHTDESUP2A:AO202305.OUT | 20LAE42AA101XB11 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
906 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201305.PNT | 2PDAS:ZT201305.PNT | 20LAE42AA101XB12 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
903 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201302.PNT | 2PDAS:FT201302.PNT | 20LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1019 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2SHTDESUP2B:AO202405.OUT | 2SHTDESUP2B:AO202405.OUT | 20LAE43AA101XB11 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
914 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201405.PNT | 2PDAS:ZT201405.PNT | 20LAE43AA101XB12 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
911 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201402.PNT | 2PDAS:FT201402.PNT | 20LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1013 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2SHTDESUP3A:AO202306.OUT | 2SHTDESUP3A:AO202306.OUT | 20LAE44AA101XB11 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
907 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201306.PNT | 2PDAS:ZT201306.PNT | 20LAE44AA101XB12 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
904 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201303.PNT | 2PDAS:FT201303.PNT | 20LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1020 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2SHTDESUP3B:AO202406.OUT | 2SHTDESUP3B:AO202406.OUT | 20LAE45AA101XB11 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE C | AO | 0 | 100 | %
915 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201406.PNT | 2PDAS:ZT201406.PNT | 20LAE45AA101XB12 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE P | AI | 0 | 100 | %
912 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201403.PNT | 2PDAS:FT201403.PNT | 20LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
214 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:PT193101.PNT | 2ODAS:PT193101.PNT | 20LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1135 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120101.PNT | 2IDAS:PT120101.PNT | 20LBA10CP202 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1143 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120201.PNT | 2IDAS:PT120201.PNT | 20LBA10CP203 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1151 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120301.PNT | 2IDAS:PT120301.PNT | 20LBA10CP204 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa
1117 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202806.PNT | 2PDAS:TE202806.PNT | 20LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | °C
1118 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE202807.PNT | 2PDAS:TE202807.PNT | 20LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | °C
1118 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER TUBE #20 |  | OPC.2MSTFLOW:CALCA2.RO01 | 2MSTFLOW:CALCA2.RO01 | 20LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h
1306 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254802.PNT | 2ODAS:TE254802.PNT | 20HAJ10CT001 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1307 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254803.PNT | 2ODAS:TE254803.PNT | 20HAJ10CT002 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1308 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254804.PNT | 2ODAS:TE254804.PNT | 20HAJ10CT003 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1309 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254805.PNT | 2ODAS:TE254805.PNT | 20HAJ10CT004 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1310 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254806.PNT | 2ODAS:TE254806.PNT | 20HAJ10CT005 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1312 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255102.PNT | 2ODAS:TE255102.PNT | 20HAJ10CT006 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1313 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255103.PNT | 2ODAS:TE255103.PNT | 20HAJ10CT007 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1314 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255104.PNT | 2ODAS:TE255104.PNT | 20HAJ10CT008 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1315 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255105.PNT | 2ODAS:TE255105.PNT | 20HAJ10CT009 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
1316 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE255106.PNT | 2ODAS:TE255106.PNT | 20HAJ10CT010 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FR | TC | 0 | 600 | °C
346 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193501.PNT | 2ODAS:TE193501.PNT | 20HAJ21CT001 | REHEATER DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1124 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203105.PNT | 2PDAS:TE203105.PNT | 20HAJ21CT002 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1125 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203106.PNT | 2PDAS:TE203106.PNT | 20HAJ21CT003 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
347 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193502.PNT | 2ODAS:TE193502.PNT | 20HAJ22CT001 | REHEATER DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1126 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203107.PNT | 2PDAS:TE203107.PNT | 20HAJ22CT002 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1127 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203108.PNT | 2PDAS:TE203108.PNT | 20HAJ22CT003 | REHEATER DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C
1289 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254506.PNT | 2ODAS:TE254506.PNT | 20HAK10CT001 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1290 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254507.PNT | 2ODAS:TE254507.PNT | 20HAK10CT002 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1296 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254606.PNT | 2ODAS:TE254606.PNT | 20HAK10CT003 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1297 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254607.PNT | 2ODAS:TE254607.PNT | 20HAK10CT004 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1303 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254706.PNT | 2ODAS:TE254706.PNT | 20HAK10CT005 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
1304 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-16 | OPC.2ODAS:TE254707.PNT | 2ODAS:TE254707.PNT | 20HAK10CT006 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER | TC | 0 | 600 | °C
218 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2ODAS:PT193105.PNT | 2ODAS:PT193105.PNT | 20LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa
349 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2ODAS:TE193504.PNT | 2ODAS:TE193504.PNT | 20LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | °C
1014 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2RHTDESUPEMG:AO202307.OUT | 2RHTDESUPEMG:AO202307.OUT | 20LAF61AA101XB11 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
909 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201308.PNT | 2PDAS:ZT201308.PNT | 20LAF61AA101XB12 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
908 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201307.PNT | 2PDAS:FT201307.PNT | 20LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1011 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2RHTDESUPA:AO202304.OUT | 2RHTDESUPA:AO202304.OUT | 20LAF62AA101XB11 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
905 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201304.PNT | 2PDAS:ZT201304.PNT | 20LAF62AA101XB12 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
902 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201301.PNT | 2PDAS:FT201301.PNT | 20LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
1018 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2RHTDESUPB:AO202404.OUT | 2RHTDESUPB:AO202404.OUT | 20LAF63AA101XB11 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | %
913 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:ZT201404.PNT | 2PDAS:ZT201404.PNT | 20LAF63AA101XB12 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
910 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-08 | OPC.2PDAS:FT201401.PNT | 2PDAS:FT201401.PNT | 20LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 60 | KPa
217 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:PT193104.PNT | 2ODAS:PT193104.PNT | 20LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa
348 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193503.PNT | 2ODAS:TE193503.PNT | 20LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | °C
215 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:PT193102.PNT | 2ODAS:PT193102.PNT | 20LBC21CP201 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
344 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193406.PNT | 2ODAS:TE193406.PNT | 20LBC21CT001 | REHEATER EMERGENCY DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1120 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203101.PNT | 2PDAS:TE203101.PNT | 20LBC21CT002 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1121 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203102.PNT | 2PDAS:TE203102.PNT | 20LBC21CT003 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
216 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:PT193103.PNT | 2ODAS:PT193103.PNT | 20LBC22CP201 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
345 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2ODAS:TE193407.PNT | 2ODAS:TE193407.PNT | 20LBC22CT001 | REHEATER EMERGENCY DESUPERHEATING INLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1122 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203103.PNT | 2PDAS:TE203103.PNT | 20LBC22CT002 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
1123 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEAT TUBE #20 | 50-F290S-J0201-04 | OPC.2PDAS:TE203104.PNT | 2PDAS:TE203104.PNT | 20LBC22CT003 | REHEATER EMERGENCY DESUPERHEATING OUTLET STEAM TEMPERATURE | TC | 0 | 400 | °C
239 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOTBLOWER #20 |  | OPC.2NDAS:AO183603.OUT | 2NDAS:AO183603.OUT | 20HCB00AA101XB11 | SOOT BLOWING STEAM SOURCE CONTROL SIGNAL | AO
204 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOTBLOWER #20 |  | OPC.2NDAS:ZT183405.PNT | 2NDAS:ZT183405.PNT | 20HCB00AA101XB12 | SOOT BLOWING STEAM SOURCE POSITION FEEDBACK OF REGULATING VALVE | AI | 0 | 100 | %
205 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOTBLOWER #20 |  | OPC.2NDAS:PT183406.PNT | 2NDAS:PT183406.PNT | 20HCB00CP201 | SOOT BLOWING STEAM SOURCE PRESSURE | AI | 0 | 10
920 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201503.PNT | 2PDAS:PT201503.PNT | 20H10CP201 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
927 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201603.PNT | 2PDAS:PT201603.PNT | 20H10CP202 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
165 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:PT163305.PNT | 2MDAS:PT163305.PNT | 20H10CP203 | A SIDE FURNACE PRESSURE | AI | -2 | 2 | KPa
166 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:PT163306.PNT | 2MDAS:PT163306.PNT | 20H10CP204 | A SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa
318 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162607.PNT | 2MDAS:TE162607.PNT | 20H10CT002 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
319 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162701.PNT | 2MDAS:TE162701.PNT | 20H10CT003 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
320 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162702.PNT | 2MDAS:TE162702.PNT | 20H10CT004 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
321 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162703.PNT | 2MDAS:TE162703.PNT | 20H10CT005 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
322 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162704.PNT | 2MDAS:TE162704.PNT | 20H10CT006 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | °C
323 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162705.PNT | 2MDAS:TE162705.PNT | 20H10CT007 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
324 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2MDAS:TE162706.PNT | 2MDAS:TE162706.PNT | 20H10CT008 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
919 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201502.PNT | 2PDAS:PT201502.PNT | 20H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
926 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201602.PNT | 2PDAS:PT201602.PNT | 20H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
1499 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F289S-K0503-02 | OPC.2QDAS:AI212501.PNT | 2QDAS:AI212501.PNT | 20H10GC001AI01 | SIDE A FURNACE FLUE GAS TEMPERATURE PROBE TEMPERATURE | AI | 0 | 580 | °C
1500 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F289S-K0503-02 | OPC.2QDAS:ZT212502.PNT | 2QDAS:ZT212502.PNT | 20H10GC001AI02 | SIDE A FURNACE FLUE GAS TEMPERATURE PROBE POSITION | AI | 0 | 100 | %
922 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201505.PNT | 2PDAS:PT201505.PNT | 20H20CP201 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
929 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201605.PNT | 2PDAS:PT201605.PNT | 20H20CP202 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa
197 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:PT183305.PNT | 2NDAS:PT183305.PNT | 20H20CP203 | B SIDE FURNACE PRESSURE | AI | -2 | 2 | KPa
198 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:PT183306.PNT | 2NDAS:PT183306.PNT | 20H20CP204 | B SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa
331 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182607.PNT | 2NDAS:TE182607.PNT | 20H20CT002 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
332 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182701.PNT | 2NDAS:TE182701.PNT | 20H20CT003 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
333 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182702.PNT | 2NDAS:TE182702.PNT | 20H20CT004 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
334 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182703.PNT | 2NDAS:TE182703.PNT | 20H20CT005 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
335 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182704.PNT | 2NDAS:TE182704.PNT | 20H20CT006 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | °C
336 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182705.PNT | 2NDAS:TE182705.PNT | 20H20CT007 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
337 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182706.PNT | 2NDAS:TE182706.PNT | 20H20CT008 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | °C
338 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2NDAS:TE182707.PNT | 2NDAS:TE182707.PNT | 20H20CT009 | B SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | °C
921 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201504.PNT | 2PDAS:PT201504.PNT | 20H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
928 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-34 | OPC.2PDAS:PT201604.PNT | 2PDAS:PT201604.PNT | 20H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
1501 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F289S-K0503-03 | OPC.2QDAS:AI212503.PNT | 2QDAS:AI212503.PNT | 20H20GC001AI01 | SIDE B FURNACE FLUE GAS TEMPERATURE PROBE TEMPERATURE | AI | 0 | 580 | °C
1502 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F289S-K0503-03 | OPC.2QDAS:ZT212504.PNT | 2QDAS:ZT212504.PNT | 20H20GC001AI02 | SIDE B FURNACE FLUE GAS TEMPERATURE PROBE POSITION | AI | 0 | 100 | %
889 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-02 | OPC.2PDAS:FT201101.PNT | 2PDAS:FT201101.PNT | 20HLA10CF201 | GAH A OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
890 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-02 | OPC.2PDAS:FT201102.PNT | 2PDAS:FT201102.PNT | 20HLA10CF202 | GAH A OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
896 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-02 | OPC.2PDAS:FT201201.PNT | 2PDAS:FT201201.PNT | 20HLA20CF201 | GAH B OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
897 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F290S-J0201-02 | OPC.2PDAS:FT201202.PNT | 2PDAS:FT201202.PNT | 20HLA20CF202 | GAH B OUTLET SECONDARY AIR FLOW | AI | 0 | 0.45
1870 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.FURPRESS:AINFURPRE.PNT | FURPRESS:AINFURPRE.PNT | 20H10CP201C1 | FURNACE PRESSURE | AI | -2500 | 2500 | Pa
1874 | 1 | UJRBG #20 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.FUELMASTER:AINCOAL.PNT | FUELMASTER:AINCOAL.PNT | 20HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
996 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-02 | OPC.2PAFLOW:AO202105.OUT | 2PAFLOW:AO202105.OUT | 20HFE10AA101XB11 | PAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
892 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT201105.PNT | 2PDAS:ZT201105.PNT | 20HFE10AA101XB12 | PAF A INLET VANE POSITION | AI | 0 | 100 | %
159 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-02 | OPC.2MDAS:CT163206.PNT | 2MDAS:CT163206.PNT | 20HFE10AN001XB13 | PAF A CURRENT | AI | 0 | 250 | A
150 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163104.PNT | 2MDAS:PT163104.PNT | 20HFE10CP201 | PAF A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
313 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-02 | OPC.2MDAS:TE162602.PNT | 2MDAS:TE162602.PNT | 20HFE10CT001 | PAF A INLET AIR TEMPERATURE | TC | 0 | 100 | °C
255 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162301.PNT | 2MDAS:RT162301.PNT | 20HFE10CT006 | PAF A MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | °C
256 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162302.PNT | 2MDAS:RT162302.PNT | 20HFE10CT007 | PAF A MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | °C
257 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162303.PNT | 2MDAS:RT162303.PNT | 20HFE10CT008 | PAF A MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | °C
258 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162304.PNT | 2MDAS:RT162304.PNT | 20HFE10CT009 | PAF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C
259 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162305.PNT | 2MDAS:RT162305.PNT | 20HFE10CT010 | PAF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162306.PNT | 2MDAS:RT162306.PNT | 20HFE10CT011 | PAF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2MDAS:RT162307.PNT | 2MDAS:RT162307.PNT | 20HFE10CT012 | PAF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2VMS:AIN1.PNT | 2VMS:AIN1.PNT | 20HFE20CY001X | #20 PAF A BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2VMS:AIN2.PNT | 2VMS:AIN2.PNT | 20HFE20CY001Y | #20 PAF A BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2VMS:AIN3.PNT | 2VMS:AIN3.PNT | 20HFE20CY002X | #20 PAF A BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #20A | 50-F290S-J0201-37 | OPC.2VMS:AIN4.PNT | 2VMS:AIN4.PNT | 20HFE20CY002Y | #20 PAF A BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
147 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163101.PNT | 2MDAS:PT163101.PNT | 20HLA10CP201 | FDF A OUTLET AIR PRESSURE | AI | 0 | 5 | KPa
312 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:TE162601.PNT | 2MDAS:TE162601.PNT | 20HLA10CT001 | FDF A INLET AIR TEMPERATURE | TC | 0 | 100 | °C
995 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-02 | OPC.2AIRFLOW:AO202104.OUT | 2AIRFLOW:AO202104.OUT | 20HLB10AA101XB11 | FDF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
891 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT201104.PNT | 2PDAS:ZT201104.PNT | 20HLB10AA101XB12 | FDF A INLET VANE POSITION | AI | 0 | 100 | %
158 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:CT163205.PNT | 2MDAS:CT163205.PNT | 20HLB10AN001XB13 | FDF A CURRENT | AI | 0 | 75 | A
241 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162101.PNT | 2MDAS:RT162101.PNT | 20HLB10CT001 | FDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
248 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162201.PNT | 2MDAS:RT162201.PNT | 20HLB10CT002 | FDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
242 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162102.PNT | 2MDAS:RT162102.PNT | 20HLB10CT003 | FDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
249 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162202.PNT | 2MDAS:RT162202.PNT | 20HLB10CT004 | FDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
243 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162103.PNT | 2MDAS:RT162103.PNT | 20HLB10CT005 | FDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
250 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162203.PNT | 2MDAS:RT162203.PNT | 20HLB10CT006 | FDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
244 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162104.PNT | 2MDAS:RT162104.PNT | 20HLB10CT007 | FDF A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C
251 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162204.PNT | 2MDAS:RT162204.PNT | 20HLB10CT008 | FDF A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C
245 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162105.PNT | 2MDAS:RT162105.PNT | 20HLB10CT009 | FDF A BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
252 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162205.PNT | 2MDAS:RT162205.PNT | 20HLB10CT010 | FDF A BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
246 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162106.PNT | 2MDAS:RT162106.PNT | 20HLB10CT011 | FDF A BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
253 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162206.PNT | 2MDAS:RT162206.PNT | 20HLB10CT012 | FDF A BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
247 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162107.PNT | 2MDAS:RT162107.PNT | 20HLB10CT013 | FDF A BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
254 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2MDAS:RT162207.PNT | 2MDAS:RT162207.PNT | 20HLB10CT014 | FDF A BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2VMS:AIN9.PNT | 2VMS:AIN9.PNT | 20HLB10CY001X | #20 FDF A BR VIBE H (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2VMS:AIN10.PNT | 2VMS:AIN10.PNT | 20HLB10CY001Y | #20 FDF A BR VIBE H (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2VMS:AIN11.PNT | 2VMS:AIN11.PNT | 20HLB10CY002X | #20 FDF A BR VIBE H (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #20A | 50-F290S-J0201-36 | OPC.2VMS:AIN12.PNT | 2VMS:AIN12.PNT | 20HLB10CY002Y | #20 FDF A BR VIBE H (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
999 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A |  | OPC.2APHCUR:AO202108.OUT | 2APHCUR:AO202108.OUT | 20CFF01DCSAO01 | AIR PRE-HEATER A MAIN AND AUXILIARY MOTOR CURRENT SELECTION LARGE OUTPUT | AO | 0 | 100 | %
151 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163105.PNT | 2MDAS:PT163105.PNT | 20HFE10CP202 | GAH A INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
152 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163106.PNT | 2MDAS:PT163106.PNT | 20HFE10CP203 | GAH A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
1132 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2QDAS:TE212201.PNT | 2QDAS:TE212201.PNT | 20HFE10CT002 | GAH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | °C
1133 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2QDAS:TE212204.PNT | 2QDAS:TE212204.PNT | 20HFE10CT005 | GAH A OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | °C
148 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163102.PNT | 2MDAS:PT163102.PNT | 20HLA10CP202 | GAH A INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
149 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163103.PNT | 2MDAS:PT163103.PNT | 20HLA10CP203 | GAH A OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
1128 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2QDAS:TE212101.PNT | 2QDAS:TE212101.PNT | 20HLA10CT002 | GAH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | °C
1129 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2QDAS:TE212104.PNT | 2QDAS:TE212104.PNT | 20HLA10CT005 | GAH A OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | °C
161 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:CT163301.PNT | 2MDAS:CT163301.PNT | 20HLD11GC001AI01 | AIR PRE-HEATER A MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
162 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:CT163302.PNT | 2MDAS:CT163302.PNT | 20HLD11GC001AI02 | AIR PRE-HEATER A AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
163 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:AI163303.PNT | 2MDAS:AI163303.PNT | 20HLD11GC001AI03 | AIR PRE-HEATER A MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 100 | %
164 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:AI163304.PNT | 2MDAS:AI163304.PNT | 20HLD11GC001AI04 | AIR PRE-HEATER A AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 100 | %
235 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:AO163601.OUT | 2MDAS:AO163601.OUT | 20HLD11GC001AO01 | AIR PRE-HEATER A MAIN MOTOR ROTATIONAL SPEED PRESET | AO
236 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:AO163602.OUT | 2MDAS:AO163602.OUT | 20HLD11GC001AO02 | AIR PRE-HEATER A AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO
155 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163202.PNT | 2MDAS:PT163202.PNT | 20HNA10CP202 | GAH A OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa
1105 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20A | 50-F290S-J0201-02 | OPC.2PDAS:TE202606.PNT | 2PDAS:TE202606.PNT | 20HNA10CT002 | GAH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | °C
867 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F290S-J0201-02 | OPC.2PDAS:PT200601.PNT | 2PDAS:PT200601.PNT | 20HFE50CP201 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
873 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F290S-J0201-02 | OPC.2PDAS:PT200701.PNT | 2PDAS:PT200701.PNT | 20HFE50CP202 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
881 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F290S-J0201-02 | OPC.2PDAS:PT200801.PNT | 2PDAS:PT200801.PNT | 20HFE50CP203 | GAH OUTLET PRIMARY AIR HEADER PRESSURE | AI | 0 | 20 | KPa
191 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-02 | OPC.2NDAS:CT183206.PNT | 2NDAS:CT183206.PNT | 20HFE20AN001XB13 | PAF B CURRENT | AI | 0 | 250 | A
183 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183104.PNT | 2NDAS:PT183104.PNT | 20HFE20CP201 | PAF B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
327 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-02 | OPC.2NDAS:TE182602.PNT | 2NDAS:TE182602.PNT | 20HFE20CT001 | PAF B INLET AIR TEMPERATURE | TC | 0 | 100 | °C
291 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182301.PNT | 2NDAS:RT182301.PNT | 20HFE20CT006 | PAF B MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | °C
292 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182302.PNT | 2NDAS:RT182302.PNT | 20HFE20CT007 | PAF B MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | °C
293 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182303.PNT | 2NDAS:RT182303.PNT | 20HFE20CT008 | PAF B MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | °C
294 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182304.PNT | 2NDAS:RT182304.PNT | 20HFE20CT009 | PAF B MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C
295 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182305.PNT | 2NDAS:RT182305.PNT | 20HFE20CT010 | PAF B MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 150 | °C
296 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182306.PNT | 2NDAS:RT182306.PNT | 20HFE20CT011 | PAF B BEARING TEMPERATURE 1 | RTD | 0 | 150 | °C |  |  |  | 80 | 85
297 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2NDAS:RT182307.PNT | 2NDAS:RT182307.PNT | 20HFE20CT012 | PAF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 80 | 85
1004 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-02 | OPC.2PAFLOW:AO202205.OUT | 2PAFLOW:AO202205.OUT | 20HFE20HB001XB11 | PAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
899 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT201205.PNT | 2PDAS:ZT201205.PNT | 20HFE20HB001XB12 | PAF B INLET VANE POSITION | AI | 0 | 100 | %
899 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2VMS:AIN5.PNT | 2VMS:AIN5.PNT | 20HFE20CY001X | #20 PAF B BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2VMS:AIN6.PNT | 2VMS:AIN6.PNT | 20HFE20CY001Y | #20 PAF B BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2VMS:AIN7.PNT | 2VMS:AIN7.PNT | 20HFE20CY002X | #20 PAF B BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
899 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #20B | 50-F290S-J0201-37 | OPC.2VMS:AIN8.PNT | 2VMS:AIN8.PNT | 20HFE20CY002Y | #20 PAF B BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
180 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183101.PNT | 2NDAS:PT183101.PNT | 20HLA20CP201 | FDF B OUTLET AIR PRESSURE | AI | 0 | 5 | KPa
326 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:TE182601.PNT | 2NDAS:TE182601.PNT | 20HLA20CT001 | FDF B INLET AIR TEMPERATURE | TC | 0 | 100 | °C
1003 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-02 | OPC.2AIRFLOW:AO202204.OUT | 2AIRFLOW:AO202204.OUT | 20HLB20AA101XB11 | FDF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | %
898 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT201204.PNT | 2PDAS:ZT201204.PNT | 20HLB20AA101XB12 | FDF B INLET VANE POSITION | AI | 0 | 100 | %
190 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:CT183205.PNT | 2NDAS:CT183205.PNT | 20HLB20AN001XB13 | FDF B CURRENT | AI | 0 | 75 | A
276 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182101.PNT | 2NDAS:RT182101.PNT | 20HLB20CT001 | FDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
284 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182201.PNT | 2NDAS:RT182201.PNT | 20HLB20CT002 | FDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
277 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182102.PNT | 2NDAS:RT182102.PNT | 20HLB20CT003 | FDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
285 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182202.PNT | 2NDAS:RT182202.PNT | 20HLB20CT004 | FDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
278 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182103.PNT | 2NDAS:RT182103.PNT | 20HLB20CT005 | FDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
286 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182203.PNT | 2NDAS:RT182203.PNT | 20HLB20CT006 | FDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
279 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182104.PNT | 2NDAS:RT182104.PNT | 20HLB20CT007 | FDF B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | °C
287 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182204.PNT | 2NDAS:RT182204.PNT | 20HLB20CT008 | FDF B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | °C
280 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182105.PNT | 2NDAS:RT182105.PNT | 20HLB20CT009 | FDF B BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
288 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182205.PNT | 2NDAS:RT182205.PNT | 20HLB20CT010 | FDF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
281 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182106.PNT | 2NDAS:RT182106.PNT | 20HLB20CT011 | FDF B BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
289 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182206.PNT | 2NDAS:RT182206.PNT | 20HLB20CT012 | FDF B BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
282 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182107.PNT | 2NDAS:RT182107.PNT | 20HLB20CT013 | FDF B BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
290 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2NDAS:RT182207.PNT | 2NDAS:RT182207.PNT | 20HLB20CT014 | FDF B BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2VMS:AIN13.PNT | 2VMS:AIN13.PNT | 20HLB20CY001X | #20 FDF B BR VIBE H (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2VMS:AIN14.PNT | 2VMS:AIN14.PNT | 20HLB20CY001Y | #20 FDF B BR VIBE H (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2VMS:AIN15.PNT | 2VMS:AIN15.PNT | 20HLB20CY002X | #20 FDF B BR VIBE H (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #20B | 50-F290S-J0201-36 | OPC.2VMS:AIN16.PNT | 2VMS:AIN16.PNT | 20HLB20CY002Y | #20 FDF B BR VIBE H (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
1007 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B |  | OPC.2APHCUR:AO202208.OUT | 2APHCUR:AO202208.OUT | 20CFF01DCSAO02 | AIR PRE-HEATER B MAIN AND AUXILIARY MOTOR CURRENT SELECTION LARGE OUTPUT | AO | 0 | 100 | %
184 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183105.PNT | 2NDAS:PT183105.PNT | 20HFE20CP202 | GAH B INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
185 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183106.PNT | 2NDAS:PT183106.PNT | 20HFE20CP203 | GAH B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa
1134 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2QDAS:TE212205.PNT | 2QDAS:TE212205.PNT | 20HFE20CT002 | GAH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | °C
1089 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2QDAS:TE212208.PNT | 2QDAS:TE212208.PNT | 20HFE20CT005 | GAH B OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | °C
181 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183102.PNT | 2NDAS:PT183102.PNT | 20HLA20CP202 | GAH B INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
182 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183103.PNT | 2NDAS:PT183103.PNT | 20HLA20CP203 | GAH B OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa
1130 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2QDAS:TE212105.PNT | 2QDAS:TE212105.PNT | 20HLA20CT002 | GAH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | °C
1131 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2QDAS:TE212108.PNT | 2QDAS:TE212108.PNT | 20HLA20CT005 | GAH B OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | °C
193 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:CT183301.PNT | 2NDAS:CT183301.PNT | 20HLD12GC001AI01 | AIR PRE-HEATER B MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
194 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:CT183302.PNT | 2NDAS:CT183302.PNT | 20HLD12GC001AI02 | AIR PRE-HEATER B AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A
195 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:AI183303.PNT | 2NDAS:AI183303.PNT | 20HLD12GC001AI03 | AIR PRE-HEATER B MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1
196 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:AI183304.PNT | 2NDAS:AI183304.PNT | 20HLD12GC001AI04 | AIR PRE-HEATER B AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1
237 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:AO183601.OUT | 2NDAS:AO183601.OUT | 20HLD12GC001AO01 | AIR PRE-HEATER B MAIN MOTOR ROTATIONAL SPEED PRESET | AO
238 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:AO183602.OUT | 2NDAS:AO183602.OUT | 20HLD12GC001AO02 | AIR PRE-HEATER B AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO
187 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183202.PNT | 2NDAS:PT183202.PNT | 20HNA20CP202 | GAH B OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa
1106 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | VERTICAL LJUNGSTROM AIR HEATER SYSTEM #20B | 50-F290S-J0201-02 | OPC.2PDAS:TE202701.PNT | 2PDAS:TE202701.PNT | 20HNA20CT002 | GAH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
156 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163203.PNT | 2MDAS:PT163203.PNT | 20HNA11CP201 | ESP A OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa
315 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:TE162604.PNT | 2MDAS:TE162604.PNT | 20HNA11CT001 | ESP A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
157 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:PT163204.PNT | 2MDAS:PT163204.PNT | 20HNA12CP201 | IDF A OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa
316 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:TE162605.PNT | 2MDAS:TE162605.PNT | 20HNA12CT001 | IDF A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
998 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2FURPRESS:AO202107.OUT | 2FURPRESS:AO202107.OUT | 20HNC11AA101XB11 | IDF A INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | %
894 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2PDAS:ZT201107.PNT | 2PDAS:ZT201107.PNT | 20HNC11AA101XB12 | IDF A INLET STATIONARY BLADE POSITION | AI | 0 | 100 | %
160 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-02 | OPC.2MDAS:CT163207.PNT | 2MDAS:CT163207.PNT | 20HNC11AN001XB13 | IDF A CURRENT | AI | 0 | 300 | A
168 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:CT163401.PNT | 2MDAS:CT163401.PNT | 20HNC11AN002XB13 | IDF A #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
169 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:CT163402.PNT | 2MDAS:CT163402.PNT | 20HNC11AN003XB13 | IDF A #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
262 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162401.PNT | 2MDAS:RT162401.PNT | 20HNC11CT001 | IDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
269 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162501.PNT | 2MDAS:RT162501.PNT | 20HNC11CT002 | IDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
263 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162402.PNT | 2MDAS:RT162402.PNT | 20HNC11CT003 | IDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
270 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162502.PNT | 2MDAS:RT162502.PNT | 20HNC11CT004 | IDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
264 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162403.PNT | 2MDAS:RT162403.PNT | 20HNC11CT005 | IDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
271 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162503.PNT | 2MDAS:RT162503.PNT | 20HNC11CT006 | IDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
265 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162404.PNT | 2MDAS:RT162404.PNT | 20HNC11CT007 | IDF A MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C
272 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162504.PNT | 2MDAS:RT162504.PNT | 20HNC11CT008 | IDF A MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C
266 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162405.PNT | 2MDAS:RT162405.PNT | 20HNC11CT009 | IDF A BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
273 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162505.PNT | 2MDAS:RT162505.PNT | 20HNC11CT010 | IDF A BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
267 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162406.PNT | 2MDAS:RT162406.PNT | 20HNC11CT011 | IDF A BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
274 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162506.PNT | 2MDAS:RT162506.PNT | 20HNC11CT012 | IDF A BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
268 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162407.PNT | 2MDAS:RT162407.PNT | 20HNC11CT013 | IDF A BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
275 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2MDAS:RT162507.PNT | 2MDAS:RT162507.PNT | 20HNC11CT014 | IDF A BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2VMS:AIN17.PNT | 2VMS:AIN17.PNT | 20HNC11CY001X | #20 IDF A BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2VMS:AIN18.PNT | 2VMS:AIN18.PNT | 20HNC11CY001Y | #20 IDF A BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2VMS:AIN19.PNT | 2VMS:AIN19.PNT | 20HNC11CY002X | #20 IDF A BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #20A | 50-F290S-J0201-38 | OPC.2VMS:AIN20.PNT | 2VMS:AIN20.PNT | 20HNC11CY002Y | #20 IDF A BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
188 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183203.PNT | 2NDAS:PT183203.PNT | 20HNA21CP201 | ESP B OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa
329 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:TE182604.PNT | 2NDAS:TE182604.PNT | 20HNA21CT001 | ESP B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
189 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:PT183204.PNT | 2NDAS:PT183204.PNT | 20HNA22CP201 | IDF B OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa
330 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:TE182605.PNT | 2NDAS:TE182605.PNT | 20HNA22CT001 | IDF B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | °C
1006 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2FURPRESS:AO202207.OUT | 2FURPRESS:AO202207.OUT | 20HNC21AA101XB11 | IDF B INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | %
901 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2PDAS:ZT201207.PNT | 2PDAS:ZT201207.PNT | 20HNC21AA101XB12 | IDF B INLET STATIONARY BLADE POSITION | AI | 0 | 100 | %
192 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-02 | OPC.2NDAS:CT183207.PNT | 2NDAS:CT183207.PNT | 20HNC21AN001XB13 | IDF B CURRENT | AI | 0 | 300 | A
200 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:CT183401.PNT | 2NDAS:CT183401.PNT | 20HNC21AN002XB13 | IDF B #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
201 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:CT183402.PNT | 2NDAS:CT183402.PNT | 20HNC21AN003XB13 | IDF B #2 COOLING FAN MOTOR CURRENT | AI | 0 | 100 | A
298 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182401.PNT | 2NDAS:RT182401.PNT | 20HNC21CT001 | IDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | °C
305 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182501.PNT | 2NDAS:RT182501.PNT | 20HNC21CT002 | IDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | °C
299 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182402.PNT | 2NDAS:RT182402.PNT | 20HNC21CT003 | IDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | °C
306 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182502.PNT | 2NDAS:RT182502.PNT | 20HNC21CT004 | IDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | °C
300 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182403.PNT | 2NDAS:RT182403.PNT | 20HNC21CT005 | IDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | °C
307 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182503.PNT | 2NDAS:RT182503.PNT | 20HNC21CT006 | IDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | °C
301 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182404.PNT | 2NDAS:RT182404.PNT | 20HNC21CT007 | IDF B MOTOR BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C
308 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182504.PNT | 2NDAS:RT182504.PNT | 20HNC21CT008 | IDF B MOTOR BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C
302 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182405.PNT | 2NDAS:RT182405.PNT | 20HNC21CT009 | IDF B BEARING TEMPERATURE 1 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
309 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182505.PNT | 2NDAS:RT182505.PNT | 20HNC21CT010 | IDF B BEARING TEMPERATURE 2 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
303 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182406.PNT | 2NDAS:RT182406.PNT | 20HNC21CT011 | IDF B BEARING TEMPERATURE 3 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
310 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182506.PNT | 2NDAS:RT182506.PNT | 20HNC21CT012 | IDF B BEARING TEMPERATURE 4 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
304 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182407.PNT | 2NDAS:RT182407.PNT | 20HNC21CT013 | IDF B BEARING TEMPERATURE 5 | RTD | 0 | 100 | °C
311 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2NDAS:RT182507.PNT | 2NDAS:RT182507.PNT | 20HNC21CT014 | IDF B BEARING TEMPERATURE 6 | RTD | 0 | 100 | °C |  |  |  | 90 | 95
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2VMS:AIN21.PNT | 2VMS:AIN21.PNT | 20HNC21CY001X | #20 IDF B BEARING VIB (DE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2VMS:AIN22.PNT | 2VMS:AIN22.PNT | 20HNC21CY001Y | #20 IDF B BEARING VIB (DE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
260 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2VMS:AIN23.PNT | 2VMS:AIN23.PNT | 20HNC21CY002X | #20 IDF B BEARING VIB (NDE,X) | AI | 0 | 20 | mm/s |  |  |  | 6.3
261 | 1 | UJRBG #20 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #20B | 50-F290S-J0201-38 | OPC.2VMS:AIN24.PNT | 2VMS:AIN24.PNT | 20HNC21CY002Y | #20 IDF B BEARING VIB (NDE,Y) | AI | 0 | 20 | mm/s |  |  |  | 6.3
417 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50-F290S-J0201-19 | OPC.2FDAS:PT073203.PNT | 2FDAS:PT073203.PNT | 20MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa
451 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50-F290S-J0201-25 | OPC.2FDAS:LT073608.PNT | 2FDAS:LT073608.PNT | 20MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 900 | mm |  |  | 340 | 810
443 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50-F290S-J0201-25 | OPC.2FDAS:PT073508.PNT | 2FDAS:PT073508.PNT | 20MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 0.4 | MPa
747 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50-F290S-J0201-25 | OPC.2FDAS:TE070802.PNT | 2FDAS:TE070802.PNT | 20MKW10CT003 | GENERATOR EXCITER SIDE H2 SIDE SEAL RETURN OIL TEMP | TC | 0 | 100 | °C
377 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50- | OPC.2EDAS:CT050803.PNT | 2EDAS:CT050803.PNT | 20MKW20AP101XB13 | GENERATOR H2 SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 100 | %
673 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL-H2 SIDE #20A | 50-F290S-J0201-25 | OPC.2FDAS:RT073805.PNT | 2FDAS:RT073805.PNT | 20MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | °C
1243 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #20A | F296S-J0201-25 | OPC.2FDAS:TE070801.PNT | 2FDAS:TE070801.PNT | 20MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C
378 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #20B | 50- | OPC.2EDAS:CT050804.PNT | 2EDAS:CT050804.PNT | 20MKW20AP102XB13 | GENERATOR H3 SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 100 | %
499 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 5 | GENERATOR SEAL OIL #20 - AIR SIDE DC EMERGENCY PUMP | 50- | OPC.2GDAS:CT092707.PNT | 2GDAS:CT092707.PNT | 20MKW10AP103XB13 | GENERATOR AIR SIDE DC EMERGENCY SEAL OIL PUMP CURRENT | AI | 0 | 105 | %
1260 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2GESTAT:AO122605.OUT | 2GESTAT:AO122605.OUT | 20MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1219 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2IDAS:ZT121404.PNT | 2IDAS:ZT121404.PNT | 20MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | %
424 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:CT073303.PNT | 2FDAS:CT073303.PNT | 20MKF10AP001XB13 | GENERATOR STATOR COOLING WATER PUMP A CURRENT | AI | 0 | 100 | %
433 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:FT073405.PNT | 2FDAS:FT073405.PNT | 20MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 45 | t/h
434 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:AI073406.PNT | 2FDAS:AI073406.PNT | 20MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2
435 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:AI073407.PNT | 2FDAS:AI073407.PNT | 20MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5
1263 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2IDAS:RT121602.PNT | 2IDAS:RT121602.PNT | 20MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | °C |  |  | 42 | 48
427 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:PT073306.PNT | 2FDAS:PT073306.PNT | 20MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.6 | MPa
428 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:PT073307.PNT | 2FDAS:PT073307.PNT | 20MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.6 | MPa
669 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-24 | OPC.2FDAS:RT073801.PNT | 2FDAS:RT073801.PNT | 20MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | °C |  |  |  | 80
660 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #20A | 50-F290S-J0201-14 | OPC.2EDAS:RT067805.PNT | 2EDAS:RT067805.PNT | 20PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | °C
431 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #20B | 50-F290S-J0201-24 | OPC.2FDAS:CT073403.PNT | 2FDAS:CT073403.PNT | 20MKF10AP002XB13 | GENERATOR STATOR COOLING WATER PUMP B CURRENT | AI | 0 | 100 | %
1267 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_6 | 2ATC:2BD117AIN.PNT_6 | 20MKA00CT0143 | GENERATOR TURBINE SIDE BABBIT TEMP | RTD | 0 | 120 | C
1268 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_5 | 2ATC:2BD115AIN.PNT_5 | 20MKA00CT0144 | GENERATOR TURBINE SIDE BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1269 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_7 | 2ATC:2BD104AIN.PNT_7 | 20TSIDEH16 | SHAFT NO.5 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1270 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_8 | 2ATC:2BD104AIN.PNT_8 | 20TSIDEH17 | SHAFT NO.5 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1271 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_7 | 2ATC:2BD105AIN.PNT_7 | 20TSIDEH24 | BEARING COVER NO.5 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1272 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_7 | 2ATC:2BD117AIN.PNT_7 | 20MKA00CT0146 | GENERATOR COLECTOR SIDE BABBIT TEMP | RTD | 0 | 120 | C
1273 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_6 | 2ATC:2BD115AIN.PNT_6 | 20MKA00CT0147 | GENERATOR COLECTOR SIDE BEARING RETURN OIL TEMP | RTD | 0 | 120 | C
1274 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_1 | 2ATC:2BD105AIN.PNT_1 | 20TSIDEH18 | SHAFT NO.6 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1275 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_2 | 2ATC:2BD105AIN.PNT_2 | 20TSIDEH19 | SHAFT NO.6 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1276 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_8 | 2ATC:2BD105AIN.PNT_8 | 20TSIDEH25 | BEARING COVER NO.6 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1261 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F289S-K0606-01 | OPC.2CCSDMD:AO122606.OUT | 2CCSDMD:AO122606.OUT | 20DCSDEH01 | CCS DEMAND 1 | AO | 0 | 100 | %
1255 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F289S-K0606-01 | OPC.2CCSDMD:AO122507.OUT | 2CCSDMD:AO122507.OUT | 20DCSDEH02 | CCS DEMAND 2 | AO | 0 | 100 | %
1221 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F289S-K0606-01 | OPC.2IDAS:AI121406.PNT | 2IDAS:AI121406.PNT | 20DEHDCS02 | GENERATOR LOAD | AI | 0 | 400 | MW |  | 0 | 0 | 350 | 400
1348 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245101.PNT | 2HDAS:TE245101.PNT | 20MKA00CT001 | GENERATOR STATOR COIL OUTLET WATER TEMP 1 | RTD | 0 | 500 | °C
1349 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245102.PNT | 2HDAS:TE245102.PNT | 20MKA00CT002 | GENERATOR STATOR COIL OUTLET WATER TEMP 2 | RTD | 0 | 500 | °C
1350 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245103.PNT | 2HDAS:TE245103.PNT | 20MKA00CT003 | GENERATOR STATOR COIL OUTLET WATER TEMP 3 | RTD | 0 | 500 | °C
1351 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245104.PNT | 2HDAS:TE245104.PNT | 20MKA00CT004 | GENERATOR STATOR COIL OUTLET WATER TEMP 4 | RTD | 0 | 500 | °C
1352 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245105.PNT | 2HDAS:TE245105.PNT | 20MKA00CT005 | GENERATOR STATOR COIL OUTLET WATER TEMP 5 | RTD | 0 | 500 | °C
1353 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245106.PNT | 2HDAS:TE245106.PNT | 20MKA00CT006 | GENERATOR STATOR COIL OUTLET WATER TEMP 6 | RTD | 0 | 500 | °C
1354 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245107.PNT | 2HDAS:TE245107.PNT | 20MKA00CT007 | GENERATOR STATOR COIL OUTLET WATER TEMP 7 | RTD | 0 | 500 | °C
1355 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245108.PNT | 2HDAS:TE245108.PNT | 20MKA00CT008 | GENERATOR STATOR COIL OUTLET WATER TEMP 8 | RTD | 0 | 500 | °C
1356 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245201.PNT | 2HDAS:TE245201.PNT | 20MKA00CT009 | GENERATOR STATOR COIL OUTLET WATER TEMP 9 | RTD | 0 | 500 | °C
1357 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245202.PNT | 2HDAS:TE245202.PNT | 20MKA00CT010 | GENERATOR STATOR COIL OUTLET WATER TEMP 10 | RTD | 0 | 500 | °C
1447 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246606.PNT | 2HDAS:TE246606.PNT | 20MKA00CT0100 | GENERATOR STATOR BARS TEMP 46 | RTD | 0 | 500 | °C
1448 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246607.PNT | 2HDAS:TE246607.PNT | 20MKA00CT0101 | GENERATOR STATOR BARS TEMP 47 | RTD | 0 | 500 | °C
1449 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246608.PNT | 2HDAS:TE246608.PNT | 20MKA00CT0102 | GENERATOR STATOR BARS TEMP 48 | RTD | 0 | 500 | °C
1450 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246701.PNT | 2HDAS:TE246701.PNT | 20MKA00CT0103 | GENERATOR STATOR BARS TEMP 49 | RTD | 0 | 500 | °C
1451 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246702.PNT | 2HDAS:TE246702.PNT | 20MKA00CT0104 | GENERATOR STATOR BARS TEMP 50 | RTD | 0 | 500 | °C
1452 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246703.PNT | 2HDAS:TE246703.PNT | 20MKA00CT0105 | GENERATOR STATOR BARS TEMP 51 | RTD | 0 | 500 | °C
1453 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246704.PNT | 2HDAS:TE246704.PNT | 20MKA00CT0106 | GENERATOR STATOR BARS TEMP 52 | RTD | 0 | 500 | °C
1454 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246705.PNT | 2HDAS:TE246705.PNT | 20MKA00CT0107 | GENERATOR STATOR BARS TEMP 53 | RTD | 0 | 500 | °C
1455 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246706.PNT | 2HDAS:TE246706.PNT | 20MKA00CT0108 | GENERATOR STATOR BARS TEMP 54 | RTD | 0 | 500 | °C
1456 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247101.PNT | 2HDAS:TE247101.PNT | 20MKA00CT0109 | GENERATOR STATOR CORE TEMP 1 | RTD | 0 | 500 | °C
1358 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245203.PNT | 2HDAS:TE245203.PNT | 20MKA00CT011 | GENERATOR STATOR COIL OUTLET WATER TEMP 11 | RTD | 0 | 500 | °C
1457 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247102.PNT | 2HDAS:TE247102.PNT | 20MKA00CT0110 | GENERATOR STATOR CORE TEMP 2 | RTD | 0 | 500 | °C
1458 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247103.PNT | 2HDAS:TE247103.PNT | 20MKA00CT0111 | GENERATOR STATOR CORE TEMP 3 | RTD | 0 | 500 | °C
1459 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247104.PNT | 2HDAS:TE247104.PNT | 20MKA00CT0112 | GENERATOR STATOR CORE TEMP 4 | RTD | 0 | 500 | °C
1460 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247105.PNT | 2HDAS:TE247105.PNT | 20MKA00CT0113 | GENERATOR STATOR CORE TEMP 5 | RTD | 0 | 500 | °C
1461 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247106.PNT | 2HDAS:TE247106.PNT | 20MKA00CT0114 | GENERATOR STATOR CORE TEMP 6 | RTD | 0 | 500 | °C
1464 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247201.PNT | 2HDAS:TE247201.PNT | 20MKA00CT0115 | GENERATOR STATOR CORE TEMP 7 | RTD | 0 | 500 | °C
1465 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247202.PNT | 2HDAS:TE247202.PNT | 20MKA00CT0116 | GENERATOR STATOR CORE TEMP 8 | RTD | 0 | 500 | °C
1466 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247203.PNT | 2HDAS:TE247203.PNT | 20MKA00CT0117 | GENERATOR STATOR CORE TEMP 9 | RTD | 0 | 500 | °C
1467 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247204.PNT | 2HDAS:TE247204.PNT | 20MKA00CT0118 | GENERATOR STATOR CORE TEMP 10 | RTD | 0 | 500 | °C
1468 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247205.PNT | 2HDAS:TE247205.PNT | 20MKA00CT0119 | GENERATOR STATOR CORE TEMP 11 | RTD | 0 | 500 | °C
1359 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245204.PNT | 2HDAS:TE245204.PNT | 20MKA00CT012 | GENERATOR STATOR COIL OUTLET WATER TEMP 12 | RTD | 0 | 500 | °C
1469 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247206.PNT | 2HDAS:TE247206.PNT | 20MKA00CT0120 | GENERATOR STATOR CORE TEMP 12 | RTD | 0 | 500 | °C
1472 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247301.PNT | 2HDAS:TE247301.PNT | 20MKA00CT0121 | GENERATOR STATOR CORE TEMP 13 | RTD | 0 | 500 | °C
1473 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247302.PNT | 2HDAS:TE247302.PNT | 20MKA00CT0122 | GENERATOR STATOR CORE TEMP 14 | RTD | 0 | 500 | °C
1474 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247303.PNT | 2HDAS:TE247303.PNT | 20MKA00CT0123 | GENERATOR STATOR CORE TEMP 15 | RTD | 0 | 500 | °C
1475 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247304.PNT | 2HDAS:TE247304.PNT | 20MKA00CT0124 | GENERATOR STATOR CORE TEMP 16 | RTD | 0 | 500 | °C
1476 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247305.PNT | 2HDAS:TE247305.PNT | 20MKA00CT0125 | GENERATOR STATOR CORE TEMP 17 | RTD | 0 | 500 | °C
1477 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247306.PNT | 2HDAS:TE247306.PNT | 20MKA00CT0126 | GENERATOR STATOR CORE TEMP 18 | RTD | 0 | 500 | °C
1479 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247402.PNT | 2HDAS:TE247402.PNT | 20MKA00CT0127 | GENERATOR COLD/HOT H2 TEMP 1 | RTD | 0 | 500 | °C
1480 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247403.PNT | 2HDAS:TE247403.PNT | 20MKA00CT0128 | GENERATOR COLD/HOT H2 TEMP 2 | RTD | 0 | 500 | °C
1481 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247404.PNT | 2HDAS:TE247404.PNT | 20MKA00CT0129 | GENERATOR COLD/HOT H2 TEMP 3 | RTD | 0 | 500 | °C
1360 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245205.PNT | 2HDAS:TE245205.PNT | 20MKA00CT013 | GENERATOR STATOR COIL OUTLET WATER TEMP 13 | RTD | 0 | 500 | °C
1482 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247405.PNT | 2HDAS:TE247405.PNT | 20MKA00CT0130 | GENERATOR COLD/HOT H2 TEMP 4 | RTD | 0 | 500 | °C
1486 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247502.PNT | 2HDAS:TE247502.PNT | 20MKA00CT0131 | GENERATOR COLD/HOT H2 TEMP 5 | RTD | 0 | 500 | °C
1487 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247503.PNT | 2HDAS:TE247503.PNT | 20MKA00CT0132 | GENERATOR COLD/HOT H2 TEMP 6 | RTD | 0 | 500 | °C
1488 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247504.PNT | 2HDAS:TE247504.PNT | 20MKA00CT0133 | GENERATOR COLD/HOT H2 TEMP 7 | RTD | 0 | 500 | °C
1489 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247505.PNT | 2HDAS:TE247505.PNT | 20MKA00CT0134 | GENERATOR COLD/HOT H2 TEMP 8 | RTD | 0 | 500 | °C
1493 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247602.PNT | 2HDAS:TE247602.PNT | 20MKA00CT0135 | GENERATOR COLD/HOT H2 TEMP 9 | RTD | 0 | 500 | °C
1494 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247603.PNT | 2HDAS:TE247603.PNT | 20MKA00CT0136 | GENERATOR COLD/HOT H2 TEMP 10 | RTD | 0 | 500 | °C
1495 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247604.PNT | 2HDAS:TE247604.PNT | 20MKA00CT0137 | GENERATOR COLD/HOT H2 TEMP 11 | RTD | 0 | 500 | °C
1496 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247605.PNT | 2HDAS:TE247605.PNT | 20MKA00CT0138 | GENERATOR COLD/HOT H2 TEMP 12 | RTD | 0 | 500 | °C
1497 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247606.PNT | 2HDAS:TE247606.PNT | 20MKA00CT0139 | GENERATOR COLD/HOT H2 TEMP 13 | RTD | 0 | 500 | °C
1361 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245206.PNT | 2HDAS:TE245206.PNT | 20MKA00CT014 | GENERATOR STATOR COIL OUTLET WATER TEMP 14 | RTD | 0 | 500 | °C
1478 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247401.PNT | 2HDAS:TE247401.PNT | 20MKA00CT0140 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 1 | RTD | 0 | 500 | °C
1485 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247501.PNT | 2HDAS:TE247501.PNT | 20MKA00CT0141 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 2 | RTD | 0 | 500 | °C
1492 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE247601.PNT | 2HDAS:TE247601.PNT | 20MKA00CT0142 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 3 | RTD | 0 | 500 | °C
1362 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245207.PNT | 2HDAS:TE245207.PNT | 20MKA00CT015 | GENERATOR STATOR COIL OUTLET WATER TEMP 15 | RTD | 0 | 500 | °C
1363 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245208.PNT | 2HDAS:TE245208.PNT | 20MKA00CT016 | GENERATOR STATOR COIL OUTLET WATER TEMP 16 | RTD | 0 | 500 | °C
1329 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244501.PNT | 2HDAS:TE244501.PNT | 20MKA00CT0160 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 500 | °C
1330 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244502.PNT | 2HDAS:TE244502.PNT | 20MKA00CT0161 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 500 | °C
1331 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244503.PNT | 2HDAS:TE244503.PNT | 20MKA00CT0162 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 500 | °C
1336 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244601.PNT | 2HDAS:TE244601.PNT | 20MKA00CT0163 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 4 | TC | 0 | 500 | °C
1337 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244602.PNT | 2HDAS:TE244602.PNT | 20MKA00CT0164 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 5 | TC | 0 | 500 | °C
1338 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244603.PNT | 2HDAS:TE244603.PNT | 20MKA00CT0165 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 6 | TC | 0 | 500 | °C
1343 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244701.PNT | 2HDAS:TE244701.PNT | 20MKA00CT0166 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 7 | TC | 0 | 500 | °C
1344 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244702.PNT | 2HDAS:TE244702.PNT | 20MKA00CT0167 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 8 | TC | 0 | 500 | °C
1345 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244703.PNT | 2HDAS:TE244703.PNT | 20MKA00CT0168 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 9 | TC | 0 | 500 | °C
1332 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244504.PNT | 2HDAS:TE244504.PNT | 20MKA00CT0169 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 500 | °C
1364 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245301.PNT | 2HDAS:TE245301.PNT | 20MKA00CT017 | GENERATOR STATOR COIL OUTLET WATER TEMP 17 | RTD | 0 | 500 | °C
1339 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244604.PNT | 2HDAS:TE244604.PNT | 20MKA00CT0170 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 500 | °C
1346 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE244704.PNT | 2HDAS:TE244704.PNT | 20MKA00CT0171 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 500 | °C
1365 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245302.PNT | 2HDAS:TE245302.PNT | 20MKA00CT018 | GENERATOR STATOR COIL OUTLET WATER TEMP 18 | RTD | 0 | 500 | °C
1366 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245303.PNT | 2HDAS:TE245303.PNT | 20MKA00CT019 | GENERATOR STATOR COIL OUTLET WATER TEMP 19 | RTD | 0 | 500 | °C
1367 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245304.PNT | 2HDAS:TE245304.PNT | 20MKA00CT020 | GENERATOR STATOR COIL OUTLET WATER TEMP 20 | RTD | 0 | 500 | °C
1368 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245305.PNT | 2HDAS:TE245305.PNT | 20MKA00CT021 | GENERATOR STATOR COIL OUTLET WATER TEMP 21 | RTD | 0 | 500 | °C
1369 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245306.PNT | 2HDAS:TE245306.PNT | 20MKA00CT022 | GENERATOR STATOR COIL OUTLET WATER TEMP 22 | RTD | 0 | 500 | °C
1370 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245307.PNT | 2HDAS:TE245307.PNT | 20MKA00CT023 | GENERATOR STATOR COIL OUTLET WATER TEMP 23 | RTD | 0 | 500 | °C
1371 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245308.PNT | 2HDAS:TE245308.PNT | 20MKA00CT024 | GENERATOR STATOR COIL OUTLET WATER TEMP 24 | RTD | 0 | 500 | °C
1372 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245401.PNT | 2HDAS:TE245401.PNT | 20MKA00CT025 | GENERATOR STATOR COIL OUTLET WATER TEMP 25 | RTD | 0 | 500 | °C
1373 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245402.PNT | 2HDAS:TE245402.PNT | 20MKA00CT026 | GENERATOR STATOR COIL OUTLET WATER TEMP 26 | RTD | 0 | 500 | °C
1374 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245403.PNT | 2HDAS:TE245403.PNT | 20MKA00CT027 | GENERATOR STATOR COIL OUTLET WATER TEMP 27 | RTD | 0 | 500 | °C
1375 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245404.PNT | 2HDAS:TE245404.PNT | 20MKA00CT028 | GENERATOR STATOR COIL OUTLET WATER TEMP 28 | RTD | 0 | 500 | °C
1376 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245405.PNT | 2HDAS:TE245405.PNT | 20MKA00CT029 | GENERATOR STATOR COIL OUTLET WATER TEMP 29 | RTD | 0 | 500 | °C
1377 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245406.PNT | 2HDAS:TE245406.PNT | 20MKA00CT030 | GENERATOR STATOR COIL OUTLET WATER TEMP 30 | RTD | 0 | 500 | °C
1378 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245407.PNT | 2HDAS:TE245407.PNT | 20MKA00CT031 | GENERATOR STATOR COIL OUTLET WATER TEMP 31 | RTD | 0 | 500 | °C
1379 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245408.PNT | 2HDAS:TE245408.PNT | 20MKA00CT032 | GENERATOR STATOR COIL OUTLET WATER TEMP 32 | RTD | 0 | 500 | °C
1380 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245501.PNT | 2HDAS:TE245501.PNT | 20MKA00CT033 | GENERATOR STATOR COIL OUTLET WATER TEMP 33 | RTD | 0 | 500 | °C
1381 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245502.PNT | 2HDAS:TE245502.PNT | 20MKA00CT034 | GENERATOR STATOR COIL OUTLET WATER TEMP 34 | RTD | 0 | 500 | °C
1382 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245503.PNT | 2HDAS:TE245503.PNT | 20MKA00CT035 | GENERATOR STATOR COIL OUTLET WATER TEMP 35 | RTD | 0 | 500 | °C
1383 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245504.PNT | 2HDAS:TE245504.PNT | 20MKA00CT036 | GENERATOR STATOR COIL OUTLET WATER TEMP 36 | RTD | 0 | 500 | °C
1384 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245505.PNT | 2HDAS:TE245505.PNT | 20MKA00CT037 | GENERATOR STATOR COIL OUTLET WATER TEMP 37 | RTD | 0 | 500 | °C
1385 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245506.PNT | 2HDAS:TE245506.PNT | 20MKA00CT038 | GENERATOR STATOR COIL OUTLET WATER TEMP 38 | RTD | 0 | 500 | °C
1386 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245507.PNT | 2HDAS:TE245507.PNT | 20MKA00CT039 | GENERATOR STATOR COIL OUTLET WATER TEMP 39 | RTD | 0 | 500 | °C
1387 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245508.PNT | 2HDAS:TE245508.PNT | 20MKA00CT040 | GENERATOR STATOR COIL OUTLET WATER TEMP 40 | RTD | 0 | 500 | °C
1388 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245601.PNT | 2HDAS:TE245601.PNT | 20MKA00CT041 | GENERATOR STATOR COIL OUTLET WATER TEMP 41 | RTD | 0 | 500 | °C
1389 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245602.PNT | 2HDAS:TE245602.PNT | 20MKA00CT042 | GENERATOR STATOR COIL OUTLET WATER TEMP 42 | RTD | 0 | 500 | °C
1390 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245603.PNT | 2HDAS:TE245603.PNT | 20MKA00CT043 | GENERATOR STATOR COIL OUTLET WATER TEMP 43 | RTD | 0 | 500 | °C
1391 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245604.PNT | 2HDAS:TE245604.PNT | 20MKA00CT044 | GENERATOR STATOR COIL OUTLET WATER TEMP 44 | RTD | 0 | 500 | °C
1392 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245605.PNT | 2HDAS:TE245605.PNT | 20MKA00CT045 | GENERATOR STATOR COIL OUTLET WATER TEMP 45 | RTD | 0 | 500 | °C
1393 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245606.PNT | 2HDAS:TE245606.PNT | 20MKA00CT046 | GENERATOR STATOR COIL OUTLET WATER TEMP 46 | RTD | 0 | 500 | °C
1394 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245607.PNT | 2HDAS:TE245607.PNT | 20MKA00CT047 | GENERATOR STATOR COIL OUTLET WATER TEMP 47 | RTD | 0 | 500 | °C
1395 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245608.PNT | 2HDAS:TE245608.PNT | 20MKA00CT048 | GENERATOR STATOR COIL OUTLET WATER TEMP 48 | RTD | 0 | 500 | °C
1396 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245701.PNT | 2HDAS:TE245701.PNT | 20MKA00CT049 | GENERATOR STATOR COIL OUTLET WATER TEMP 49 | RTD | 0 | 500 | °C
1397 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245702.PNT | 2HDAS:TE245702.PNT | 20MKA00CT050 | GENERATOR STATOR COIL OUTLET WATER TEMP 50 | RTD | 0 | 500 | °C
1398 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245703.PNT | 2HDAS:TE245703.PNT | 20MKA00CT051 | GENERATOR STATOR COIL OUTLET WATER TEMP 51 | RTD | 0 | 500 | °C
1399 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245704.PNT | 2HDAS:TE245704.PNT | 20MKA00CT052 | GENERATOR STATOR COIL OUTLET WATER TEMP 52 | RTD | 0 | 500 | °C
1400 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245705.PNT | 2HDAS:TE245705.PNT | 20MKA00CT053 | GENERATOR STATOR COIL OUTLET WATER TEMP 53 | RTD | 0 | 500 | °C
1401 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE245706.PNT | 2HDAS:TE245706.PNT | 20MKA00CT054 | GENERATOR STATOR COIL OUTLET WATER TEMP 54 | RTD | 0 | 500 | °C
1402 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246101.PNT | 2HDAS:TE246101.PNT | 20MKA00CT055 | GENERATOR STATOR BARS TEMP 1 | RTD | 0 | 500 | °C
1403 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246102.PNT | 2HDAS:TE246102.PNT | 20MKA00CT056 | GENERATOR STATOR BARS TEMP 2 | RTD | 0 | 500 | °C
1404 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246103.PNT | 2HDAS:TE246103.PNT | 20MKA00CT057 | GENERATOR STATOR BARS TEMP 3 | RTD | 0 | 500 | °C
1405 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246104.PNT | 2HDAS:TE246104.PNT | 20MKA00CT058 | GENERATOR STATOR BARS TEMP 4 | RTD | 0 | 500 | °C
1406 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246105.PNT | 2HDAS:TE246105.PNT | 20MKA00CT059 | GENERATOR STATOR BARS TEMP 5 | RTD | 0 | 500 | °C
1407 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246106.PNT | 2HDAS:TE246106.PNT | 20MKA00CT060 | GENERATOR STATOR BARS TEMP 6 | RTD | 0 | 500 | °C
1408 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246107.PNT | 2HDAS:TE246107.PNT | 20MKA00CT061 | GENERATOR STATOR BARS TEMP 7 | RTD | 0 | 500 | °C
1409 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246108.PNT | 2HDAS:TE246108.PNT | 20MKA00CT062 | GENERATOR STATOR BARS TEMP 8 | RTD | 0 | 500 | °C
1410 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246201.PNT | 2HDAS:TE246201.PNT | 20MKA00CT063 | GENERATOR STATOR BARS TEMP 9 | RTD | 0 | 500 | °C
1411 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246202.PNT | 2HDAS:TE246202.PNT | 20MKA00CT064 | GENERATOR STATOR BARS TEMP 10 | RTD | 0 | 500 | °C
1412 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246203.PNT | 2HDAS:TE246203.PNT | 20MKA00CT065 | GENERATOR STATOR BARS TEMP 11 | RTD | 0 | 500 | °C
1413 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246204.PNT | 2HDAS:TE246204.PNT | 20MKA00CT066 | GENERATOR STATOR BARS TEMP 12 | RTD | 0 | 500 | °C
1414 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246205.PNT | 2HDAS:TE246205.PNT | 20MKA00CT067 | GENERATOR STATOR BARS TEMP 13 | RTD | 0 | 500 | °C
1415 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246206.PNT | 2HDAS:TE246206.PNT | 20MKA00CT068 | GENERATOR STATOR BARS TEMP 14 | RTD | 0 | 500 | °C
1416 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246207.PNT | 2HDAS:TE246207.PNT | 20MKA00CT069 | GENERATOR STATOR BARS TEMP 15 | RTD | 0 | 500 | °C
1417 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246208.PNT | 2HDAS:TE246208.PNT | 20MKA00CT070 | GENERATOR STATOR BARS TEMP 16 | RTD | 0 | 500 | °C
1418 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246301.PNT | 2HDAS:TE246301.PNT | 20MKA00CT071 | GENERATOR STATOR BARS TEMP 17 | RTD | 0 | 500 | °C
1419 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246302.PNT | 2HDAS:TE246302.PNT | 20MKA00CT072 | GENERATOR STATOR BARS TEMP 18 | RTD | 0 | 500 | °C
1420 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246303.PNT | 2HDAS:TE246303.PNT | 20MKA00CT073 | GENERATOR STATOR BARS TEMP 19 | RTD | 0 | 500 | °C
1421 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246304.PNT | 2HDAS:TE246304.PNT | 20MKA00CT074 | GENERATOR STATOR BARS TEMP 20 | RTD | 0 | 500 | °C
1422 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246305.PNT | 2HDAS:TE246305.PNT | 20MKA00CT075 | GENERATOR STATOR BARS TEMP 21 | RTD | 0 | 500 | °C
1423 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246306.PNT | 2HDAS:TE246306.PNT | 20MKA00CT076 | GENERATOR STATOR BARS TEMP 22 | RTD | 0 | 500 | °C
1424 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246307.PNT | 2HDAS:TE246307.PNT | 20MKA00CT077 | GENERATOR STATOR BARS TEMP 23 | RTD | 0 | 500 | °C
1425 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246308.PNT | 2HDAS:TE246308.PNT | 20MKA00CT078 | GENERATOR STATOR BARS TEMP 24 | RTD | 0 | 500 | °C
1426 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246401.PNT | 2HDAS:TE246401.PNT | 20MKA00CT079 | GENERATOR STATOR BARS TEMP 25 | RTD | 0 | 500 | °C
1427 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246402.PNT | 2HDAS:TE246402.PNT | 20MKA00CT080 | GENERATOR STATOR BARS TEMP 26 | RTD | 0 | 500 | °C
1428 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246403.PNT | 2HDAS:TE246403.PNT | 20MKA00CT081 | GENERATOR STATOR BARS TEMP 27 | RTD | 0 | 500 | °C
1429 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246404.PNT | 2HDAS:TE246404.PNT | 20MKA00CT082 | GENERATOR STATOR BARS TEMP 28 | RTD | 0 | 500 | °C
1430 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246405.PNT | 2HDAS:TE246405.PNT | 20MKA00CT083 | GENERATOR STATOR BARS TEMP 29 | RTD | 0 | 500 | °C
1431 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246406.PNT | 2HDAS:TE246406.PNT | 20MKA00CT084 | GENERATOR STATOR BARS TEMP 30 | RTD | 0 | 500 | °C
1432 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246407.PNT | 2HDAS:TE246407.PNT | 20MKA00CT085 | GENERATOR STATOR BARS TEMP 31 | RTD | 0 | 500 | °C
1433 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246408.PNT | 2HDAS:TE246408.PNT | 20MKA00CT086 | GENERATOR STATOR BARS TEMP 32 | RTD | 0 | 500 | °C
1434 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246501.PNT | 2HDAS:TE246501.PNT | 20MKA00CT087 | GENERATOR STATOR BARS TEMP 33 | RTD | 0 | 500 | °C
1435 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246502.PNT | 2HDAS:TE246502.PNT | 20MKA00CT088 | GENERATOR STATOR BARS TEMP 34 | RTD | 0 | 500 | °C
1436 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246503.PNT | 2HDAS:TE246503.PNT | 20MKA00CT089 | GENERATOR STATOR BARS TEMP 35 | RTD | 0 | 500 | °C
1437 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246504.PNT | 2HDAS:TE246504.PNT | 20MKA00CT090 | GENERATOR STATOR BARS TEMP 36 | RTD | 0 | 500 | °C
1438 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246505.PNT | 2HDAS:TE246505.PNT | 20MKA00CT091 | GENERATOR STATOR BARS TEMP 37 | RTD | 0 | 500 | °C
1439 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246506.PNT | 2HDAS:TE246506.PNT | 20MKA00CT092 | GENERATOR STATOR BARS TEMP 38 | RTD | 0 | 500 | °C
1440 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246507.PNT | 2HDAS:TE246507.PNT | 20MKA00CT093 | GENERATOR STATOR BARS TEMP 39 | RTD | 0 | 500 | °C
1441 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246508.PNT | 2HDAS:TE246508.PNT | 20MKA00CT094 | GENERATOR STATOR BARS TEMP 40 | RTD | 0 | 500 | °C
1442 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246601.PNT | 2HDAS:TE246601.PNT | 20MKA00CT095 | GENERATOR STATOR BARS TEMP 41 | RTD | 0 | 500 | °C
1443 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246602.PNT | 2HDAS:TE246602.PNT | 20MKA00CT096 | GENERATOR STATOR BARS TEMP 42 | RTD | 0 | 500 | °C
1444 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246603.PNT | 2HDAS:TE246603.PNT | 20MKA00CT097 | GENERATOR STATOR BARS TEMP 43 | RTD | 0 | 500 | °C
1445 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246604.PNT | 2HDAS:TE246604.PNT | 20MKA00CT098 | GENERATOR STATOR BARS TEMP 44 | RTD | 0 | 500 | °C
1446 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50-F290S-K0301-04 | OPC.2HDAS:TE246605.PNT | 2HDAS:TE246605.PNT | 20MKA00CT099 | GENERATOR STATOR BARS TEMP 45 | RTD | 0 | 500 | °C
1185 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50- | OPC.2IDAS:AI120707.PNT | 2IDAS:AI120707.PNT | 20RPSP001 | REAL POWER SET POINT | AI | 0 | 330 | MW
1192 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50- | OPC.2IDAS:AI120807.PNT | 2IDAS:AI120807.PNT | 20MPVSP001 | MAX POWER VARIATION SET POINT | AI | 0 | 15 | MW/Min
1222 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | 50- | OPC.2IDAS:AI121407.PNT | 2IDAS:AI121407.PNT | 20LFC001 | LOAD FREQ CONTROL N_LEVEL | AI | -1 | 1
1434 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD106AIN.PNT_3 | 2VALVE:2AD106AIN.PNT_3 | 20DCSDEHAI01 | CCS DEMAND 1 | AI | 0 | 100 | %
1435 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD107AIN.PNT_3 | 2VALVE:2AD107AIN.PNT_3 | 20DCSDEHAI02 | CCS DEMAND 2 | AI | 0 | 100 | %
1436 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD11206AOUT.OUT | 2VALVE:2AD11206AOUT.OUT | 20DEHDCSAO02 | GENERATOR LOAD | AO | 0 | 519.6 | MW
1437 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD106AIN.PNT_1 | 2VALVE:2AD106AIN.PNT_1 | 20DQDEH01 | GENERATOR LOAD 1 | AI | 0 | 519.6 | MW
1438 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD107AIN.PNT_1 | 2VALVE:2AD107AIN.PNT_1 | 20DQDEH02 | GENERATOR LOAD 2 | AI | 0 | 519.6 | MW
1439 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #20 | F296S-K0606 | OPC.2VALVE:2AD108AIN.PNT_1 | 2VALVE:2AD108AIN.PNT_1 | 20DQDEH03 | GENERATOR LOAD 3 | AI | 0 | 519.6 | MW
1464 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2RDAS:AI220101.PNT | 2RDAS:AI220101.PNT | 20BAT10CE001XR01 | GT HV WINDING TEMPERATURE | AI | 0 | 150 | C
1465 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2RDAS:AI220102.PNT | 2RDAS:AI220102.PNT | 20BAT10CE002XR01 | GT LV WINDING TEMPERATURE | AI | 0 | 150 | C
1462 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2RDAS:AI220103.PNT | 2RDAS:AI220103.PNT | 20BAT10CE003XR01 | GT OIL TEMPERATURE | AI | 0 | 150 | C
1466 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-12 | OPC.2RDAS:AI220104.PNT | 2RDAS:AI220104.PNT | 20BAT10CE004XR01 | GT OLTC CHANGING POSITION | AI | 0 | 20 | TAP
1443 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174101.PNT | 2SDAS:CT174101.PNT | 20MKA01-01 | GEN. CURRENT Ia | AI | 0 | 15000 | A
1444 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174102.PNT | 2SDAS:CT174102.PNT | 20MKA01-02 | GEN. CURRENT Ib | AI | 0 | 15000 | A
1445 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174103.PNT | 2SDAS:CT174103.PNT | 20MKA01-03 | GEN. CURRENT Ic | AI | 0 | 15000 | A
1446 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174104.PNT | 2SDAS:CT174104.PNT | 20MKA01-04 | GEN. NEGATIVE-SEQUENCE CURRENT | AI | 0 | 15000 | A
1447 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174105.PNT | 2SDAS:CT174105.PNT | 20MKA01-05 | GEN. NEUTRAL POINT CURRENT | AI | 0 | 5 | A
1448 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174201.PNT | 2SDAS:CT174201.PNT | 20MKA01-06 | EXCITING TR. HV SIDE CURRENT Ia | AI | 0 | 300 | A
1449 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174202.PNT | 2SDAS:CT174202.PNT | 20MKA01-07 | EXCITING TR. HV SIDE CURRENT Ib | AI | 0 | 300 | A
1450 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:CT174203.PNT | 2SDAS:CT174203.PNT | 20MKA01-08 | EXCITING TR. HV SIDE CURRENT Ic | AI | 0 | 300 | A
1451 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174106.PNT | 2SDAS:AI174106.PNT | 20MKA01-09 | GEN. A-C VOLTAGE | AI | 0 | 24 | kV
1452 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174107.PNT | 2SDAS:AI174107.PNT | 20MKA01-10 | GEN. OUTLET ZERO-SEQUENCE VOLTAGE | AI | 0 | 100 | V
1456 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174108.PNT | 2SDAS:AI174108.PNT | 20MKA01-11 | GEN. ACTIVE POWER | AI | 0 | 450 | MW
1454 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174204.PNT | 2SDAS:AI174204.PNT | 20MKA01-12 | GEN. REACTIVE POWER | AI | -400 | 400 | MVAR
1457 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174205.PNT | 2SDAS:AI174205.PNT | 20MKA01-13 | GEN. POWER FACTOR | AI | -1 | 1 | pF
1458 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-05 | OPC.2SDAS:AI174206.PNT | 2SDAS:AI174206.PNT | 20MKA01-14 | GEN. FREQUENCY | AI | 0 | 60 | Hz
1460 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-14 | OPC.2SDAS:CT174207.PNT | 2SDAS:CT174207.PNT | 20MKA01-15 | FIELD CURRENT | AI | 0 | 3000 | A
1461 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-14 | OPC.2SDAS:AI174208.PNT | 2SDAS:AI174208.PNT | 20MKA01-16 | FIELD VOLTAGE | AI | 0 | 1000 | V
1467 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2SDAS:AI174301.PNT | 2SDAS:AI174301.PNT | 20MKA01-17A | ET A PHASE TEMPERATURE | AI | 0 | 150 | C
1468 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2SDAS:AI174302.PNT | 2SDAS:AI174302.PNT | 20MKA01-18B | ET B PHASE TEMPERATURE | AI | 0 | 150 | C
1469 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #20 | F296S-D0606-11 | OPC.2SDAS:AI174303.PNT | 2SDAS:AI174303.PNT | 20MKA01-19C | ET C PHASE TEMPERATURE | AI | 0 | 150 | C
440 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073505.PNT | 2FDAS:AI073505.PNT | 20MKG00GH001AI01 | GENERATOR H2 LEAKAGE RATE 1 | AI | 0.1 | 2 | %
441 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073506.PNT | 2FDAS:AI073506.PNT | 20MKG00GH001AI02 | GENERATOR H2 LEAKAGE RATE 2 | AI | 0.1 | 2 | %
442 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073507.PNT | 2FDAS:AI073507.PNT | 20MKG00GH001AI03 | GENERATOR H2 LEAKAGE RATE 3 | AI | 0.1 | 2 | %
444 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073601.PNT | 2FDAS:AI073601.PNT | 20MKG00GH001AI04 | GENERATOR H2 LEAKAGE RATE 4 | AI | 0.1 | 2 | %
445 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073602.PNT | 2FDAS:AI073602.PNT | 20MKG00GH001AI05 | GENERATOR H2 LEAKAGE RATE 5 | AI | 0.1 | 2 | %
446 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073603.PNT | 2FDAS:AI073603.PNT | 20MKG00GH001AI06 | GENERATOR H2 LEAKAGE RATE 6 | AI | 0.1 | 2 | %
447 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073604.PNT | 2FDAS:AI073604.PNT | 20MKG00GH001AI07 | GENERATOR H2 LEAKAGE RATE 7 | AI | 0.1 | 2 | %
448 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073605.PNT | 2FDAS:AI073605.PNT | 20MKG00GH001AI08 | GENERATOR H2 LEAKAGE RATE 8 | AI | 0.1 | 2 | %
436 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:PT073501.PNT | 2FDAS:PT073501.PNT | 20MKG10CP201 | GENERATOR INLET HYDROGEN PRESS | AI | 0 | 0.6 | MPa
670 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:RT073802.PNT | 2FDAS:RT073802.PNT | 20MKG10CT001 | GENERATOR INLET HYDROGEN TEMP | RTD | 0 | 100 | °C
671 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:RT073803.PNT | 2FDAS:RT073803.PNT | 20MKG11CT001 | GENERATOR EXHAUST HYDROGEN TEMP | RTD | 0 | 100 | °C
438 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073503.PNT | 2FDAS:AI073503.PNT | 20MKG30CQ201 | GENERATOR TURBINE SIDE HYDROGEN HUMIDITY | AI | 0 | 4 | g/m3
439 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073504.PNT | 2FDAS:AI073504.PNT | 20MKG30CQ202 | GENERATOR COLLECTOR SIDE HYDROGEN HUMIDITY | AI | 0 | 4 | g/m3
437 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-26 | OPC.2FDAS:AI073502.PNT | 2FDAS:AI073502.PNT | 20MKG50CQ201 | GENERATOR HYDROGEN PURITY | AI | 75 | 100 | % |  |  | 95
1498 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2HDAS:TE247607.PNT | 2HDAS:TE247607.PNT | 20PGA33CT001 | GENERATOR HYDROGEN COOLER MAIN PIPE INLET TEMP | RTD | 0 | 50 | °C
1462 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2HDAS:TE247107.PNT | 2HDAS:TE247107.PNT | 20PGA33CT002 | GENERATOR HYDROGEN COOLER NO.1 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1463 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2HDAS:TE247108.PNT | 2HDAS:TE247108.PNT | 20PGA33CT003 | GENERATOR HYDROGEN COOLER NO.2 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1470 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2HDAS:TE247207.PNT | 2HDAS:TE247207.PNT | 20PGA33CT004 | GENERATOR HYDROGEN COOLER NO.3 OUTLET WATER TEMP | RTD | 0 | 50 | °C
1471 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2HDAS:TE247208.PNT | 2HDAS:TE247208.PNT | 20PGA33CT005 | GENERATOR HYDROGEN COOLER NO.4 OUTLET WATER TEMP | RTD | 0 | 50 | °C
648 | 1 | UJRBG #20 | 9 | GENERATOR SYSTEM #2 | 13 | GAS COOLING SYSTEM, INCL. H2-, CO2, SUPPLY SYSTEM | 50-F290S-J0201-14 | OPC.2EDAS:RT067607.PNT | 2EDAS:RT067607.PNT | 20PGA33CT006 | TURBINE HOUSER COOLING RETURN WATER TEMP 3 | RTD | 0 | 50 | °C
1870 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 1 | AUX TRANSFORMER #20 SYSTEM |  | OPC.2RDAS:AI220105.PNT | 2RDAS:AI220105.PNT | 20BBT10CE001XR01 | UAT-2 HV Wdg. Temp. | AI | 0 | 150 | ℃
1871 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 1 | AUX TRANSFORMER #20 SYSTEM |  | OPC.2RDAS:AI220106.PNT | 2RDAS:AI220106.PNT | 20BBT10CE002XR01 | UAT-2 LV-1 Wdg. Temp. | AI | 0 | 150 | ℃
1872 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 1 | AUX TRANSFORMER #20 SYSTEM |  | OPC.2RDAS:AI220107.PNT | 2RDAS:AI220107.PNT | 20BBT10CE003XR01 | UAT-2 LV-2 Wdg. Temp. | AI | 0 | 150 | ℃
1873 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 1 | AUX TRANSFORMER #20 SYSTEM |  | OPC.2RDAS:AI220201.PNT | 2RDAS:AI220201.PNT | 20BBT10CE004XR01 | UAT-2 Oil Temp. | AI | 0 | 150 | ℃
1874 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 1 | AUX TRANSFORMER #20 SYSTEM |  | OPC.2RDAS:AI220202.PNT | 2RDAS:AI220202.PNT | 20BBT10CE005XR01 | UAT-2 Tap Position | AI | 1 | 17 | tap
1875 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220203.PNT | 2RDAS:AI220203.PNT | 20BFA10CE001XR01 | 400V Unit PCC#2A-Bus-A R-Y Voltage | AI | 0 | 440 | V
1876 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220204.PNT | 2RDAS:AI220204.PNT | 20BFA10CE001XR02 | 400V Unit PCC#2A-Bus-A Y-B Voltage | AI | 0 | 440 | V
1877 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220205.PNT | 2RDAS:AI220205.PNT | 20BFA10CE001XR03 | 400V Unit PCC#2A-Bus-A B-R Voltage | AI | 0 | 440 | V
1878 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220206.PNT | 2RDAS:AI220206.PNT | 20BFA20CE001XR01 | 400V Unit PCC#2A-Bus-B R-Y Voltage | AI | 0 | 440 | V
1879 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220207.PNT | 2RDAS:AI220207.PNT | 20BFA20CE001XR02 | 400V Unit PCC#2A-Bus-B Y-B Voltage | AI | 0 | 440 | V
1880 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220208.PNT | 2RDAS:AI220208.PNT | 20BFA20CE001XR03 | 400V Unit PCC#2A-Bus-B B-R Voltage | AI | 0 | 440 | V
1881 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220301.PNT | 2RDAS:AI220301.PNT | 20BFB10CE001XR01 | 400V UNIT PCC#2B-Bus-A R-Y Voltage | AI | 0 | 440 | V
1882 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220302.PNT | 2RDAS:AI220302.PNT | 20BFB10CE001XR02 | 400V UNIT PCC#2B-Bus-A Y-B Voltage | AI | 0 | 440 | V
1883 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220303.PNT | 2RDAS:AI220303.PNT | 20BFB10CE001XR03 | 400V UNIT PCC#2B-Bus-A B-R Voltage | AI | 0 | 440 | V
1884 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220304.PNT | 2RDAS:AI220304.PNT | 20BFB20CE001XR01 | 400V UNIT PCC#2B-Bus-B R-Y Voltage | AI | 0 | 440 | V
1885 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220305.PNT | 2RDAS:AI220305.PNT | 20BFB20CE001XR02 | 400V UNIT PCC#2B-Bus-B Y-B Voltage | AI | 0 | 440 | V
1886 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220306.PNT | 2RDAS:AI220306.PNT | 20BFB20CE001XR03 | 400V UNIT PCC#2B-Bus-B B-R Voltage | AI | 0 | 440 | V
1887 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220401.PNT | 2RDAS:AI220401.PNT | 20BMA20CE001XR01 | 400V N/E Switchboard-2 R-Y Voltage | AI | 0 | 440 | V
1888 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220402.PNT | 2RDAS:AI220402.PNT | 20BMA20CE001XR02 | 400V N/E Switchboard-2 Y-B Voltage | AI | 0 | 440 | V
1889 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220403.PNT | 2RDAS:AI220403.PNT | 20BMA20CE001XR03 | 400V N/E Switchboard-2 B-R Voltage | AI | 0 | 440 | V
1893 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220501.PNT | 2RDAS:AI220501.PNT | 20BFC10CE001XR01 | 400V ESP PCC#2-Bus-A R-Y Voltage | AI | 0 | 440 | V
1894 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220502.PNT | 2RDAS:AI220502.PNT | 20BFC10CE001XR02 | 400V ESP PCC#2-Bus-A Y-B Voltage | AI | 0 | 440 | V
1895 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220503.PNT | 2RDAS:AI220503.PNT | 20BFC10CE001XR03 | 400V ESP PCC#2A-Bus-A B-R Voltage | AI | 0 | 440 | V
1896 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220504.PNT | 2RDAS:AI220504.PNT | 20BFC20CE001XR01 | 400V ESP PCC#2-BUS-B R-Y Voltage | AI | 0 | 440 | V
1897 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220505.PNT | 2RDAS:AI220505.PNT | 20BFC20CE001XR02 | 400V ESP PCC#2-BUS-B Y-B Voltage | AI | 0 | 440 | V
1898 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 2 | LV MAIN DISTRIBUTION BOARD (380 V PDC SWGR) #20 |  | OPC.2RDAS:AI220506.PNT | 2RDAS:AI220506.PNT | 20BFC20CE001XR03 | 400V ESP PCC#2-BUS-B B-R Voltage | AI | 0 | 440 | V
1905 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 3 | 6,3KV UNIT SWBD 2A |  | OPC.2SDAS:AI231101.PNT | 2SDAS:AI231101.PNT | 20BBA21CE001XR01 | 6.3kV UNIT SWBD #2A Bus R-Y Voltage | AI | 0 | 7.2 | kV
1906 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 3 | 6,3KV UNIT SWBD 2A |  | OPC.2SDAS:AI231102.PNT | 2SDAS:AI231102.PNT | 20BBA21CE001XR02 | 6.3kV UNIT SWBD #2A Bus Y-B Voltage | AI | 0 | 7.2 | kV
1907 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 3 | 6,3KV UNIT SWBD 2A |  | OPC.2SDAS:AI231103.PNT | 2SDAS:AI231103.PNT | 20BBA21CE001XR03 | 6.3kV UNIT SWBD #2A Bus B-R Voltage | AI | 0 | 7.2 | kV
1908 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 4 | 6,3KV UNIT SWBD 2B |  | OPC.2SDAS:AI231201.PNT | 2SDAS:AI231201.PNT | 20BBB21CE001XR01 | 6.3kV UNIT SWBD #2B Bus R-Y Voltage | AI | 0 | 7.2 | kV
1909 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 4 | 6,3KV UNIT SWBD 2B |  | OPC.2SDAS:AI231202.PNT | 2SDAS:AI231202.PNT | 20BBB21CE001XR02 | 6.3kV UNIT SWBD #2B Bus Y-B Voltage | AI | 0 | 7.2 | kV
1910 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 4 | 6,3KV UNIT SWBD 2B |  | OPC.2SDAS:AI231203.PNT | 2SDAS:AI231203.PNT | 20BBB21CE001XR03 | 6.3kV UNIT SWBD #2B Bus B-R Voltage | AI | 0 | 7.2 | kV
1899 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 5 | 220V CUM BOOST BATTERY CHARGER #20 |  | OPC.2RDAS:AI220601.PNT | 2RDAS:AI220601.PNT | 20BTL10CE001XR01 | Unit-2 220V DC battery Voltage | AI | 0 | 250 | V
1900 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 5 | 220V CUM BOOST BATTERY CHARGER #20 |  | OPC.2RDAS:AI220602.PNT | 2RDAS:AI220602.PNT | 20BTL10CE001XR02 | Unit-2 220V DCDB Bus Voltage | AI | 0 | 250 | V
1901 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 6 | 110V CUM BOOST BATTERY CHARGER #20 |  | OPC.2RDAS:AI220603.PNT | 2RDAS:AI220603.PNT | 20BTM10CE001XR01 | Unit-2 110V DC battery Voltage | AI | 0 | 150 | V
1902 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 6 | 110V CUM BOOST BATTERY CHARGER #20 |  | OPC.2RDAS:AI220604.PNT | 2RDAS:AI220604.PNT | 20BTM10CE001XR02 | Unit-2 110V DCDB Bus Voltage | AI | 0 | 150 | V
1903 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 7 | UPS #20 |  | OPC.2RDAS:AI220605.PNT | 2RDAS:AI220605.PNT | 20BRU11CE001XR01 | Unit-2 UPS-2A DB bus Voltage | AI | 0 | 300 | V
1904 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 7 | UPS #20 |  | OPC.2RDAS:AI220606.PNT | 2RDAS:AI220606.PNT | 20BRU12CE001XR01 | Unit-2 UPS-2B DB bus Voltage | AI | 0 | 300 | V
1890 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 8 | EDG #20 |  | OPC.2RDAS:AI220404.PNT | 2RDAS:AI220404.PNT | 20XK10CE001XR01 | Unit-2 EDG Voltage (R-Y ph) | AI | 0 | 440 | V
1891 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 8 | EDG #20 |  | OPC.2RDAS:AI220405.PNT | 2RDAS:AI220405.PNT | 20XK10CE001XR02 | Unit-2 EDG Voltage (Y-B ph) | AI | 0 | 440 | V
1892 | 1 | UJRBG #20 | 10 | POWER TRANSFORMER #20 | 8 | EDG #20 |  | OPC.2RDAS:AI220406.PNT | 2RDAS:AI220406.PNT | 20XK10CE001XR03 | Unit-2 EDG Voltage (R-B ph) | AI | 0 | 440 | V
918 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:PT201501.PNT | 2PDAS:PT201501.PNT | 20EGD10CP201 | OIL FEED MAIN PIPE PRESSURE 1 | AI | 0 | 5 | MPa
925 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:PT201601.PNT | 2PDAS:PT201601.PNT | 20EGD10CP202 | OIL FEED MAIN PIPE PRESSURE 2 | AI | 0 | 5 | MPa
283 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2NDAS:RT182108.PNT | 2NDAS:RT182108.PNT | 20EGD10CT001 | OIL FEED MAIN PIPE TEMPERATURE | RTD | 0 | 100 | °C
475 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-06 | OPC.2FDAS:PT086703.PNT | 2FDAS:PT086703.PNT | 20HCB12CP201 | AFTER FUEL OIL ATTEMPERATOR PRESS | AI | 0 | 1 | MPa
1264 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-06 | OPC.2IDAS:TE121501.PNT | 2IDAS:TE121501.PNT | 20HCB12CT001 | AFTER FUEL OIL ATTEMPERATOR TEMP | TC | 0 | 400 | °C
886 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:FT200806.PNT | 2PDAS:FT200806.PNT | 20HJF50CF201 | SUPPLYING OIL FLOW | AI | 0 | 25 | t/h
885 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:PT200805.PNT | 2PDAS:PT200805.PNT | 20HJF50CP201 | SUPPLYING OIL PRESSURE | AI | 0 | 4 | MPa
146 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2LDAS:RT150504.PNT | 2LDAS:RT150504.PNT | 20HJF50CT001 | SUPPLYING OIL TEMPERATURE | RTD | 0 | 100 | °C
1028 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2FUELOIL:AO202507.OUT | 2FUELOIL:AO202507.OUT | 20HJF60AA101XB11 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE CONTROL | AO | 0 | 100 | %
888 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:ZT200808.PNT | 2PDAS:ZT200808.PNT | 20HJF60AA101XB12 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE POSITION | AI | 0 | 100 | %
887 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2PDAS:FT200807.PNT | 2PDAS:FT200807.PNT | 20HJF60CF201 | RETURNED OIL FLOW | AI | 0 | 25 | t/h
222 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-17 | OPC.2ODAS:PT193202.PNT | 2ODAS:PT193202.PNT | 20HJF60CP201 | RETURN OIL PRESSURE | AI | 0 | 1 | MPa
1232 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-07 | OPC.2FULSTMDESUP:AO122205.OUT | 2FULSTMDESUP:AO122205.OUT | 20LCE13AA101XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATING DESUPERHEATING WATER MOTORIZE | AO | 0 | 100 | %
1178 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120605.PNT | 2IDAS:ZT120605.PNT | 20LCE13AA101XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATING DESUPERHEATING WATER MOTORIZE | AI | 0 | 100 | %
1233 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-07 | OPC.2CNCURT:AO122206.OUT | 2CNCURT:AO122206.OUT | 20LCE13AA102XB11 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE | AO | 0 | 100 | %
1179 | 1 | UJRBG #20 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120606.PNT | 2IDAS:ZT120606.PNT | 20LCE13AA102XB12 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE | AI | 0 | 100 | %
1162 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2IDAS:PT120404.PNT | 2IDAS:PT120404.PNT | 20(20)LBG10CP201 | AUXILIARY STEAM HEADER TEMP | AI | 0 | 1.1 | MPa
776 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2FDAS:TE087405.PNT | 2FDAS:TE087405.PNT | 20(20)LBG10CT001 | AUXILIARY STEAM HEADER TEMP | TC | 0 | 400 | °C
1225 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2AUXHDR:AO122104.OUT | 2AUXHDR:AO122104.OUT | 20(20)LBG13AA101XB11 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE CONTRO | AO | 0 | 100 | %
1163 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2IDAS:ZT120405.PNT | 2IDAS:ZT120405.PNT | 20(20)LBG13AA101XB12 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE POSITI | AI | 0 | 100 | %
1226 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2DAPRESS:AO122105.OUT | 2DAPRESS:AO122105.OUT | 20(20)LBG17AA101XB11 | AUXILIARY HEADER TO DEAERATOR SUPPLY STEAM CONTROL VALVE CONTROL C | AO | 0 | 100 | %
1164 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | 50-F290S-J0201-06 | OPC.2IDAS:ZT120406.PNT | 2IDAS:ZT120406.PNT | 20(20)LBG17AA101XB12 | AUXILIARY HEADER TO DEAERATOR SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | %
479 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | 50-F290S-J0201-11 | OPC.2FDAS:ZT086707.PNT | 2FDAS:ZT086707.PNT | 20MAW10AA001XB12 | REGULATING FLOW VALVE (RFV) POSITION | AI | 0 | 100 | %
478 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | 50-F290S-J0201-11 | OPC.2FDAS:PT086706.PNT | 2FDAS:PT086706.PNT | 20MAW10CP201 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX PRESS | AI | 0 | 20
791 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | 50-F290S-J0201-11 | OPC.2FDAS:TE087608.PNT | 2FDAS:TE087608.PNT | 20MAW10CT001 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX TEMP | TC | 0 | 800 | °C
1265 | 1 | UJRBG #20 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | 50-F290S-J0201-11 | OPC.2IDAS:TE121502.PNT | 2IDAS:TE121502.PNT | 20MAW10CT002 | IP CYLINDER START STEAM TEMP | TC | 0 | 400 | °C
6 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2JDAS:AI130606.PNT | 2JDAS:AI130606.PNT | 20HJF71CB201B | 1# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
22 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2KDAS:AI140606.PNT | 2KDAS:AI140606.PNT | 20HJF71CB202B | 1# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
45 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2LDAS:AI150606.PNT | 2LDAS:AI150606.PNT | 20HJF71CB203B | 1# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
7 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2JDAS:AI130607.PNT | 2JDAS:AI130607.PNT | 20HJF72CB201B | 2# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
23 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2KDAS:AI140607.PNT | 2KDAS:AI140607.PNT | 20HJF72CB202B | 2# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
46 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2LDAS:AI150607.PNT | 2LDAS:AI150607.PNT | 20HJF72CB203B | 2# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
14 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2JDAS:AI130706.PNT | 2JDAS:AI130706.PNT | 20HJF73CB201B | 3# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
30 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2KDAS:AI140706.PNT | 2KDAS:AI140706.PNT | 20HJF73CB202B | 3# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
49 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2LDAS:AI150706.PNT | 2LDAS:AI150706.PNT | 20HJF73CB203B | 3# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
15 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2JDAS:AI130707.PNT | 2JDAS:AI130707.PNT | 20HJF74CB201B | 4# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
31 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2KDAS:AI140707.PNT | 2KDAS:AI140707.PNT | 20HJF74CB202B | 4# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
50 | 1 | UJRBG #20 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F290S-J0201-17 | OPC.2LDAS:AI150707.PNT | 2LDAS:AI150707.PNT | 20HJF74CB203B | 4# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | %
1026 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2BLFLOW:AO202505.OUT | 2BLFLOW:AO202505.OUT | 20LCQ10AA101XB11 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE CONTROL | AO | 0 | 100 | %
879 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2PDAS:ZT200707.PNT | 2PDAS:ZT200707.PNT | 20LCQ10AA101XB12 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE POSITION | AI | 0 | 100 | %
877 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2PDAS:FT200705.PNT | 2PDAS:FT200705.PNT | 20LCQ10CF201 | DRUM CONTINUOUS BLOWDOWN FLOW | AI | 0 | 160 | KPa
878 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2PDAS:LT200706.PNT | 2PDAS:LT200706.PNT | 20LCQ10CL201 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL | AI | 0 | 10 | KPa
1027 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2BLLVL:AO202506.OUT | 2BLLVL:AO202506.OUT | 20LCQ11AA101XB11 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE CONTROL | AO | 0 | 100 | %
880 | 1 | UJRBG #20 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F290S-J0201-16 | OPC.2PDAS:ZT200708.PNT | 2PDAS:ZT200708.PNT | 20LCQ11AA101XB12 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE POSITIO | AI | 0 | 100 | %
409 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2FDAS:PT073102.PNT | 2FDAS:PT073102.PNT | 20LBW00CP201 | GLAND STEAM CONDENSER STEAM SIDE PRESS | AI | -99 | 99 | KPa
1214 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:PT121307.PNT | 2IDAS:PT121307.PNT | 20LBW10CP201 | GLAND MAIN PIPE PRESS | AI | 0 | 129 | Kpa
408 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2FDAS:PT073101.PNT | 2FDAS:PT073101.PNT | 20LBW10CP202 | BFP TURBINE GLAND MAIN PIPE PRESS | AI | 0 | 129 | MPa
783 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2FDAS:TE087507.PNT | 2FDAS:TE087507.PNT | 20LBW10CT001 | GLAND MAIN PIPE TEMP(BEFORE TEMPERATURE REDUCING DEVICE) | TC | 0 | 310 | °C
790 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2FDAS:TE087607.PNT | 2FDAS:TE087607.PNT | 20LBW10CT002 | BFP TURBINE GLAND MAIN PIPE TEMP | TC | 0 | 310 | °C
1262 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:RT121601.PNT | 2IDAS:RT121601.PNT | 20LBW10CT003 | GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | RTD | 0 | 150 | °C
1257 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2GLDHDRP:AO122602.OUT | 2GLDHDRP:AO122602.OUT | 20LBW12AA101XB11 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMA | AO | 0 | 100 | %
1216 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:ZT121401.PNT | 2IDAS:ZT121401.PNT | 20LBW12AA101XB12 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1256 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2GLDHDRP:AO122601.OUT | 2GLDHDRP:AO122601.OUT | 20LBW13AA002XB11 | HP STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1215 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:ZT121308.PNT | 2IDAS:ZT121308.PNT | 20LBW13AA002XB12 | HP STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1258 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2GLDHDRP:AO122603.OUT | 2GLDHDRP:AO122603.OUT | 20LBW14AA101XB11 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAN | AO | 0 | 100 | %
1217 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:ZT121402.PNT | 2IDAS:ZT121402.PNT | 20LBW14AA101XB12 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | %
1259 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2GLDESUP:AO122604.OUT | 2GLDESUP:AO122604.OUT | 20LBW15AA101XB11 | LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
1218 | 1 | UJRBG #20 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | TURBINE SEALING SYSTEM #2 | 50-F290S-J0201-10 | OPC.2IDAS:ZT121403.PNT | 2IDAS:ZT121403.PNT | 20LBW15AA101XB12 | LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
1231 | 1 | UJRBG #20 | 81 | TURBINE SEALING #2 | 3 | IP CYLINDER STARTUP STEAM PIPE #2 | 50-F290S-J0201-07 | OPC.2IPSTDESUP:AO122204.OUT | 2IPSTDESUP:AO122204.OUT | 20LCE12AA101XB11 | IP CYLINDER STARTUP STEAM DESUPERHEATING DESUPERHEATING WATER MOTO | AO | 0 | 100 | %
1177 | 1 | UJRBG #20 | 81 | TURBINE SEALING #2 | 3 | IP CYLINDER STARTUP STEAM PIPE #2 | 50-F290S-J0201-07 | OPC.2IDAS:ZT120604.PNT | 2IDAS:ZT120604.PNT | 20LCE12AA101XB12 | IP CYLINDER STARTUP STEAM DESUPERHEATING DESUPERHEATING WATER MOTO | AI | 0 | 100 | %
419 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.2FDAS:LT073205.PNT | 2FDAS:LT073205.PNT | 20MAV00CL201 | MAIN OIL TANK LEVEL | AI | 0 | 2000 | mm |  | 1330 | 1410 | 1910 | 2000
663 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.2FDAS:RT073701.PNT | 2FDAS:RT073701.PNT | 20MAV00CT001 | MAIN OIL TANK OIL TEMP | RTD | 0 | 400 | °C
663 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-19 | OPC.2ATC:2BD116AIN.PNT_2 | 2ATC:2BD116AIN.PNT_2 | 20MAV00CT002 | MAIN OIL TANK OIL TEMP | RTD | 0 | 400 | °C
426 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | TURBINE MAIN OIL TANK | 50-F290S-J0201-23 | OPC.2FDAS:CT073305.PNT | 2FDAS:CT073305.PNT | 20MAV20GC001AI02 | TURBINE LUBE OIL TANK ELECTRIC HEATER CURRENT | AI | 0 | 100 | %
418 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.2FDAS:PT073204.PNT | 2FDAS:PT073204.PNT | 20MAV00CP205 | OIL COOLER OUTLET MAIN PIPE OIL PRESS | AI | 0 | 0.6 | MPa
664 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.2FDAS:RT073702.PNT | 2FDAS:RT073702.PNT | 20MAV00CT003 | OIL COOLER INLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | °C
665 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-19 | OPC.2FDAS:RT073703.PNT | 2FDAS:RT073703.PNT | 20MAV00CT004 | OIL COOLER OUTLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | °C
661 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-14 | OPC.2EDAS:RT067806.PNT | 2EDAS:RT067806.PNT | 20PGA34CT001 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
662 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | TURBINE LUBE OIL COOLER A | 50-F290S-J0201-14 | OPC.2EDAS:RT067807.PNT | 2EDAS:RT067807.PNT | 20PGA34CT002 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | °C
415 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 6 | MAIN OIL PUMP #2 | 50-F290S-J0201-19 | OPC.2FDAS:PT073201.PNT | 2FDAS:PT073201.PNT | 20MAV00CP201 | MAIN OIL PUMP INLET PRESS | AI | 0 | 2.5 | MPa
416 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 6 | MAIN OIL PUMP #2 | 50-F290S-J0201-19 | OPC.2FDAS:PT073202.PNT | 2FDAS:PT073202.PNT | 20MAV00CP202 | MAIN OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
413 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 7 | TURBINE AC OIL PUMP #20 | 50-F290S-J0201-19 | OPC.2FDAS:PT073106.PNT | 2FDAS:PT073106.PNT | 20MAV20CP201 | A.C. LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
421 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 7 | TURBINE AC OIL PUMP #20 | 50-F290S-J0201-19 | OPC.2FDAS:CT073207.PNT | 2FDAS:CT073207.PNT | 20MAV20GC001AI01 | TURBINE AC OIL PUMP CURRENT | AI | 0 | 100 | %
449 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 8 | TURBINE JACKING OIL PUMP #20A | 50-F290S-K0301-01 | OPC.2FDAS:PT073606.PNT | 2FDAS:PT073606.PNT | 20MAV00CP206 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa
425 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 8 | TURBINE JACKING OIL PUMP #20A | 50-F290S-K0301-01 | OPC.2FDAS:CT073304.PNT | 2FDAS:CT073304.PNT | 20MAV30AP101XB13 | TURBINE JACKING OIL PUMP A CURRENT | AI | 0 | 100 | %
432 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 9 | TURBINE JACKING OIL PUMP #20B | 50-F290S-K0301-01 | OPC.2FDAS:CT073404.PNT | 2FDAS:CT073404.PNT | 20MAV40AP101XB13 | TURBINE JACKING OIL PUMP B CURRENT | AI | 0 | 100 | %
1642 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 10 | LUBE OIL PIPE #2 | F296S-J0201-19 | OPC.2VALVE:2AD111AIN.PNT_2 | 2VALVE:2AD111AIN.PNT_2 | 20MAV00CP204 | LUBE OIL PRESS | AI | 0 | 0.6 | MPa
1643 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 10 | LUBE OIL PIPE #2 | F296S-J0201-19 | OPC.2ATC:2BD116AIN.PNT_1 | 2ATC:2BD116AIN.PNT_1 | 20MAV00CT042 | LUBE OIL TEMP | RTD | 0 | 120 | C
420 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 11 | TURBINE DC EMERGENCY OIL PUMP #20 | 50-F290S-J0201-19 | OPC.2FDAS:CT073206.PNT | 2FDAS:CT073206.PNT | 20MAV10AP101XB13 | TURBINE DC EMERGENCY OIL PUMP CURRENT | AI | 0 | 100 | %
412 | 1 | UJRBG #20 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 11 | TURBINE DC EMERGENCY OIL PUMP #20 | 50-F290S-J0201-19 | OPC.2FDAS:PT073105.PNT | 2FDAS:PT073105.PNT | 20MAV10CP201 | D.C. EMERGENCY LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa
1649 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD103AIN.PNT_7 | 2ATC:2BD103AIN.PNT_7 | 20TSIDEH08 | SHAFT NO.1 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1650 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD103AIN.PNT_8 | 2ATC:2BD103AIN.PNT_8 | 20TSIDEH09 | SHAFT NO.1 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1651 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_3 | 2ATC:2BD105AIN.PNT_3 | 20TSIDEH20 | BEARING COVER NO.1 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1646 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_1 | 2ATC:2BD115AIN.PNT_1 | 20MAV00CT005 | #1 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1647 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD116AIN.PNT_5 | 2ATC:2BD116AIN.PNT_5 | 20MAV00CT012 | #1 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1648 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.2ATC:2BD116AIN.PNT_6 | 2ATC:2BD116AIN.PNT_6 | 20MAV00CT013 | #1 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1655 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_1 | 2ATC:2BD104AIN.PNT_1 | 20TSIDEH10 | SHAFT NO.2 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1656 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_2 | 2ATC:2BD104AIN.PNT_2 | 20TSIDEH11 | SHAFT NO.2 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1657 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_4 | 2ATC:2BD105AIN.PNT_4 | 20TSIDEH21 | BEARING COVER NO.2 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1652 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_2 | 2ATC:2BD115AIN.PNT_2 | 20MAV00CT006 | #2 BEARING OIL DRAIN TEMP | RTD | 0 | 120 | C
1653 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD116AIN.PNT_7 | 2ATC:2BD116AIN.PNT_7 | 20MAV00CT014 | #2 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1654 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_1 | 2ATC:2BD117AIN.PNT_1 | 20MAV00CT015 | #2 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1661 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_3 | 2ATC:2BD104AIN.PNT_3 | 20TSIDEH12 | SHAFT NO.3 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1662 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_4 | 2ATC:2BD104AIN.PNT_4 | 20TSIDEH13 | SHAFT NO.3 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1663 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_5 | 2ATC:2BD105AIN.PNT_5 | 20TSIDEH22 | BEARING COVER NO.3 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1658 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_3 | 2ATC:2BD115AIN.PNT_3 | 20MAV00CT010 | #3 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1659 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_2 | 2ATC:2BD117AIN.PNT_2 | 20MAV00CT016 | #3 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1660 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_3 | 2ATC:2BD117AIN.PNT_3 | 20MAV00CT017 | #3 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
1667 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_5 | 2ATC:2BD104AIN.PNT_5 | 20TSIDEH14 | SHAFT NO.4 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1668 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD104AIN.PNT_6 | 2ATC:2BD104AIN.PNT_6 | 20TSIDEH15 | SHAFT NO.4 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um
1669 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD105AIN.PNT_6 | 2ATC:2BD105AIN.PNT_6 | 20TSIDEH23 | BEARING COVER NO.4 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um
1664 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD115AIN.PNT_4 | 2ATC:2BD115AIN.PNT_4 | 20MAV00CT011 | #4 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C
1665 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_4 | 2ATC:2BD117AIN.PNT_4 | 20MAV00CT018 | #4 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C
1666 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.2ATC:2BD117AIN.PNT_5 | 2ATC:2BD117AIN.PNT_5 | 20MAV00CT019 | #4 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C
666 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | 50-F290S-J0201-19 | OPC.2FDAS:RT073704.PNT | 2FDAS:RT073704.PNT | 20MAV00CT007 | POSITION THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | °C
667 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | 50-F290S-J0201-19 | OPC.2FDAS:RT073705.PNT | 2FDAS:RT073705.PNT | 20MAV00CT008 | THRUST BEARING OIL DRAIN TEMP | RTD | -50 | 150 | °C
668 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | 50-F290S-J0201-19 | OPC.2FDAS:RT073706.PNT | 2FDAS:RT073706.PNT | 20MAV00CT009 | WORK THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | °C
1684 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_1 | 2ATC:2BD112AIN.PNT_1 | 20MAV00CT031 | #1 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1685 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_2 | 2ATC:2BD112AIN.PNT_2 | 20MAV00CT032 | #2 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1686 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_3 | 2ATC:2BD112AIN.PNT_3 | 20MAV00CT033 | #3 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1687 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_4 | 2ATC:2BD112AIN.PNT_4 | 20MAV00CT034 | #4 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1688 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_5 | 2ATC:2BD112AIN.PNT_5 | 20MAV00CT035 | #5 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1689 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_6 | 2ATC:2BD112AIN.PNT_6 | 20MAV00CT036 | #6 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1690 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_7 | 2ATC:2BD112AIN.PNT_7 | 20MAV00CT037 | #7 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1691 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD112AIN.PNT_8 | 2ATC:2BD112AIN.PNT_8 | 20MAV00CT038 | #8 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1692 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_1 | 2ATC:2BD113AIN.PNT_1 | 20MAV00CT039 | #9 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1693 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_2 | 2ATC:2BD113AIN.PNT_2 | 20MAV00CT040 | #10 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1694 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_3 | 2ATC:2BD113AIN.PNT_3 | 20MAV00CT041 | #11 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C
1673 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_4 | 2ATC:2BD113AIN.PNT_4 | 20MAV00CT020 | #1 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1674 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_5 | 2ATC:2BD113AIN.PNT_5 | 20MAV00CT021 | #2 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1675 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_6 | 2ATC:2BD113AIN.PNT_6 | 20MAV00CT022 | #3 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1676 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_7 | 2ATC:2BD113AIN.PNT_7 | 20MAV00CT023 | #4 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1677 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD113AIN.PNT_8 | 2ATC:2BD113AIN.PNT_8 | 20MAV00CT024 | #5 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1678 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_1 | 2ATC:2BD114AIN.PNT_1 | 20MAV00CT025 | #6 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1679 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_2 | 2ATC:2BD114AIN.PNT_2 | 20MAV00CT026 | #7 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1680 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_3 | 2ATC:2BD114AIN.PNT_3 | 20MAV00CT027 | #8 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1681 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_4 | 2ATC:2BD114AIN.PNT_4 | 20MAV00CT028 | #9 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1682 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_5 | 2ATC:2BD114AIN.PNT_5 | 20MAV00CT029 | #10 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1683 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD114AIN.PNT_6 | 2ATC:2BD114AIN.PNT_6 | 20MAV00CT030 | #11 WORK THRUST PAD TEMP | RTD | 0 | 120 | C
1695 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD124AIN.PNT_1 | 2ATC:2BD124AIN.PNT_1 | 20TSIDEH03 | AXIAL DISPLACEMENT NO.1 OUTPUT | AI | -2 | 2 | um
1696 | 1 | UJRBG #20 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.2ATC:2BD124AIN.PNT_2 | 2ATC:2BD124AIN.PNT_2 | 20TSIDEH04 | AXIAL DISPLACEMENT NO.2 OUTPUT (4~20mA) | AI | -2 | 2 | um
555 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-08 | OPC.2HBP:AO113706.OUT | 2HBP:AO113706.OUT | 20LAB21AA101XB11 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
528 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-08 | OPC.2HDAS:ZT113203.PNT | 2HDAS:ZT113203.PNT | 20LAB21AA101XB12 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
529 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113204.PNT | 2HDAS:PT113204.PNT | 20LBA30CP101 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 20 | MPa
530 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113205.PNT | 2HDAS:PT113205.PNT | 20LBA30CP102 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 20 | MPa
835 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:TE113603.PNT | 2HDAS:TE113603.PNT | 20LBA30CT001 | HP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | °C
531 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113206.PNT | 2HDAS:PT113206.PNT | 20LBC30CP101 | HP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 6 | MPa
836 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:TE113604.PNT | 2HDAS:TE113604.PNT | 20LBC30CT001 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 400 | °C
550 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HBP:AO113701.OUT | 2HBP:AO113701.OUT | 20LBF10AA101XB11 | HP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
526 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:ZT113201.PNT | 2HDAS:ZT113201.PNT | 20LBF10AA101XB12 | HP BYPASS PRESS CONTROL VALVE CONTROL POSITION | AI | 0 | 100 | %
1699 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS CONTROL VALVE #20 | F296S-J0201-08 | OPC.2HDAS:PT113208.PNT | 2HDAS:PT113208.PNT | 20LAB21CP201 | HP BYPASS DESUPERHEATING WATER PRESS | AI | 0 | 25 | MPa
521 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113104.PNT | 2HDAS:PT113104.PNT | 20LBB30CP101 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 6 | MPa
833 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:TE113601.PNT | 2HDAS:TE113601.PNT | 20LBB30CT001 | LP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | °C
522 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113105.PNT | 2HDAS:PT113105.PNT | 20LBB40CP101 | LP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 2 | MPa
834 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:TE113602.PNT | 2HDAS:TE113602.PNT | 20LBB40CT001 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 200 | °C
1266 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2IDAS:TE121503.PNT | 2IDAS:TE121503.PNT | 20LBB41CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CON | TC | 0 | 400 | °C
1267 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2IDAS:TE121504.PNT | 2IDAS:TE121504.PNT | 20LBB42CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CON | TC | 0 | 400 | °C
552 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2LBP:AO113703.OUT | 2LBP:AO113703.OUT | 20LCE16AA101XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AO | 0 | 100 | %
519 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2HDAS:ZT113102.PNT | 2HDAS:ZT113102.PNT | 20LCE16AA101XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AI | 0 | 100 | %
553 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2LBP:AO113704.OUT | 2LBP:AO113704.OUT | 20LCE16AA102XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AO | 0 | 100 | %
527 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2HDAS:ZT113202.PNT | 2HDAS:ZT113202.PNT | 20LCE16AA102XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATI | AI | 0 | 100 | %
554 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2LBP:AO113705.OUT | 2LBP:AO113705.OUT | 20LCE17AA101XB11 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
520 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-07 | OPC.2HDAS:ZT113103.PNT | 2HDAS:ZT113103.PNT | 20LCE17AA101XB12 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | %
551 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2LBP:AO113702.OUT | 2LBP:AO113702.OUT | 20MAN10AA101XB11 | LP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | %
518 | 1 | UJRBG #20 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS CONTROL VALVE #20 | 50-F290S-J0201-04 | OPC.2HDAS:ZT113101.PNT | 2HDAS:ZT113101.PNT | 20MAN10AA101XB12 | LP BYPASS PRESS CONTROL VALVE POSITION | AI | 0 | 100 | %
1729 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 2 | HP TURBINE #2 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.2ATC:2BD124AIN.PNT_4 | 2ATC:2BD124AIN.PNT_4 | 20MAX20AA001XB12 | MSV2 POSITION | AI | 0 | 100 | %
1730 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 2 | HP TURBINE #2 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.2ATC:2BD12405AOUT.OUT | 2ATC:2BD12405AOUT.OUT | 20MAX20AA001XB11 | MSV2 CONTROL COMMAND | AO | 0 | 100 | %
1732 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 3 | HP TURBINE #2 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.2VALVE:2AD11105AOUT.OUT | 2VALVE:2AD11105AOUT.OUT | 20MAX10AA102XB11 | CV4 CONTROL COMMAND | AO | 0 | 100 | %
1731 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 3 | HP TURBINE #2 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.2VALVE:2AD111AIN.PNT_4 | 2VALVE:2AD111AIN.PNT_4 | 20MAX10AA102XB12 | CV4 POSITION | AI | 0 | 100 | %
1734 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 4 | HP TURBINE #2 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.2VALVE:2AD10605AOUT.OUT | 2VALVE:2AD10605AOUT.OUT | 20MAX10AA101XB11 | CV1 CONTROL COMMAND | AO | 0 | 100 | %
1733 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 4 | HP TURBINE #2 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.2VALVE:2AD106AIN.PNT_4 | 2VALVE:2AD106AIN.PNT_4 | 20MAX10AA101XB12 | CV1 POSITION | AI | 0 | 100 | %
1736 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 5 | HP TURBINE #2 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.2VALVE:2AD10705AOUT.OUT | 2VALVE:2AD10705AOUT.OUT | 20MAX20AA101XB11 | CV2 CONTROL COMMAND | AO | 0 | 100 | %
1735 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 5 | HP TURBINE #2 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.2VALVE:2AD107AIN.PNT_4 | 2VALVE:2AD107AIN.PNT_4 | 20MAX20AA101XB12 | CV2 POSITION | AI | 0 | 100 | %
1739 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 6 | HP TURBINE #2 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.2VALVE:2AD10805AOUT.OUT | 2VALVE:2AD10805AOUT.OUT | 20MAX20AA102XB11 | CV3 CONTROL COMMAND | AO | 0 | 100 | %
1738 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 6 | HP TURBINE #2 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.2VALVE:2AD108AIN.PNT_4 | 2VALVE:2AD108AIN.PNT_4 | 20MAX20AA102XB12 | CV3 POSITION | AI | 0 | 100 | %
476 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | 50-F290S-J0201-04 | OPC.2FDAS:PT086704.PNT | 2FDAS:PT086704.PNT | 20LBB11CP202 | IP GOV VALVE REAR STEAM PRESS (LEFT) | AI | 0 | 6 | MPa
1742 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296S-J0201-04 | OPC.2VALVE:2AD11205AOUT.OUT | 2VALVE:2AD11205AOUT.OUT | 20MAB10AA001XB11 | ICV1 CONTROL COMMAND | AO | 0 | 100 | %
1741 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296S-J0201-04 | OPC.2VALVE:2AD112AIN.PNT_4 | 2VALVE:2AD112AIN.PNT_4 | 20MAB10AA001XB12 | ICV1 POSITION | AI | 0 | 100 | %
1803 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296Z-J0201-04 | OPC.2ATC:2BD103AIN.PNT_1 | 2ATC:2BD103AIN.PNT_1 | 20LBB11CP201 | IP GOV VALVE FRONT STEAM PRESS (LEFT) | AI | 0 | 6 | MPa
1804 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 7 | REHEAT STOP INTERCEPTOR VALVE A (RIGTH) | F296Z-J0201-04 | OPC.2ATC:2BD106AIN.PNT_3 | 2ATC:2BD106AIN.PNT_3 | 20LBB11CT001 | REHEAT STEAM TEMP(LEFT) | TC | 0 | 600 | C
1745 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296S-J0201-04 | OPC.2VALVE:2AD11305AOUT.OUT | 2VALVE:2AD11305AOUT.OUT | 20MAB20AA001XB11 | ICV2 CONTROL COMMAND | AO | 0 | 100 | %
1744 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296S-J0201-04 | OPC.2VALVE:2AD113AIN.PNT_4 | 2VALVE:2AD113AIN.PNT_4 | 20MAB20AA001XB12 | ICV2 POSITION | AI | 0 | 100 | %
1805 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296Z-J0201-04 | OPC.2ATC:2BD103AIN.PNT_2 | 2ATC:2BD103AIN.PNT_2 | 20LBB12CP201 | IP GOV VALVE FRONT STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa
1806 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | F296Z-J0201-04 | OPC.2ATC:2BD106AIN.PNT_4 | 2ATC:2BD106AIN.PNT_4 | 20LBB12CT001 | REHEAT STEAM TEMP(RIGHT) | TC | 0 | 600 | C
483 | 1 | UJRBG #20 | 85 | TURBINE VALVE #2 | 8 | REHEAT STOP INTERCEPTOR VALVE B (LEFT) | 50-F290S-J0201-04 | OPC.2FDAS:PT086804.PNT | 2FDAS:PT086804.PNT | 20LBB12CP202 | IP GOV VALVE REAR STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa
1220 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F289S-K0606-01 | OPC.2IDAS:ZT121405.PNT | 2IDAS:ZT121405.PNT | 20DEHDCS01 | TURBINE POSITION | AI | 0 | 100
480 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:PT086801.PNT | 2FDAS:PT086801.PNT | 20LBA12CP202 | HP GOV VALVE STEAM PRESS | AI | 0 | 20 | MPa
781 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087505.PNT | 2FDAS:TE087505.PNT | 20LBC11CT001 | HP EXHAUSTING PIPE(LEFT) TOP TEMP | TC | 0 | 800 | °C
788 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087605.PNT | 2FDAS:TE087605.PNT | 20LBC11CT002 | HP EXHAUSTING PIPE(LEFT) BOTTOM TEMP | TC | 0 | 400 | °C
782 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087506.PNT | 2FDAS:TE087506.PNT | 20LBC12CT001 | HP EXHAUSTING PIPE(RIGHT) TOP TEMP | TC | 0 | 400 | °C
789 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087606.PNT | 2FDAS:TE087606.PNT | 20LBC12CT002 | HP EXHAUSTING PIPE(RIGHT) BOTTOM TEMP | TC | 0 | 400 | °C
1136 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120102.PNT | 2IDAS:PT120102.PNT | 20MAA10CP202 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1144 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120202.PNT | 2IDAS:PT120202.PNT | 20MAA10CP203 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1152 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2IDAS:PT120302.PNT | 2IDAS:PT120302.PNT | 20MAA10CP204 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
532 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2HDAS:PT113207.PNT | 2HDAS:PT113207.PNT | 20MAA10CP205 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
481 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-J0201-04 | OPC.2FDAS:PT086802.PNT | 2FDAS:PT086802.PNT | 20MAA10CP206 | HP SIXTH STAGE STEAM PRESS | AI | 0 | 10 | MPa
1347 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244705.PNT | 2HDAS:TE244705.PNT | 20MAA10CT010 | HP INNER & OUTER CYLINDER INTERLAY BAFFLE PLATE FRONT TEMP | TC | 0 | 500 | °C
1317 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244301.PNT | 2HDAS:TE244301.PNT | 20MAA10CT011 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(LEFT) | TC | 0 | 500 | °C
1318 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244302.PNT | 2HDAS:TE244302.PNT | 20MAA10CT012 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(LEFT) | TC | 0 | 500 | °C
1319 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244303.PNT | 2HDAS:TE244303.PNT | 20MAA10CT013 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(LEFT) | TC | 0 | 500 | °C
1323 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244401.PNT | 2HDAS:TE244401.PNT | 20MAA10CT014 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1324 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244402.PNT | 2HDAS:TE244402.PNT | 20MAA10CT015 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1325 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244403.PNT | 2HDAS:TE244403.PNT | 20MAA10CT016 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(RIGHT) | TC | 0 | 500 | °C
1320 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244304.PNT | 2HDAS:TE244304.PNT | 20MAA10CT023 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 500 | °C
1321 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244305.PNT | 2HDAS:TE244305.PNT | 20MAA10CT024 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 500 | °C
1322 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244306.PNT | 2HDAS:TE244306.PNT | 20MAA10CT025 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 500 | °C
1326 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244404.PNT | 2HDAS:TE244404.PNT | 20MAA10CT026 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 500 | °C
1327 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244405.PNT | 2HDAS:TE244405.PNT | 20MAA10CT027 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 500 | °C
1328 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244406.PNT | 2HDAS:TE244406.PNT | 20MAA10CT028 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 500 | °C
1333 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244505.PNT | 2HDAS:TE244505.PNT | 20MAA10CT029 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 500 | °C
1334 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244506.PNT | 2HDAS:TE244506.PNT | 20MAA10CT030 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 500 | °C
1335 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244507.PNT | 2HDAS:TE244507.PNT | 20MAA10CT031 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 500 | °C
1340 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244605.PNT | 2HDAS:TE244605.PNT | 20MAA10CT032 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 500 | °C
1341 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244606.PNT | 2HDAS:TE244606.PNT | 20MAA10CT033 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 500 | °C
1342 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F290S-K0301-03 | OPC.2HDAS:TE244607.PNT | 2HDAS:TE244607.PNT | 20MAA10CT034 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 500 | °C
450 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | 50-F289S-K0302-03 | OPC.2FDAS:AI073607.PNT | 2FDAS:AI073607.PNT | 20TSIDCS21 | TURBINE SPEED (4~20mA) | AI | 0 | 5000 | rpm
1746 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296S-K0606 | OPC.2VALVE:2AD11106AOUT.OUT | 2VALVE:2AD11106AOUT.OUT | 20DEHDCSAO01 | TURBINE POSITION | AO | 0 | 100 | %
1748 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2VALVE:2AD111AIN.PNT_1 | 2VALVE:2AD111AIN.PNT_1 | 20LBA11CP201 | MAIN STEAM PRESS(LEFT) | AI | 0 | 18 | MPa
1749 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2ATC:2BD106AIN.PNT_1 | 2ATC:2BD106AIN.PNT_1 | 20LBA11CT001 | MAIN STEAM TEMPERATURE (LEFT) | TC | 0 | 600 | C
1750 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2VALVE:2AD112AIN.PNT_1 | 2VALVE:2AD112AIN.PNT_1 | 20LBA12CP201 | MAIN STEAM PRESS(RIGHT) | AI | 0 | 18 | MPa
1751 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2ATC:2BD106AIN.PNT_2 | 2ATC:2BD106AIN.PNT_2 | 20LBA12CT001 | MAIN STEAM TEMPERATURE (RIGHT) | TC | 0 | 600 | C
1756 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2VALVE:2AD107AIN.PNT_2 | 2VALVE:2AD107AIN.PNT_2 | 20MAA10CP201 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa
1763 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2VALVE:2AD108AIN.PNT_2 | 2VALVE:2AD108AIN.PNT_2 | 20MAA10CP207 | HP EXHAUSTING STEAM PRESS | AI | 0 | 5 | MPa
1764 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2ATC:2BD107AIN.PNT_2 | 2ATC:2BD107AIN.PNT_2 | 20MAA10CT001 | HP EXHAUSTING TEMP (UPPER) | TC | 0 | 600 | C
1765 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2ATC:2BD111AIN.PNT_1 | 2ATC:2BD111AIN.PNT_1 | 20MAA10CT002 | HP EXHAUSTING TEMP (LOWER) | TC | 0 | 600 | C
1766 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-04 | OPC.2ATC:2BD107AIN.PNT_1 | 2ATC:2BD107AIN.PNT_1 | 20MAA10CT003 | STEAM TEMP AFTER HP GOV STAGE | TC | 0 | 600 | C
1767 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_5 | 2ATC:2BD108AIN.PNT_5 | 20MAA10CT004 | HP EXHAUSTING UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C
1768 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_6 | 2ATC:2BD108AIN.PNT_6 | 20MAA10CT005 | HP EXHAUSTING BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C
1769 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD107AIN.PNT_4 | 2ATC:2BD107AIN.PNT_4 | 20MAA10CT006 | HP INNER CYLINDER UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C
1770 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD107AIN.PNT_6 | 2ATC:2BD107AIN.PNT_6 | 20MAA10CT007 | HP INNER CYLINDER UPPER HALF OUTER WALL TEMP | TC | 0 | 600 | C
1771 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD107AIN.PNT_5 | 2ATC:2BD107AIN.PNT_5 | 20MAA10CT008 | HP INNER CYLINDER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C
1772 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD107AIN.PNT_7 | 2ATC:2BD107AIN.PNT_7 | 20MAA10CT009 | HP INNER CYLINDER BOTTOM HALF OUTER WALL TEMP | TC | 0 | 600 | C
1780 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD106AIN.PNT_7 | 2ATC:2BD106AIN.PNT_7 | 20MAA10CT017 | HP MSV INNER WALL METAL TEMP (LEFT) | TC | 0 | 600 | C
1781 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD106AIN.PNT_5 | 2ATC:2BD106AIN.PNT_5 | 20MAA10CT018 | HP MSV OUTER WALL METAL TEMP | TC | 0 | 600 | C
1782 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD106AIN.PNT_8 | 2ATC:2BD106AIN.PNT_8 | 20MAA10CT019 | HP MSV INNER WALL METAL TEMP | TC | 0 | 600 | C
1783 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD106AIN.PNT_6 | 2ATC:2BD106AIN.PNT_6 | 20MAA10CT020 | HP MSV OUTER WALL METAL TEMP (RIGHT) | TC | 0 | 600 | C
1784 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD111AIN.PNT_4 | 2ATC:2BD111AIN.PNT_4 | 20MAA10CT021 | HP MSCV INNER WALL METAL TEMP | TC | 0 | 600 | C
1785 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296Z-J0201-46 | OPC.2ATC:2BD111AIN.PNT_5 | 2ATC:2BD111AIN.PNT_5 | 20MAA10CT022 | HP MSCV OUTER WALL METAL TEMP | TC | 0 | 600 | C
1799 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296S-J0201-19 | OPC.2VALVE:2AD113AIN.PNT_1 | 2VALVE:2AD113AIN.PNT_1 | 20TSIDEH01 | ECCENTRICITY OUTPUT (4~20mA) | AI | 0 | 100 | um
1800 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296S-J0201-19 | OPC.2VALVE:2AD111AIN.PNT_3 | 2VALVE:2AD111AIN.PNT_3 | 20TSIDEH02 | HP/IP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | -7 | 9 | um
1801 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296S-J0201-19 | OPC.2ATC:2BD103AIN.PNT_5 | 2ATC:2BD103AIN.PNT_5 | 20TSIDEH06 | HP CYLINDER(LEFT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm
1802 | 1 | UJRBG #20 | 86 | TURBINE #2 | 1 | HP TURBINE #20 | F296S-J0201-19 | OPC.2ATC:2BD103AIN.PNT_6 | 2ATC:2BD103AIN.PNT_6 | 20TSIDEH07 | HP CYLINDER(RIGHT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm
482 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:PT086803.PNT | 2FDAS:PT086803.PNT | 20MAB10CP202 | IP THIRD STAGE STEAM PRESS | AI | 0 | 2 | MPa
1807 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-04 | OPC.2VALVE:2AD108AIN.PNT_3 | 2VALVE:2AD108AIN.PNT_3 | 20MAB10CP201 | IP EXHAUSTING STEAM PRESS | AI | 0 | 1 | MPa
1809 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-04 | OPC.2ATC:2BD107AIN.PNT_3 | 2ATC:2BD107AIN.PNT_3 | 20MAB10CT001 | IP EXHAUSTING STEAM TEMP | TC | 0 | 600 | C
1810 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_2 | 2ATC:2BD108AIN.PNT_2 | 20MAB10CT002 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF INNER TEMP | TC | 0 | 600 | C
1811 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_4 | 2ATC:2BD108AIN.PNT_4 | 20MAB10CT003 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF OUTER TEMP | TC | 0 | 600 | C
1812 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_1 | 2ATC:2BD108AIN.PNT_1 | 20MAB10CT004 | HP/IP OUTER CYLINDER IP STEAM INLET UPPER HALF INNER TEMP | TC | 0 | 600 | C
1813 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_3 | 2ATC:2BD108AIN.PNT_3 | 20MAB10CT005 | HP/IP OUTER CYLINDER IP STEAM INLETA UPPER HALF OUTER TEMP | TC | 0 | 600 | C
1814 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_8 | 2ATC:2BD108AIN.PNT_8 | 20MAB10CT006 | IP EXHAUSTING BOTTOM HALF INNER METAL TEMP | TC | 0 | 600 | C
1815 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD108AIN.PNT_7 | 2ATC:2BD108AIN.PNT_7 | 20MAB10CT007 | IP EXHAUSTING UPPER HALF INNER METAL TEMP | TC | 0 | 600 | C
1816 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD111AIN.PNT_3 | 2ATC:2BD111AIN.PNT_3 | 20MAB10CT008 | CLAPBOARD BOTTOM HALF INNER TEMP | TC | 0 | 600 | C
1817 | 1 | UJRBG #20 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #20 | F296Z-J0201-46 | OPC.2ATC:2BD111AIN.PNT_2 | 2ATC:2BD111AIN.PNT_2 | 20MAB10CT009 | CLAPBOARD UPPER HALF INNER TEMP | TC | 0 | 600 | C
674 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:RT087701.PNT | 2FDAS:RT087701.PNT | 20MAC10CT001B | LP EXHAUSTING STEAM TEMP(FRONT & RIGHT) | RTD | 0 | 400 | °C
675 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:RT087702.PNT | 2FDAS:RT087702.PNT | 20MAC10CT002B | LP EXHAUSTING STEAM TEMP(REAR & LEFT) | RTD | 0 | 800 | °C
780 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087504.PNT | 2FDAS:TE087504.PNT | 20MAC10CT003 | BACKWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 800 | °C
787 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087604.PNT | 2FDAS:TE087604.PNT | 20MAC10CT004 | FORWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 800 | °C
777 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087501.PNT | 2FDAS:TE087501.PNT | 20MAC10CT005 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 800 | °C
784 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087601.PNT | 2FDAS:TE087601.PNT | 20MAC10CT006 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 800 | °C
778 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087502.PNT | 2FDAS:TE087502.PNT | 20MAC10CT007 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 800 | °C
785 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2FDAS:TE087602.PNT | 2FDAS:TE087602.PNT | 20MAC10CT008 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 800 | °C
1818 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2ATC:1BD116AIN.PNT_3 | 2ATC:2BD116AIN.PNT_3 | 20MAC10CT001A | LP EXHAUSTING STEAM TEMP（FRONT & RIGHT） | RTD | 0 | 120 | C
1820 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2ATC:1BD116AIN.PNT_4 | 2ATC:2BD116AIN.PNT_4 | 20MAC10CT002A | LP EXHAUSTING STEAM TEMP（BACK & LEFT） | RTD | 0 | 120 | C
1828 | 1 | UJRBG #20 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #20 | 50-F290S-J0201-04 | OPC.2ATC:1BD124AIN.PNT_3 | 2ATC:2BD124AIN.PNT_3 | 20TSIDEH05 | LP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | 0 | 16 | um
1830 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060501.PNT | 0EDAS:LT060501.PNT | 20PAA10CL001XR01 | UPSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 2A | AI | 0 | 10 | m
1831 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060502.PNT | 0EDAS:LT060502.PNT | 20PAA10CL002XR01 | DOWNSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 2A | AI | 0 | 10 | m
1832 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060503.PNT | 0EDAS:LT060503.PNT | 20PAA10CL003XR01 | UPSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 2A | AI | 0 | 12 | m
1833 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060504.PNT | 0EDAS:LT060504.PNT | 20PAA10CL004XR01 | DOWNSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 2A | AI | 0 | 12 | m
1831 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060103.PNT | 0EDAS:LT060103.PNT | 20PAC10CL001XR01 | SEAWATER INTAKE WATER PIT 2A LEVEL TRANSMITTER A | AI | 0 | 10 | m
1832 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060203.PNT | 0EDAS:LT060203.PNT | 20PAC10CL002XR01 | SEAWATER INTAKE WATER PIT 2A LEVEL TRANSMITTER B | AI | 0 | 10 | m
1833 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:LT060303.PNT | 0EDAS:LT060303.PNT | 20PAC10CL003XR01 | SEAWATER INTAKE WATER PIT 2A LEVEL TRANSMITTER C | AI | 0 | 10 | m
1835 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:AI060603.PNT | 0EDAS:AI060603.PNT | 20PAC10GC001XR01 | #0 CWP 2A DISCHAREG VALVE OPENING | AI | 0 | 100 | %
1829 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:CT060307.PNT | 0EDAS:CT060307.PNT | 00BCD12CE001XQ01 | CIRCULATING WATER PUMP 2A MOTOR CURRENT | AI | 0 | 300 | A
1837 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061501.PNT | 0EDAS:RT061501.PNT | 20PAC10CT001XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE #1 (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1838 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061601.PNT | 0EDAS:RT061601.PNT | 20PAC10CT002XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE#2 (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1839 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061502.PNT | 0EDAS:RT061502.PNT | 20PAC10CT003XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE #1(S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1840 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061602.PNT | 0EDAS:RT061602.PNT | 20PAC10CT004XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE #2 (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1841 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061503.PNT | 0EDAS:RT061503.PNT | 20PAC10CT005XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE #1 (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1842 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061603.PNT | 0EDAS:RT061603.PNT | 20PAC10CT006XR01 | CIRC.WATER PUMP 2A WINDING TEMPERATURE #2(T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1843 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061504.PNT | 0EDAS:RT061504.PNT | 20PAC10CT007XR01 | CIRC.WATER PUMP 2A GUIDE BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1844 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061604.PNT | 0EDAS:RT061604.PNT | 20PAC10CT008XR01 | CIRC.WATER PUMP 2A GUIDE BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1845 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061505.PNT | 0EDAS:RT061505.PNT | 20PAC10CT009XR01 | CIRC.WATER PUMP 2A THRUST BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1846 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061605.PNT | 0EDAS:RT061605.PNT | 20PAC10CT010XR01 | CIRC.WATER PUMP 2A THRUST BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1847 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:RT061506.PNT | 0EDAS:RT061506.PNT | 20PAC10CT011XR01 | CIRC.WATER PUMP 2A LOWER MOTOR BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1848 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:AI060106.PNT | 0EDAS:AI060106.PNT | 20PAC10CY001XR01 | CIRC. WATER PUMP 2A HORIZONTAL VIBRATION 1 | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:AI060703.PNT | 0EDAS:AI060703.PNT | 20PAC10CY002XR01 | CIRC. WATER PUMP 2A HORIZONTAL VIBRATION 2 | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:AI060107.PNT | 0EDAS:AI060107.PNT | 20PAC10CY003XR01 | CIRC.WATER PUMP 2A VERTICAL VIBRATION | AI | 0 | 7 | mm/s
1849 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.0EDAS:PT060208.PNT | 0EDAS:PT060208.PNT | 20PAB30CP001XR01 | CIRCULATING WATER DISCHARGE HEADER PRESSURE | AI | 0 | 0.6 | MPa
1851 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060505.PNT | 0EDAS:LT060505.PNT | 20PAA20CL001XR01 | UPSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 2B | AI | 0 | 10 | m
1852 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060506.PNT | 0EDAS:LT060506.PNT | 20PAA20CL002XR01 | DOWNSTREAM BARSCREEN LEVEL TRANSMITTER - UNIT 2B | AI | 0 | 10 | m
1853 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060507.PNT | 0EDAS:LT060507.PNT | 20PAA20CL003XR01 | UPSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 2B | AI | 0 | 12 | m
1854 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060508.PNT | 0EDAS:LT060508.PNT | 20PAA20CL004XR01 | DOWNSTREAM BANDSCREEN LEVEL TRANSMITTER - UNIT 2B | AI | 0 | 12 | m
1852 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060104.PNT | 0EDAS:LT060104.PNT | 20PAC20CL001XR01 | SEAWATER INTAKE WATER PIT 2B LEVEL TRANSMITTER A | AI | 0 | 10 | m
1853 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060204.PNT | 0EDAS:LT060204.PNT | 20PAC20CL002XR01 | SEAWATER INTAKE WATER PIT 2B LEVEL TRANSMITTER B | AI | 0 | 10 | m
1854 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:LT060304.PNT | 0EDAS:LT060304.PNT | 20PAC20CL003XR01 | SEAWATER INTAKE WATER PIT 2B LEVEL TRANSMITTER C | AI | 0 | 10 | m
1855 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:AI060604.PNT | 0EDAS:AI060604.PNT | 20PAC20GC001XR01 | #0 CWP 2B DISCHAREG VALVE OPENING | AI | 0 | 100 | %
1850 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:CT060308.PNT | 0EDAS:CT060308.PNT | 00BCD13CE001XQ01 | CIRCULATING WATER PUMP 2B MOTOR CURRENT | AI | 0 | 300 | A
1857 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061701.PNT | 0EDAS:RT061701.PNT | 20PAC20CT001XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1858 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061801.PNT | 0EDAS:RT061801.PNT | 20PAC20CT002XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (R PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1859 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061702.PNT | 0EDAS:RT061702.PNT | 20PAC20CT003XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1860 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061802.PNT | 0EDAS:RT061802.PNT | 20PAC20CT004XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (S PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1861 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061703.PNT | 0EDAS:RT061703.PNT | 20PAC20CT005XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1862 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061803.PNT | 0EDAS:RT061803.PNT | 20PAC20CT006XR01 | CIRC.WATER PUMP 2B WINDING TEMPERATURE (T PHASE) | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140
1863 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061704.PNT | 0EDAS:RT061704.PNT | 20PAC20CT007XR01 | CIRC.WATER PUMP 2B GUIDE BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1864 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061804.PNT | 0EDAS:RT061804.PNT | 20PAC20CT008XR01 | CIRC.WATER PUMP 2B GUIDE BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1865 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061705.PNT | 0EDAS:RT061705.PNT | 20PAC20CT009XR01 | CIRC.WATER PUMP 2B THRUST BEARING TEMPERATURE A | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1866 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061805.PNT | 0EDAS:RT061805.PNT | 20PAC20CT010XR01 | CIRC.WATER PUMP 2B THRUST BEARING TEMPERATURE B | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1867 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:RT061706.PNT | 0EDAS:RT061706.PNT | 20PAC20CT011XR01 | CIRC.WATER PUMP 2B LOWER MOTOR BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85
1868 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:AI060206.PNT | 0EDAS:AI060206.PNT | 20PAC20CY001XR01 | CIRC. WATER PUMP 2B HORIZONTAL VIBRATION 1 | AI | 0 | 7 | mm/s
1869 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:AI060207.PNT | 0EDAS:AI060207.PNT | 20PAC20CY003XR01 | CIRC.WATER PUMP 2B VERTICAL VIBRATION | AI | 0 | 7 | mm/s
1869 | 3 | UJRBG COMMON | 2 | COOLING WATER SYSTEM #1 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.0EDAS:AI060704.PNT | 0EDAS:AI060704.PNT | 20PAC20CY002XR01 | CIRC. WATER PUMP 2B HORIZONTAL VIBRATION 2 | AI | 0 | 7 | mm/s