## UNIT#1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL11CF101 |  | 10HHL11CF101 | Side-A front upper secondary air flow | AI | 0 | 999999 | Nm3/h
2 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL12CF101 |  | 10HHL12CF101 | Side-A back upper secondary air flow | AI | 0 | 999999 | Nm3/h
3 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL13CF101 |  | 10HHL13CF101 | Side-A front lower secondary air flow | AI | 0 | 999999 | Nm3/h
4 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL14CF101 |  | 10HHL14CF101 | Side-A back lower secondary air flow | AI | 0 | 999999 | Nm3/h
5 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL21CF101 |  | 10HHL21CF101 | Side-B front upper secondary air flow | AI | 0 | 999999 | Nm3/h
6 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL22CF101 |  | 10HHL22CF101 | Side-B back upper secondary air flow | AI | 0 | 999999 | Nm3/h
7 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL23CF101 |  | 10HHL23CF101 | Side-B front lower secondary air flow | AI | 0 | 999999 | Nm3/h
8 | Manipulated Variable | Secondary Air Flow | KALTIM1.SIGNAL.AI.10HHL24CF101 |  | 10HHL24CF101 | Side-B back lower secondary air flow | AI | 0 | 999999 | Nm3/h
9 | Disturbance Variable | Coal Flow | 10HFB10AF901XQ02 |  | 10HFB10AF901XQ02 | Total flow rate coal Fuel #1 | CALC | 0 | 100 | t/h | [6 empty] | (KALTIM1.SIGNAL.AI.10HFB10AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB20AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB30AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB40AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB50AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB60AF001XQ02)
10 | Disturbance Variable | Load | KALTIM1.SIGNAL.AI.10MKA01CE004 |  | 10MKA01CE004 | #1 Gen. Active Power | AI | 0 | 132 | MW
11 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HHL02CF101 |  | 10HHL02CF101 | A air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
12 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HHL03CF101 |  | 10HHL03CF101 | B air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
13 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HHL04CF101 |  | 10HHL04CF101 | Upper bed burner hot primary air flow | AI | 0 | 999999 | Nm3/h
14 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW11CF101 |  | 10HEW11CF101 | A coal feeder seal air flow | AI | 0 | 4000 | m3/h
15 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE11CF101 |  | 10HFE11CF101 | A inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
16 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE12CF101 |  | 10HFE12CF101 | A inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
17 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW12CF101 |  | 10HEW12CF101 | B coal feeder seal air flow | AI | 0 | 4000 | m3/h
18 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE21CF101 |  | 10HFE21CF101 | B inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
19 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE22CF101 |  | 10HFE22CF101 | B inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
20 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE32CF101 |  | 10HFE32CF101 | C inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
21 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW13CF101 |  | 10HEW13CF101 | C coal feeder seal air flow | AI | 0 | 4000 | m3/h
22 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE31CF101 |  | 10HFE31CF101 | C inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
23 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW14CF101 |  | 10HEW14CF101 | D coal feeder seal air flow | AI | 0 | 4000 | m3/h
24 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE41CF101 |  | 10HFE41CF101 | D inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
25 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE42CF101 |  | 10HFE42CF101 | D inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
26 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW15CF101 |  | 10HEW15CF101 | E coal feeder seal air flow | AI | 0 | 4000 | m3/h
27 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE51CF101 |  | 10HFE51CF101 | E inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
28 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE52CF101 |  | 10HFE52CF101 | E inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
29 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HEW16CF101 |  | 10HEW16CF101 | F coal feeder seal air flow | AI | 0 | 4000 | m3/h
30 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE61CF101 |  | 10HFE61CF101 | F inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
31 | Disturbance Variable | Primary Air Flow | KALTIM1.SIGNAL.AI.10HFE62CF101 |  | 10HFE62CF101 | F inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
32 | Constrain Variable | Oxygen Sensor | KALTIM1.SIGNAL.AI.10HBK31CQ101 |  | 10HBK31CQ101 | Side-A air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
33 | Constrain Variable | Oxygen Sensor | KALTIM1.SIGNAL.AI.10HBK41CQ101 |  | 10HBK41CQ101 | Side-B air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
34 | Constrain Variable | Furnace Pressure | KALTIM1.SIGNAL.AI.10HBK11CP101 |  | 10HBK11CP101 | Side-A furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
35 | Constrain Variable | Furnace Pressure | KALTIM1.SIGNAL.AI.10HBK21CP101 |  | 10HBK21CP101 | Side-B furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
36 | Constrain Variable | Bed Differential Pressure | KALTIM1.SIGNAL.AI.10HBK11CP102 |  | 10HBK11CP102 | Side-A furnace differencial pressure | AI | -500 | 4000 | Pa
37 | Constrain Variable | Bed Differential Pressure | KALTIM1.SIGNAL.AI.10HBK21CP102 |  | 10HBK21CP102 | Side-B furnace differencial pressure | AI | -500 | 4000 | Pa
38 | Constrain Variable | Bed Temperature | 10HBK11CT902 |  | 10HBK11CT902 | Boiler Bed Temperature | CALC | 0 | 1200 | ℃
39 | Constrain Variable | Furnace Temperature | KALTIM1.SIGNAL.TC.10HBK11CT101 |  | 10HBK11CT101 | Side-A furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950
40 | Constrain Variable | Furnace Temperature | KALTIM1.SIGNAL.TC.10HBK21CT101 |  | 10HBK21CT101 | Side-B furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950
41 | Constrain Variable | Stack NOx | KALTIM 0.SIGNAL.AI.10HNA30CQ104 |  | 10HNA30CQ104 | Flue gas NOX unit 1 | AI | 0 | 2000 | mg/m3
42 | Constrain Variable | Stack CO | KALTIM 0.SIGNAL.AI.10HNA30CQ105 |  | 10HNA30CQ105 | Flue gas CO unit 1 | AI | 0 | 500 | mg/m3
43 | Efficiency Variable | Coal Flow | 10HFB10AF901XQ02 |  | 10HFB10AF901XQ02 | Total flow rate coal Fuel #1 | AI | 0 | 300 | T/H
44 | Efficiency Variable | Main Steam Pressure | KALTIM1.SIGNAL.AI.10LBA01CP101 |  | 10LBA01CP101 | Side-A HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10
45 | Efficiency Variable | Main Steam Pressure | KALTIM1.SIGNAL.AI.10LBA02CP101 |  | 10LBA02CP101 | Side-B HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10
46 | Efficiency Variable | Feed Water Pressure | KALTIM1.SIGNAL.AI.10LAB50CP102 |  | 10LAB50CP102 | Economizer inlet water pressure | AI | 0 | 15 | MPa
47 | Efficiency Variable | SH Spray Water Pressure | KALTIM1.SIGNAL.AI.10LAE20CP101 |  | 10LAE20CP101 | Desuperheater water filter outlet pressure | AI | 0 | 15 | MPa
48 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA01CT101 |  | 10LBA01CT101 | Side-A HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545
49 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA01CT102 |  | 10LBA01CT102 | Side-A HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545
50 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA01CT103 |  | 10LBA01CT103 | Side-A HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545
51 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA02CT101 |  | 10LBA02CT101 | Side-B HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545
52 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA02CT102 |  | 10LBA02CT102 | Side-B HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545
53 | Efficiency Variable | Main Steam Temperature | KALTIM1.SIGNAL.TC.10LBA02CT103 |  | 10LBA02CT103 | Side-B HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545
54 | Efficiency Variable | Feed Water Temperature | KALTIM1.SIGNAL.TC.10LAB50CT102 |  | 10LAB50CT102 | Main boiler feed water temperature | TC | 0 | 400 | ℃ |  |  |  | 545
55 | Efficiency Variable | SH Spray Temperature | KALTIM1.SIGNAL.RTD.10LAE20CT101 |  | 10LAE20CT101 | Desuperheater water filter outlet temperature | RTD | 0 | 200 | ℃
56 | Efficiency Variable | Main Steam Flow | KALTIM1.SIGNAL.AI.AM11CCS20A01 |  | 10LBA10CF101 | Main steam flow | AI | 0 | 500 | t/h
57 | Efficiency Variable | Feed Water Flow | KALTIM1.SIGNAL.AI.10LAB50CF101 |  | 10LAB50CF101 | Main boiler feed water flow 1 | AI | 0 | 1000 | t/h
58 | Efficiency Variable | Feed Water Flow | KALTIM1.SIGNAL.AI.10LAB50CF102 |  | 10LAB50CF102 | Main boiler feed water flow 2 | AI | 0 | 1000 | t/h
59 | Efficiency Variable | SH Spray Water Flow | KALTIM1.SIGNAL.AI.10LAE21CF101 |  | 10LAE21CF101 | Side-A primary desuperheater water flow | AI | 0 | 100 | t/h
60 | Efficiency Variable | SH Spray Water Flow | KALTIM1.SIGNAL.AI.10LAE22CF101 |  | 10LAE22CF101 | Side-B primary desuperheater water flow | AI | 0 | 100 | t/h
61 | Efficiency Variable | SH Spray Water Flow | KALTIM1.SIGNAL.AI.10LAE23CF101 |  | 10LAE23CF101 | Side-A secondary desuperheater water flow | AI | 0 | 100 | t/h
62 | Efficiency Variable | SH Spray Water Flow | KALTIM1.SIGNAL.AI.10LAE24CF101 |  | 10LAE24CF101 | Side-B secondary desuperheater water flow | AI | 0 | 999999 | t/h
63 | Control Variable | FD Fan Air Flow | KALTIM1.SIGNAL.AO.10HLB30AA101XQ11 |  | 10HLB30AA101XQ11 | A secondary air fan inlet control valve control command | AO | 0 | 100 | %
64 | Control Variable | FD Fan Air Flow | KALTIM1.SIGNAL.AO.10HLB40AA101XQ11 |  | 10HLB40AA101XQ11 | B secondary air fan inlet control valve control command | AO | 0 | 100 | %

## UNIT#2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL11CF101 |  | 20HHL11CF101 | Side-A front upper secondary air flow | AI | 0 | 999999 | Nm3/h
2 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL12CF101 |  | 20HHL12CF101 | Side-A back upper secondary air flow | AI | 0 | 999999 | Nm3/h
3 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL13CF101 |  | 20HHL13CF101 | Side-A front lower secondary air flow | AI | 0 | 999999 | Nm3/h
4 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL14CF101 |  | 20HHL14CF101 | Side-A back lower secondary air flow | AI | 0 | 999999 | Nm3/h
5 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL21CF101 |  | 20HHL21CF101 | Side-B front upper secondary air flow | AI | 0 | 999999 | Nm3/h
6 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL22CF101 |  | 20HHL22CF101 | Side-B back upper secondary air flow | AI | 0 | 999999 | Nm3/h
7 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL23CF101 |  | 20HHL23CF101 | Side-B front lower secondary air flow | AI | 0 | 999999 | Nm3/h
8 | Manipulated Variable | Secondary Air Flow | KALTIM2.SIGNAL.AI.20HHL24CF101 |  | 20HHL24CF101 | Side-B back lower secondary air flow | AI | 0 | 999999 | Nm3/h
9 | Disturbance Variable | Coal Flow | 20HFB10AF901XQ02 |  | 20HFB10AF901XQ02 | Total flow rate coal Fuel #2 | CALC | 0 | 100 | t/h | [6 empty] | (KALTIM1.SIGNAL.AI.10HFB10AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB20AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB30AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB40AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB50AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB60AF001XQ02)
10 | Disturbance Variable | Load | KALTIM2.SIGNAL.AI.20MKA01CE004 |  | 20MKA01CE004 | #2 Gen. Active Power | AI | 0 | 132 | MW
11 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HHL02CF101 |  | 20HHL02CF101 | A air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
12 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HHL03CF101 |  | 20HHL03CF101 | B air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
13 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HHL04CF101 |  | 20HHL04CF101 | Upper bed burner hot primary air flow | AI | 0 | 999999 | Nm3/h
14 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW11CF101 |  | 20HEW11CF101 | A coal feeder seal air flow | AI | 0 | 4000 | m3/h
15 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE11CF101 |  | 20HFE11CF101 | A inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
16 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE12CF101 |  | 20HFE12CF101 | A inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
17 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW12CF101 |  | 20HEW12CF101 | B coal feeder seal air flow | AI | 0 | 4000 | m3/h
18 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE21CF101 |  | 20HFE21CF101 | B inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
19 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE22CF101 |  | 20HFE22CF101 | B inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
20 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE32CF101 |  | 20HFE32CF101 | C inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
21 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW13CF101 |  | 20HEW13CF101 | C coal feeder seal air flow | AI | 0 | 4000 | m3/h
22 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE31CF101 |  | 20HFE31CF101 | C inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
23 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW14CF101 |  | 20HEW14CF101 | D coal feeder seal air flow | AI | 0 | 4000 | m3/h
24 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE41CF101 |  | 20HFE41CF101 | D inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
25 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE42CF101 |  | 20HFE42CF101 | D inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
26 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW15CF101 |  | 20HEW15CF101 | E coal feeder seal air flow | AI | 0 | 4000 | m3/h
27 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE51CF101 |  | 20HFE51CF101 | E inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
28 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE52CF101 |  | 20HFE52CF101 | E inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
29 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HEW16CF101 |  | 20HEW16CF101 | F coal feeder seal air flow | AI | 0 | 4000 | m3/h
30 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE61CF101 |  | 20HFE61CF101 | F inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
31 | Disturbance Variable | Primary Air Flow | KALTIM2.SIGNAL.AI.20HFE62CF101 |  | 20HFE62CF101 | F inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
32 | Constrain Variable | Oxygen Sensor | KALTIM2.SIGNAL.AI.20HBK31CQ101 |  | 20HBK31CQ101 | Side-A air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
33 | Constrain Variable | Oxygen Sensor | KALTIM2.SIGNAL.AI.20HBK41CQ101 |  | 20HBK41CQ101 | Side-B air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
34 | Constrain Variable | Furnace Pressure | KALTIM2.SIGNAL.AI.20HBK11CP101 |  | 20HBK11CP101 | Side-A furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
35 | Constrain Variable | Furnace Pressure | KALTIM2.SIGNAL.AI.20HBK21CP101 |  | 20HBK21CP101 | Side-B furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
36 | Constrain Variable | Bed Differential Pressure | KALTIM2.SIGNAL.AI.20HBK11CP102 |  | 20HBK11CP102 | Side-A furnace differencial pressure | AI | -500 | 4000 | Pa
37 | Constrain Variable | Bed Differential Pressure | KALTIM2.SIGNAL.AI.20HBK21CP102 |  | 20HBK21CP102 | Side-B furnace differencial pressure | AI | -500 | 4000 | Pa
38 | Constrain Variable | Bed Temperature | 20HBK11CT902 |  | 20HBK11CT902 | Boiler Bed Temperature | CALC | 0 | 1200 | ℃
39 | Constrain Variable | Furnace Temperature | KALTIM2.SIGNAL.TC.20HBK11CT101 |  | 20HBK11CT101 | Side-A furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950
40 | Constrain Variable | Furnace Temperature | KALTIM2.SIGNAL.TC.20HBK21CT101 |  | 20HBK21CT101 | Side-B furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950
41 | Constrain Variable | Stack NOx | KALTIM 0.SIGNAL.AI.20HNA30CQ104 |  | 20HNA30CQ104 | Flue gas NOX unit 2 | AI | 0 | 2000 | mg/m3
42 | Constrain Variable | Stack CO | KALTIM 0.SIGNAL.AI.20HNA30CQ105 |  | 20HNA30CQ105 | Flue gas CO unit 2 | AI | 0 | 500 | mg/m3
43 | Efficiency Variable | Coal Flow | 20HFB10AF901XQ02 |  | 20HFB10AF901XQ02 | Total flow rate coal Fuel #2 | AI | 0 | 300 | T/H
44 | Efficiency Variable | Main Steam Pressure | KALTIM2.SIGNAL.AI.20LBA01CP101 |  | 20LBA01CP101 | Side-A HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10
45 | Efficiency Variable | Main Steam Pressure | KALTIM2.SIGNAL.AI.20LBA02CP101 |  | 20LBA02CP101 | Side-B HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10
46 | Efficiency Variable | Feed Water Pressure | KALTIM2.SIGNAL.AI.20LAB50CP102 |  | 20LAB50CP102 | Economizer inlet water pressure | AI | 0 | 15 | MPa
47 | Efficiency Variable | SH Spray Water Pressure | KALTIM2.SIGNAL.AI.20LAE20CP101 |  | 20LAE20CP101 | Desuperheater water filter outlet pressure | AI | 0 | 15 | MPa
48 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA01CT101 |  | 20LBA01CT101 | Side-A HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545
49 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA01CT102 |  | 20LBA01CT102 | Side-A HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545
50 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA01CT103 |  | 20LBA01CT103 | Side-A HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545
51 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA02CT101 |  | 20LBA02CT101 | Side-B HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545
52 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA02CT102 |  | 20LBA02CT102 | Side-B HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545
53 | Efficiency Variable | Main Steam Temperature | KALTIM2.SIGNAL.TC.20LBA02CT103 |  | 20LBA02CT103 | Side-B HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545
54 | Efficiency Variable | Feed Water Temperature | KALTIM2.SIGNAL.TC.20LAB50CT102 |  | 20LAB50CT102 | Main boiler feed water temperature | TC | 0 | 400 | ℃ |  |  |  | 545
55 | Efficiency Variable | SH Spray Temperature | KALTIM2.SIGNAL.RTD.20LAE20CT101 |  | 20LAE20CT101 | Desuperheater water filter outlet temperature | RTD | 0 | 200 | ℃
56 | Efficiency Variable | Main Steam Flow | KALTIM2.SIGNAL.AO.20LBA10CF101 |  | 20LBA10CF101 | Main steam flow | AI | 0 | 500 | t/h
57 | Efficiency Variable | Feed Water Flow | KALTIM2.SIGNAL.AI.20LAB50CF101 |  | 20LAB50CF101 | Main boiler feed water flow 1 | AI | 0 | 1000 | t/h
58 | Efficiency Variable | Feed Water Flow | KALTIM2.SIGNAL.AI.20LAB50CF102 |  | 20LAB50CF102 | Main boiler feed water flow 2 | AI | 0 | 1000 | t/h
59 | Efficiency Variable | SH Spray Water Flow | KALTIM2.SIGNAL.AI.20LAE21CF101 |  | 20LAE21CF101 | Side-A primary desuperheater water flow | AI | 0 | 100 | t/h
60 | Efficiency Variable | SH Spray Water Flow | KALTIM2.SIGNAL.AI.20LAE22CF101 |  | 20LAE22CF101 | Side-B primary desuperheater water flow | AI | 0 | 100 | t/h
61 | Efficiency Variable | SH Spray Water Flow | KALTIM2.SIGNAL.AI.20LAE23CF101 |  | 20LAE23CF101 | Side-A secondary desuperheater water flow | AI | 0 | 100 | t/h
62 | Efficiency Variable | SH Spray Water Flow | KALTIM2.SIGNAL.AI.20LAE24CF101 |  | 20LAE24CF101 | Side-B secondary desuperheater water flow | AI | 0 | 999999 | t/h
63 | Control Variable | FD Fan Air Flow | KALTIM2.SIGNAL.AO.20HLB30AA101XQ11 |  | 20HLB30AA101XQ11 | A secondary air fan inlet control valve control command | AO | 0 | 100 | %
64 | Control Variable | FD Fan Air Flow | KALTIM2.SIGNAL.AO.20HLB40AA101XQ11 |  | 20HLB40AA101XQ11 | B secondary air fan inlet control valve control command | AO | 0 | 100 | %

## IM_TAGS_UJKTT (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS | f_ah_check | f_interlock
46251 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLB10AA101XQ12 |  | 10HLB10AA101XQ12 | A primary air fan inlet control valve position feedback | AI | 0 | 100 | %
46252 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AO.10HLB10AA101XQ11 |  | 10HLB10AA101XQ11 | A primary air fan inlet control valve control command | AO | 0 | 100 | %
46253 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLB10AN001XQ01 |  | 10HLB10AN001XQ01 | A primary air fan current | AI | 0 | 200 | A
46254 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLA10CT101 |  | 10HLA10CT101 | A primary air fan outlet temperature | RTD | 0 | 100 | ℃
46255 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT101 |  | 10HLB10CT101 | A primary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46256 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT102 |  | 10HLB10CT102 | A primary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46257 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT103 |  | 10HLB10CT103 | A primary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 85 |  |  |  |  | 1 | 1
46258 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT104 |  | 10HLB10CT104 | A primary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 85 |  |  |  |  | 1 | 1
46259 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT105 |  | 10HLB10CT105 | A primary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46260 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT106 |  | 10HLB10CT106 | A primary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46261 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT107 |  | 10HLB10CT107 | A primary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46262 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT108 |  | 10HLB10CT108 | A primary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46263 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT109 |  | 10HLB10CT109 | A primary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46264 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB10CT110 |  | 10HLB10CT110 | A primary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46265 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLA10CP101 |  | 10HLA10CP101 | A primary air fan outlet pressure | AI | 0 | 25 | kPa
46266 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLA10CP102 |  | 10HLA10CP102 | Air preheater primary air inlet pressure | AI | 0 | 25 | kPa
46267 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLB10CY101 |  | 10HLB10CY101 | A primary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46268 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLB10CY102 |  | 10HLB10CY102 | A primary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48901 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 1 | #1 PA FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HLA10CP102 |  | 10HLA10CP102 | Air preheater primary air inlet pressure | AI | 0 | 25 | kPa
46269 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HLB20AA101XQ12 |  | 10HLB20AA101XQ12 | B primary air fan inlet control valve position feedback | AI | 0 | 100 | %
46270 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AO.10HLB20AA101XQ11 |  | 10HLB20AA101XQ11 | B primary air fan inlet control valve control command | AO | 0 | 100 | %
46271 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HLB20AN001XQ01 |  | 10HLB20AN001XQ01 | B primary air fan current | AI | 0 | 200 | A
46272 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLA20CT101 |  | 10HLA20CT101 | B primary air fan outlet temperature | RTD | 0 | 100 | ℃
46273 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT101 |  | 10HLB20CT101 | B primary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46274 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT102 |  | 10HLB20CT102 | B primary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46275 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT103 |  | 10HLB20CT103 | B primary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 85 |  |  |  |  | 1 | 1
46276 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT104 |  | 10HLB20CT104 | B primary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 85 |  |  |  |  | 1 | 1
46277 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT105 |  | 10HLB20CT105 | B primary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46278 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT106 |  | 10HLB20CT106 | B primary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46279 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT107 |  | 10HLB20CT107 | B primary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46280 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT108 |  | 10HLB20CT108 | B primary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46281 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT109 |  | 10HLB20CT109 | B primary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46282 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HLB20CT110 |  | 10HLB20CT110 | B primary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46283 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HLA20CP101 |  | 10HLA20CP101 | B primary air fan outlet pressure | AI | 0 | 25 | kPa
46284 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HLB20CY101 |  | 10HLB20CY101 | B primary air fan front bearing vibration | AI | 0 | 22 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46285 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 2 | #1 PA FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HLB20CY102 |  | 10HLB20CY102 | B primary air fan rear bearing vibration | AI | 0 | 22 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46286 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AI.10HLB30AA101XQ12 |  | 10HLB30AA101XQ12 | A secondary air fan inlet control valve position feedback | AI | 0 | 100 | %
46287 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AO.10HLB30AA101XQ11 |  | 10HLB30AA101XQ11 | A secondary air fan inlet control valve control command | AO | 0 | 100 | %
46288 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AI.10HLB30AN001XQ01 |  | 10HLB30AN001XQ01 | A secondary air fan current | AI | 0 | 150 | A
46289 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLA30CT101 |  | 10HLA30CT101 | A secondary air fan outlet temperature | RTD | 0 | 100 | ℃
46290 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT101 |  | 10HLB30CT101 | A secondary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46291 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT102 |  | 10HLB30CT102 | A secondary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46292 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT103 |  | 10HLB30CT103 | A secondary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
46293 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT104 |  | 10HLB30CT104 | A secondary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
46294 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT105 |  | 10HLB30CT105 | A secondary air fan motor stator temperature 1 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46295 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT106 |  | 10HLB30CT106 | A secondary air fan motor stator temperature 2 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46296 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT107 |  | 10HLB30CT107 | A secondary air fan motor stator temperature 3 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46297 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT108 |  | 10HLB30CT108 | A secondary air fan motor stator temperature 4 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46298 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT109 |  | 10HLB30CT109 | A secondary air fan motor stator temperature 5 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46299 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB30CT110 |  | 10HLB30CT110 | A secondary air fan motor stator temperature 6 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46300 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AI.10HLA30CP101 |  | 10HLA30CP101 | A secondary air fan outlet pressure | AI | 0 | 15 | kPa
46301 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AI.10HLB30CY101 |  | 10HLB30CY101 | A secondary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46302 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 3 | #1 SA FAN A | K0102-05 | KALTIM1.SIGNAL.AI.10HLB30CY102 |  | 10HLB30CY102 | A secondary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46303 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AI.10HLB40AA101XQ12 |  | 10HLB40AA101XQ12 | B secondary air fan inlet control valve position feedback | AI | 0 | 100 | %
46304 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AO.10HLB40AA101XQ11 |  | 10HLB40AA101XQ11 | B secondary air fan inlet control valve control command | AO | 0 | 100 | %
46305 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AI.10HLB40AN001XQ01 |  | 10HLB40AN001XQ01 | B secondary air fan current | AI | 0 | 150 | A
46306 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLA40CT101 |  | 10HLA40CT101 | B secondary air fan outlet temperature | RTD | 0 | 100 | ℃
46307 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT101 |  | 10HLB40CT101 | B secondary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46308 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT102 |  | 10HLB40CT102 | B secondary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46309 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT103 |  | 10HLB40CT103 | B secondary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
46310 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT104 |  | 10HLB40CT104 | B secondary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
46311 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT105 |  | 10HLB40CT105 | B secondary air fan motor stator temperature 1 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46312 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT106 |  | 10HLB40CT106 | B secondary air fan motor stator temperature 2 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46313 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT107 |  | 10HLB40CT107 | B secondary air fan motor stator temperature 3 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46314 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT108 |  | 10HLB40CT108 | B secondary air fan motor stator temperature 4 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46315 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT109 |  | 10HLB40CT109 | B secondary air fan motor stator temperature 5 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46316 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.RTD.10HLB40CT110 |  | 10HLB40CT110 | B secondary air fan motor stator temperature 6 | RTD | 0 | 150 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
46317 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AI.10HLA40CP101 |  | 10HLA40CP101 | B secondary air fan outlet pressure | AI | 0 | 15 | kPa
46318 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AI.10HLB40CY101 |  | 10HLB40CY101 | B secondary air fan front bearing vibration | AI | 0 | 22 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46319 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 4 | #1 SA FAN B | K0102-05 | KALTIM1.SIGNAL.AI.10HLB40CY102 |  | 10HLB40CY102 | B secondary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46320 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CQ101 |  | 10HBK31CQ101 | Side-A air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
46321 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-06 | KALTIM1.SIGNAL.AI.10HDF49AA101XQ12 |  | 10HDF49AA101XQ12 | Control valve for fluidizing air to air preheater outlet positio | AI | 0 | 100 | %
46322 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CQ101 |  | 10HBK41CQ101 | Side-B air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
46323 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-09 | KALTIM1.SIGNAL.AI.10HNA10AA102XQ12 |  | 10HNA10AA102XQ12 | Motor-driven control damper for side-A boiler outlet flue gas to | AI | 0 | 100 | %
46324 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-09 | KALTIM1.SIGNAL.AI.10HNA20AA102XQ12 |  | 10HNA20AA102XQ12 | Motor-driven control damper for side-B boiler outlet flue gas to | AI | 0 | 100 | %
46325 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-06 | KALTIM1.SIGNAL.AO.10HDF49AA101XQ11 |  | 10HDF49AA101XQ11 | Control valve for fluidizing air to air preheater outlet control | AO | 0 | 100 | %
46326 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-09 | KALTIM1.SIGNAL.AO.10HNA10AA102XQ11 |  | 10HNA10AA102XQ11 | Motor-driven control damper for side-A boiler outlet flue gas to | AO | 0 | 100 | %
46327 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-09 | KALTIM1.SIGNAL.AO.10HNA20AA102XQ11 |  | 10HNA20AA102XQ11 | Motor-driven control damper for side-B boiler outlet flue gas to | AO | 0 | 100 | %
46328 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-04 | KALTIM1.SIGNAL.RTD.10HHL01CT101 |  | 10HHL01CT101 | Air preheater primary air outlet temperature | RTD | 0 | 300 | ℃
46329 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-05 | KALTIM1.SIGNAL.RTD.10HHL10CT101 |  | 10HHL10CT101 | Side-A hot secondary air temperature | RTD | 0 | 300 | ℃
46330 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT105 |  | 10HBK31CT105 | Side-A air preheater outlet flue gas temperautre 1 | TC | 0 | 800 | ℃
46331 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT106 |  | 10HBK31CT106 | Side-A air preheater outlet flue gas temperautre 2 | TC | 0 | 800 | ℃
46332 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT105 |  | 10HBK41CT105 | Side-B air preheater outlet flue gas temperautre 1 | TC | 0 | 200 | ℃
46333 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT106 |  | 10HBK41CT106 | Side-B air preheater outlet flue gas temperautre 2 | TC | 0 | 800 | ℃
46334 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP106 |  | 10HBK31CP106 | Differential pressure between side-A air preheater outlet and ec | AI | 0 | 10 | kPa
46335 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP105 |  | 10HBK31CP105 | Side-A air preheater outlet flue gas pressure | AI | -9 | 0 | kPa
46336 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP105 |  | 10HBK41CP105 | Side-B air preheater outlet flue gas pressure | AI | -9 | 0 | kPa
46337 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP106 |  | 10HBK41CP106 | Differential pressure between side-B air preheater outlet and ec | AI | 0 | 10 | kPa
46338 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-04 | KALTIM1.SIGNAL.AI.10HHL01CP101 |  | 10HHL01CP101 | Air preheater primary air outlet pressure | AI | 0 | 25 | kPa
46339 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-04 | KALTIM1.SIGNAL.AI.10HHL01CP102 |  | 10HHL01CP102 | Air preheater primary air differencial pressure | AI | 0 | 6 | kPa
46340 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-05 | KALTIM1.SIGNAL.AI.10HHL10CP101 |  | 10HHL10CP101 | Side-A hot secondary air pressure | AI | 0 | 15 | kPa
46341 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 5 | #1 AIR HEATER | K0102-05 | KALTIM1.SIGNAL.AI.10HLA30CP102 |  | 10HLA30CP102 | Air preheater secondary air differencial pressure | AI | 0 | 15 | kPa
46342 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF10AN001XQ01 |  | 10HDF10AN001XQ01 | A HP fluidizing air fan current | AI | 0 | 50 | A
46343 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT101 |  | 10HDF10CT101 | A HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46344 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT103 |  | 10HDF10CT103 | A HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46345 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT104 |  | 10HDF10CT104 | A HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46346 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT105 |  | 10HDF10CT105 | A HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46347 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT106 |  | 10HDF10CT106 | A HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46348 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT107 |  | 10HDF10CT107 | A HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46349 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT108 |  | 10HDF10CT108 | A HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46350 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT109 |  | 10HDF10CT109 | A HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46351 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT110 |  | 10HDF10CT110 | A HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46352 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF10CT111 |  | 10HDF10CT111 | A HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
46353 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF40CT101 |  | 10HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
46354 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF10CP101 |  | 10HDF10CP101 | A HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
46355 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF40CP101 |  | 10HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa |  |  | 35 | [6 empty] | 2 | 1
48903 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF40CP101 |  | 10HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa |  |  | 35 | [6 empty] | 2
48904 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF40CT101 |  | 10HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
48905 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF40CP101 |  | 10HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa |  |  | 35 | [6 empty] | 2
48906 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 6 | #1 HPFB A | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF40CT101 |  | 10HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
46356 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF20AN001XQ01 |  | 10HDF20AN001XQ01 | B HP fluidizing air fan current | AI | 0 | 50 | A
46357 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT101 |  | 10HDF20CT101 | B HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46358 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT103 |  | 10HDF20CT103 | B HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46359 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT104 |  | 10HDF20CT104 | B HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46360 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT105 |  | 10HDF20CT105 | B HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46361 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT106 |  | 10HDF20CT106 | B HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46362 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT107 |  | 10HDF20CT107 | B HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46363 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT108 |  | 10HDF20CT108 | B HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46364 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT109 |  | 10HDF20CT109 | B HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46365 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT110 |  | 10HDF20CT110 | B HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46366 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF20CT111 |  | 10HDF20CT111 | B HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
46367 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 7 | #1 HPFB B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF20CP101 |  | 10HDF20CP101 | B HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
46368 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.AI.10HDF30AN001XQ01 |  | 10HDF30AN001XQ01 | C HP fluidizing air fan current | AI | 0 | 50 | A
46369 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT101 |  | 10HDF30CT101 | C HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46370 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT103 |  | 10HDF30CT103 | C HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
46371 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT104 |  | 10HDF30CT104 | C HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46372 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT105 |  | 10HDF30CT105 | C HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46373 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT106 |  | 10HDF30CT106 | C HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46374 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT107 |  | 10HDF30CT107 | C HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46375 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT108 |  | 10HDF30CT108 | C HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46376 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT109 |  | 10HDF30CT109 | C HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46377 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT110 |  | 10HDF30CT110 | C HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46378 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.RTD.10HDF30CT111 |  | 10HDF30CT111 | C HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
46379 | 1 | UJKTT #1 | 1 | #1 AIR SYSTEM | 8 | #1 HPFB C | K0102-06 | KALTIM1.SIGNAL.AI.10HDF30CP101 |  | 10HDF30CP101 | C HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
46380 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJA11CB101 |  | 10HJA11CB101 | A upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46381 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJA11CB103 |  | 10HJA11CB103 | A upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46382 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10AA101XQ12 |  | 10HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
46383 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10AA101XQ12 |  | 10HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
46384 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJA11CB102 |  | 10HJA11CB102 | A upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46385 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJF10AA101XQ11 |  | 10HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
46386 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJS10AA101XQ11 |  | 10HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
46387 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.TC.10HJS01CT101 |  | 10HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃ |  |  | 140 | [6 empty] | 2
46388 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.TC.10HJS10CT101 |  | 10HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
46389 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP101 |  | 10HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa |  |  |  | 50 | [5 empty] | 1
46390 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10CP101 |  | 10HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
46391 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP102 |  | 10HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
46392 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJL10CP101 |  | 10HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
46393 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.AI.10HJS01CP101 |  | 10HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa |  |  | 0.4 | [6 empty] | 2
48911 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJF10AA101XQ11 |  | 10HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48912 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10AA101XQ12 |  | 10HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48913 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP101 |  | 10HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48914 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP102 |  | 10HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48915 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJL10CP101 |  | 10HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48916 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.AI.10HJS01CP101 |  | 10HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa |  |  | 0.4 | [6 empty] | 2
48917 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.TC.10HJS01CT101 |  | 10HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
48918 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJS10AA101XQ11 |  | 10HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48919 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10AA101XQ12 |  | 10HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48920 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10CP101 |  | 10HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48921 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.TC.10HJS10CT101 |  | 10HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
48922 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJF10AA101XQ11 |  | 10HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48923 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10AA101XQ12 |  | 10HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48924 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP101 |  | 10HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48925 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP102 |  | 10HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48926 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJL10CP101 |  | 10HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48927 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.AI.10HJS01CP101 |  | 10HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa
48928 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.TC.10HJS01CT101 |  | 10HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
48929 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJS10AA101XQ11 |  | 10HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48930 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10AA101XQ12 |  | 10HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48931 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10CP101 |  | 10HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48932 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.TC.10HJS10CT101 |  | 10HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
48933 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJF10AA101XQ11 |  | 10HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48934 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10AA101XQ12 |  | 10HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48935 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP101 |  | 10HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa |  |  |  | 50 | [5 empty] | 1
48936 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJF10CP102 |  | 10HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48937 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJL10CP101 |  | 10HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48938 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.AI.10HJS01CP101 |  | 10HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa |  |  | 0.4 | [6 empty] | 2
48939 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-11 | KALTIM1.SIGNAL.TC.10HJS01CT101 |  | 10HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
48940 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AO.10HJS10AA101XQ11 |  | 10HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48941 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10AA101XQ12 |  | 10HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48942 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.AI.10HJS10CP101 |  | 10HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48943 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 1 | #1 BURNER A | K0102-12 | KALTIM1.SIGNAL.TC.10HJS10CT101 |  | 10HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
46394 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM1.SIGNAL.AI.10HJA12CB101 |  | 10HJA12CB101 | B upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46395 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM1.SIGNAL.AI.10HJA12CB102 |  | 10HJA12CB102 | B upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46396 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM1.SIGNAL.AI.10HJA12CB103 |  | 10HJA12CB103 | B upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
47586 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM2.SIGNAL.AI.20HLA10CP102 |  | 20HLA10CP102 | Air preheater primary air inlet pressure | AI | 0 | 25 | kPa
47673 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM2.SIGNAL.RTD.20HDF40CT101 |  | 20HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
47675 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-11 | KALTIM2.SIGNAL.AI.20HDF40CP101 |  | 20HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa |  |  | 35 | [6 empty] | 2 | 1
48902 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM2.SIGNAL.AI.20HLA10CP102 |  | 20HLA10CP102 | Air preheater primary air inlet pressure | AI | 0 | 25 | kPa
48907 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-11 | KALTIM2.SIGNAL.AI.20HDF40CP101 |  | 20HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa
48908 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM2.SIGNAL.RTD.20HDF40CT101 |  | 20HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
48909 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-11 | KALTIM2.SIGNAL.AI.20HDF40CP101 |  | 20HDF40CP101 | HP fluidizing air fan outlet header pressure | AI | 0 | 100 | kPa
48910 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 2 | #1 BURNER B | K0102-12 | KALTIM2.SIGNAL.RTD.20HDF40CT101 |  | 20HDF40CT101 | HP fluidizing air fan outlet header temperature | RTD | 0 | 100 | ℃
46397 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 3 | #1 BURNER C | K0102-12 | KALTIM1.SIGNAL.AI.10HJA13CB102 |  | 10HJA13CB102 | C upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46398 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 3 | #1 BURNER C | K0102-12 | KALTIM1.SIGNAL.AI.10HJA13CB103 |  | 10HJA13CB103 | C upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46399 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 3 | #1 BURNER C | K0102-12 | KALTIM1.SIGNAL.AI.10HJA13CB101 |  | 10HJA13CB101 | C upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46400 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 4 | #1 BURNER D | K0102-12 | KALTIM1.SIGNAL.AI.10HJA14CB101 |  | 10HJA14CB101 | D upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46401 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 4 | #1 BURNER D | K0102-12 | KALTIM1.SIGNAL.AI.10HJA14CB102 |  | 10HJA14CB102 | D upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46402 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 4 | #1 BURNER D | K0102-12 | KALTIM1.SIGNAL.AI.10HJA14CB103 |  | 10HJA14CB103 | D upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46403 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT101 |  | 10HAH11CT101 | Steam temperature of connection pipe 1 between Side-A seperator | TC | 0 | 400 | °C
46404 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT102 |  | 10HAH11CT102 | Steam temperature of connection pipe 2 between Side-A seperator | TC | 0 | 400 | °C
46405 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT103 |  | 10HAH11CT103 | Steam temperature of connection pipe 3 between Side-A seperator | TC | 0 | 400 | °C
46406 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT104 |  | 10HAH11CT104 | Steam temperature of connection pipe 4 between Side-A seperator | TC | 0 | 400 | °C
46407 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT105 |  | 10HAH11CT105 | Steam temperature of connection pipe 5 between Side-A seperator | TC | 0 | 400 | °C
46408 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH11CT106 |  | 10HAH11CT106 | Steam temperature of connection pipe 6 between Side-A seperator | TC | 0 | 400 | °C
46409 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT101 |  | 10HAH12CT101 | Steam temperature of connection pipe 1 between Side-B seperator | TC | 0 | 400 | °C
46410 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT102 |  | 10HAH12CT102 | Steam temperature of connection pipe 2 between Side-B seperator | TC | 0 | 400 | °C
46411 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT103 |  | 10HAH12CT103 | Steam temperature of connection pipe 3 between Side-B seperator | TC | 0 | 400 | °C
46412 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT104 |  | 10HAH12CT104 | Steam temperature of connection pipe 4 between Side-B seperator | TC | 0 | 400 | °C
46413 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT105 |  | 10HAH12CT105 | Steam temperature of connection pipe 5 between Side-B seperator | TC | 0 | 400 | °C
46414 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 5 | #1 WATERWALL | K0102-03 | KALTIM1.SIGNAL.TC.10HAH12CT106 |  | 10HAH12CT106 | Steam temperature of connection pipe 6 between Side-B seperator | TC | 0 | 400 | °C
46415 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH |  | KALTIM1.SIGNAL.AI.10LAE10AA101XQ12 |  | 10LAE10AA101XQ12 | Main steam to aux steam desuperheatin water valve feedback | AI | 0 | 100 | %
46416 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE21AA101XQ12 |  | 10LAE21AA101XQ12 | Side-A primary desuperheater water control valve position feedba | AI | 0 | 100 | %
46417 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE22AA101XQ12 |  | 10LAE22AA101XQ12 | Side-B primary desuperheater water control valve position feedba | AI | 0 | 100 | %
46418 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH |  | KALTIM1.SIGNAL.AO.10LAE10AA101XQ11 |  | 10LAE10AA101XQ11 | Main steam to aux steam desuperheatin water valve cmd | AO | 0 | 100 | %
46419 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AO.10LAE21AA101XQ11 |  | 10LAE21AA101XQ11 | Side-A primary desuperheater water control valve control command | AO | 0 | 100 | %
46420 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AO.10LAE22AA101XQ11 |  | 10LAE22AA101XQ11 | Side-B primary desuperheater water control valve control command | AO | 0 | 100 | %
46421 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT101 |  | 10HAH20CT101 | LT superheater outlet pipe wall temperature 1 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46422 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT102 |  | 10HAH20CT102 | LT superheater outlet pipe wall temperature 2 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46423 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT103 |  | 10HAH20CT103 | LT superheater outlet pipe wall temperature 3 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46424 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT104 |  | 10HAH20CT104 | LT superheater outlet pipe wall temperature 4 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46425 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT105 |  | 10HAH20CT105 | LT superheater outlet pipe wall temperature 5 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46426 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH20CT106 |  | 10HAH20CT106 | LT superheater outlet pipe wall temperature 6 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
46427 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.RTD.10LAE20CT101 |  | 10LAE20CT101 | Desuperheater water filter outlet temperature | RTD | 0 | 200 | ℃
46428 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH21CT101 |  | 10HAH21CT101 | Temperature of steam before Side-A primary desuperheater | TC | 0 | 500 | ℃
46429 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH21CT102 |  | 10HAH21CT102 | Temperature 1 of steam after Side-A primary desuperheater | TC | 0 | 500 | ℃
46430 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH21CT103 |  | 10HAH21CT103 | Temperature 2 of steam after Side-A primary desuperheater | TC | 0 | 500 | ℃
46431 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH22CT101 |  | 10HAH22CT101 | Temperature of steam before Side-B primary desuperheater | TC | 0 | 500 | ℃
46432 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH22CT102 |  | 10HAH22CT102 | Temperature 1 of steam after Side-B primary desuperheater | TC | 0 | 500 | ℃
46433 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH22CT103 |  | 10HAH22CT103 | Temperature 2 of steam after Side-B primary desuperheater | TC | 0 | 500 | ℃
46434 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT102 |  | 10HBK31CT102 | Side-A low temperature super heater inlet flue gas temperature | TC | 0 | 800 | ℃
46435 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT103 |  | 10HBK31CT103 | Side-A low temperature super heater outlet flue gas temperature | TC | 0 | 800 | ℃
46436 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT102 |  | 10HBK41CT102 | Side-B low temperature super heater inlet flue gas temperature | TC | 0 | 940 | ℃
46437 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT103 |  | 10HBK41CT103 | Side-B low temperature super heater outlet flue gas temperature | TC | 0 | 700 | ℃
46438 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP102 |  | 10HBK31CP102 | Side-A low temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
46439 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP103 |  | 10HBK31CP103 | Side-A low temperature super heater outlet flue gas pressure | AI | -8 | 1 | kPa
46440 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP102 |  | 10HBK41CP102 | Side-B low temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
46441 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP103 |  | 10HBK41CP103 | Side-B low temperature super heater outlet flue gas pressure | AI | -8 | 1 | kPa
46442 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE20CP101 |  | 10LAE20CP101 | Desuperheater water filter outlet pressure | AI | 0 | 15 | MPa
46443 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE21CF101 |  | 10LAE21CF101 | Side-A primary desuperheater water flow | AI | 0 | 100 | t/h
46444 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE22CF101 |  | 10LAE22CF101 | Side-B primary desuperheater water flow | AI | 0 | 100 | t/h
46445 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH |  | KALTIM 0.SIGNAL.AI.10GUA10CQ101 |  | 10GUA10CQ101 | Unit 1 Left/right side of Saturated steam CC | AI | 0 | 20
46446 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH |  | KALTIM 0.SIGNAL.AI.10GUA20CQ103 |  | 10GUA20CQ103 | Unit 1 Left/right side of Saturated steam SiO2 | AI | 0 | 100
48889 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 6 | #1 LTSH |  | 10LAE21CF901 |  | 10LAE21CF901 | Superheater Spray Water Flow | CALC | 0 | 100 | t/h | [8 empty] | (KALTIM1.SIGNAL.AI.10LAE21CF101)+(KALTIM1.SIGNAL.AI.10LAE22CF101)+(KALTIM1.SIGNAL.AI.10LAE23CF101)+(KALTIM1.SIGNAL.AI.10LAE24CF101)
48898 | 1 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH |  | 20LAE21CF901 |  | 20LAE21CF901 | Superheater Spray Water Flow | CALC | 0 | 100 | t/h | [8 empty] | (KALTIM2.SIGNAL.AI.20LAE21CF101)+(KALTIM2.SIGNAL.AI.20LAE22CF101)+(KALTIM2.SIGNAL.AI.20LAE23CF101)+(KALTIM2.SIGNAL.AI.20LAE24CF101)
46447 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE23AA101XQ12 |  | 10LAE23AA101XQ12 | Side-A secondary desuperheater water control valve position feed | AI | 0 | 100 | %
46448 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE24AA101XQ12 |  | 10LAE24AA101XQ12 | Side-B secondary desuperheater water control valve position feed | AI | 0 | 100 | %
46449 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AO.10LAE23AA101XQ11 |  | 10LAE23AA101XQ11 | Side-A secondary desuperheater water control valve control comma | AO | 0 | 100 | %
46450 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AO.10LAE24AA101XQ11 |  | 10LAE24AA101XQ11 | Side-B secondary desuperheater water control valve control | AO | 0 | 100 | %
46451 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT101 |  | 10HAH31CT101 | Side-A platen superheater outlet #1 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46452 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT102 |  | 10HAH31CT102 | Side-A platen superheater outlet #1 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46453 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT103 |  | 10HAH31CT103 | Side-A platen superheater outlet #1 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46454 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT104 |  | 10HAH31CT104 | Side-A platen superheater outlet #1 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46455 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT105 |  | 10HAH31CT105 | Side-A platen superheater outlet #2 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46456 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT106 |  | 10HAH31CT106 | Side-A platen superheater outlet #2 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46457 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT107 |  | 10HAH31CT107 | Side-A platen superheater outlet #2 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46458 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT108 |  | 10HAH31CT108 | Side-A platen superheater outlet #2 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46459 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT109 |  | 10HAH31CT109 | Side-A platen superheater outlet #3 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46460 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT110 |  | 10HAH31CT110 | Side-A platen superheater outlet #3 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46461 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT111 |  | 10HAH31CT111 | Side-A platen superheater outlet #3 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46462 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH31CT112 |  | 10HAH31CT112 | Side-A platen superheater outlet #3 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46463 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT101 |  | 10HAH32CT101 | Side-B platen superheater outlet #1 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46464 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT102 |  | 10HAH32CT102 | Side-B platen superheater outlet #1 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46465 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT103 |  | 10HAH32CT103 | Side-B platen superheater outlet #1 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46466 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT104 |  | 10HAH32CT104 | Side-B platen superheater outlet #1 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46467 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT105 |  | 10HAH32CT105 | Side-B platen superheater outlet #2 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46468 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT106 |  | 10HAH32CT106 | Side-B platen superheater outlet #2 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46469 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT107 |  | 10HAH32CT107 | Side-B platen superheater outlet #2 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46470 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT108 |  | 10HAH32CT108 | Side-B platen superheater outlet #2 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46471 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT109 |  | 10HAH32CT109 | Side-B platen superheater outlet #3 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46472 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT110 |  | 10HAH32CT110 | Side-B platen superheater outlet #3 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46473 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT111 |  | 10HAH32CT111 | Side-B platen superheater outlet #3 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46474 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH32CT112 |  | 10HAH32CT112 | Side-B platen superheater outlet #3 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46475 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH41CT101 |  | 10HAH41CT101 | Temperature of steam before Side-A secondary desuperheater | TC | 0 | 500 | ℃
46476 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH41CT102 |  | 10HAH41CT102 | Temperature 1 of steam after Side-A secondary desuperheater | TC | 0 | 500 | ℃
46477 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH41CT103 |  | 10HAH41CT103 | Temperature 2 of steam after Side-A secondary desuperheater | TC | 0 | 500 | ℃
46478 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH42CT101 |  | 10HAH42CT101 | Temperature of steam before Side-B secondary desuperheater | TC | 0 | 500 | ℃
46479 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH42CT102 |  | 10HAH42CT102 | Temperature 1 of steam after Side-B secondary desuperheater | TC | 0 | 500 | ℃
46480 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH42CT103 |  | 10HAH42CT103 | Temperature 2 of steam after Side-B secondary desuperheater | TC | 0 | 500 | ℃
46481 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE23CF101 |  | 10LAE23CF101 | Side-A secondary desuperheater water flow | AI | 0 | 100 | t/h
46482 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 7 | #1 PLATEN SH | K0102-03 | KALTIM1.SIGNAL.AI.10LAE24CF101 |  | 10LAE24CF101 | Side-B secondary desuperheater water flow | AI | 0 | 999999 | t/h
46483 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT101 |  | 10HAH50CT101 | HT superheater outlet pipe wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46484 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT102 |  | 10HAH50CT102 | HT superheater outlet pipe wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46485 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT103 |  | 10HAH50CT103 | HT superheater outlet pipe wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46486 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT104 |  | 10HAH50CT104 | HT superheater outlet pipe wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46487 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT105 |  | 10HAH50CT105 | HT superheater outlet pipe wall temperature 5 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46488 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT106 |  | 10HAH50CT106 | HT superheater outlet pipe wall temperature 6 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46489 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT107 |  | 10HAH50CT107 | HT superheater outlet pipe wall temperature 7 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46490 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT108 |  | 10HAH50CT108 | HT superheater outlet pipe wall temperature 8 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46491 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH50CT109 |  | 10HAH50CT109 | HT superheater outlet pipe wall temperature 9 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
46492 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-17 | KALTIM1.SIGNAL.TC.10LBA10CT103 |  | 10LBA10CT103 | MAIN STEAM TEMP | TC | 0 | 800 | °C
46493 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10HAH60CT102 |  | 10HAH60CT102 | Side-B HT superheater outlet header temperature | TC | 0 | 600 | ℃
46494 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT101 |  | 10HBK31CT101 | Side-A high temperature super heater inlet flue gas temperature | TC | 0 | 1200 | ℃
46495 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT101 |  | 10HBK41CT101 | Side-B high temperature super heater inlet flue gas temperature | TC | 0 | 1200 | ℃
46496 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA01CT101 |  | 10LBA01CT101 | Side-A HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46497 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA01CT102 |  | 10LBA01CT102 | Side-A HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46498 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA01CT103 |  | 10LBA01CT103 | Side-A HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46499 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA02CT101 |  | 10LBA02CT101 | Side-B HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46500 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA02CT102 |  | 10LBA02CT102 | Side-B HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46501 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.TC.10LBA02CT103 |  | 10LBA02CT103 | Side-B HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
46502 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP101 |  | 10HBK31CP101 | Side-A high temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
46503 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP101 |  | 10HBK41CP101 | Side-B high temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
46504 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LBA01CP101 |  | 10LBA01CP101 | Side-A HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10 | [5 empty] | 1
46505 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-03 | KALTIM1.SIGNAL.AI.10LBA02CP101 |  | 10LBA02CP101 | Side-B HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10 | [5 empty] | 1
46506 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-17 | KALTIM1.SIGNAL.AI.10LBA10CP103 |  | 10LBA10CP103 | P OF MAIN STM MAIN PIP | AI | 0 | 16 | MPa
46507 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH | K0102-17 | KALTIM1.SIGNAL.AI.AM11CCS20A01 |  | 10LBA10CF101 | Main steam flow | AI | 0 | 500 | t/h
46508 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH |  | KALTIM 0.SIGNAL.AI.10GUA20CQ101 |  | 10GUA20CQ101 | Unit 1 Left/right side of Superheated steam SiO2 | AI | 0 | 20
46509 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 8 | #1 HTSH |  | KALTIM 0.SIGNAL.AI.10GUA20CQ102 |  | 10GUA20CQ102 | Unit 1 Left/right side of Superheated steam SiO2 | AI | 0 | 100
46510 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK31CT104 |  | 10HBK31CT104 | Side-A economiser outlet flue gas temperature | TC | 0 | 800 | ℃
46511 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-08 | KALTIM1.SIGNAL.TC.10HBK41CT104 |  | 10HBK41CT104 | Side-B economiser outlet flue gas temperature | TC | 0 | 370 | ℃
46512 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-02 | KALTIM1.SIGNAL.TC.10LAB50CT103 |  | 10LAB50CT103 | Economizer inlet water temperature | TC | 0 | 400 | ℃
46513 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-02 | KALTIM1.SIGNAL.TC.10LAB50CT104 |  | 10LAB50CT104 | Temperature of water from economizer to drum | TC | 0 | 400 | ℃
46514 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-23 | KALTIM1.SIGNAL.TC.10LBG21CT101 |  | 10LBG21CT101 | TEMP OF THE STM FROM AUX STM TO ECONOMIZER START-UP BLOW | TC | 0 | 800 | ℃
46515 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK31CP104 |  | 10HBK31CP104 | Side-A economiser outlet flue gas pressure | AI | -8 | 0.5 | kPa
46516 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-08 | KALTIM1.SIGNAL.AI.10HBK41CP104 |  | 10HBK41CP104 | Side-B economiser outlet flue gas pressure | AI | -8 | 0.5 | kPa
46517 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-02 | KALTIM1.SIGNAL.AI.10LAB50CP102 |  | 10LAB50CP102 | Economizer inlet water pressure | AI | 0 | 15 | MPa
46518 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER | K0102-23 | KALTIM1.SIGNAL.AI.10LBG21CP101 |  | 10LBG21CP101 | P OF THE STM FROM AUX STM TO ECONOMIZER START-UP BLOW | AI | 0 | 1.6 | MPa
46519 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.10GUB30CQ101 |  | 10GUB30CQ101 | Unit 1 Economizer import N2H4 | AI | 0 | 100
46520 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.10GUB30CQ102 |  | 10GUB30CQ102 | Unit 1 Economizer import PH | AI | 0 | 14
46521 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 9 | #1 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.10GUB30CQ103 |  | 10GUB30CQ103 | Unit 1 Economizer import CC | AI | 0 | 20
46522 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AI.10HAN11AA101XQ12 |  | 10HAN11AA101XQ12 | Side-B drum continuous blowdown control valve position feedback | AI | 0 | 100 | %
46523 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AI.10HAN13AA101XQ12 |  | 10HAN13AA101XQ12 | Side-A drum continuous blowdown control valve position feedback | AI | 0 | 100 | %
46524 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AI.10LCQ20AA101XQ12 |  | 10LCQ20AA101XQ12 | Control valve for continuous blowdown flash tank to periodic blo | AI | 0 | 100 | %
46525 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AO.10HAN11AA101XQ11 |  | 10HAN11AA101XQ11 | Side-B drum continuous blowdown control valve control command | AO | 0 | 100 | %
46526 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AO.10HAN13AA101XQ11 |  | 10HAN13AA101XQ11 | Side-A drum continuous blowdown control valve control command | AO | 0 | 100 | %
46527 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AO.10LCQ20AA101XQ11 |  | 10LCQ20AA101XQ11 | Control valve for continuous blowdown flash tank to periodic blo | AO | 0 | 100 | %
46528 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT101 |  | 10HAD01CT101 | Drum wall temperature 1 | TC | 0 | 350 | °C
46529 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT102 |  | 10HAD01CT102 | Drum wall temperature 2 | TC | 0 | 350 | °C
46530 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT103 |  | 10HAD01CT103 | Drum wall temperature 3 | TC | 0 | 350 | °C
46531 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT104 |  | 10HAD01CT104 | Drum wall temperature 4 | TC | 0 | 350 | °C
46532 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT105 |  | 10HAD01CT105 | Drum wall temperature 5 | TC | 0 | 350 | °C
46533 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT106 |  | 10HAD01CT106 | Drum wall temperature 6 | TC | 0 | 350 | °C
46534 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT107 |  | 10HAD01CT107 | Drum wall temperature 7 | TC | 0 | 350 | °C
46535 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT108 |  | 10HAD01CT108 | Drum wall temperature 8 | TC | 0 | 350 | °C
46536 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT109 |  | 10HAD01CT109 | Drum wall temperature 9 | TC | 0 | 350 | °C
46537 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT110 |  | 10HAD01CT110 | Drum wall temperature 10 | TC | 0 | 350 | °C
46538 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT111 |  | 10HAD01CT111 | Drum wall temperature 11 | TC | 0 | 350 | °C
46539 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT112 |  | 10HAD01CT112 | Drum wall temperature 12 | TC | 0 | 350 | °C
46540 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT113 |  | 10HAD01CT113 | Wall temperature of guide pipe after balance container 1 | TC | 0 | 350 | ℃
46541 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT114 |  | 10HAD01CT114 | Wall temperature of guide pipe after balance container 2 | TC | 0 | 350 | ℃
46542 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.TC.10HAD01CT115 |  | 10HAD01CT115 | Wall temperature of guide pipe after balance container 3 | TC | 0 | 350 | ℃
46543 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-14 | KALTIM1.SIGNAL.AI.10LCQ20CL102 |  | 10LCQ20CL102 | Continuous blowdown flash tank water level | AI | 0 | 400 | mm
46544 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.AM12MCS02A05 |  | 10HAD01CL101 | Drum water level 1 | AI | -600 | 600 | mm | -280 |  | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
46545 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.AM12MCS02A06 |  | 10HAD01CL102 | Drum water level 2 | AI | -600 | 600 | mm | -280 |  | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
46546 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.AM12MCS02A07 |  | 10HAD01CL103 | Drum water level 3 | AI | -600 | 600 | mm | -280 |  | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
46547 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.10HAD01CP101 |  | 10HAD01CP101 | Drum pressure 1 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
46548 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.10HAD01CP102 |  | 10HAD01CP102 | Drum pressure 2 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
46549 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM | K0102-02 | KALTIM1.SIGNAL.AI.10HAD01CP103 |  | 10HAD01CP103 | Drum pressure 3 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
46550 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.10GUE10CQ101 |  | 10GUE10CQ101 | Unit 1 Left/right side of Drum boiler water PH | AI | 0 | 14
46551 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.10GUE10CQ102 |  | 10GUE10CQ102 | Unit 1 Left/right side of Drum boiler water SC | AI | 0 | 200
46552 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.10GUE10CQ103 |  | 10GUE10CQ103 | Unit 1 Left/right side of Drum boiler water SiO2 | AI | 0 | 1000
48886 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM |  | 10HAD01CP901 |  | 10HAD01CP901 | Steam Drum Pressure Average | CALC | 0 | 16 | MPa | [8 empty] | ((KALTIM1.SIGNAL.AI.10HAD01CP101)+(KALTIM1.SIGNAL.AI.10HAD01CP102)+(KALTIM1.SIGNAL.AI.10HAD01CP103))/3
48887 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 10 | #1 STEAM DRUM |  | 10HAD01CT901 |  | 10HAD01CT901 | Steam Drum Temperature Average | CALC | 0 | 350 | °C | [8 empty] | ((KALTIM1.SIGNAL.TC.10HAD01CT102)+(KALTIM1.SIGNAL.TC.10HAD01CT104)+(KALTIM1.SIGNAL.TC.10HAD01CT108)+(KALTIM1.SIGNAL.TC.10HAD01CT110))/4
48895 | 1 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM |  | 20HAD01CP901 |  | 20HAD01CP901 | Steam Drum Pressure Average | CALC | 0 | 16 | MPa | [8 empty] | ((KALTIM2.SIGNAL.AI.20HAD01CP101)+(KALTIM2.SIGNAL.AI.20HAD01CP102)+(KALTIM2.SIGNAL.AI.20HAD01CP103))/3
48896 | 1 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM |  | 20HAD01CT901 |  | 20HAD01CT901 | Steam Drum Temperature Average | CALC | 0 | 350 | °C | [8 empty] | ((KALTIM2.SIGNAL.TC.20HAD01CT102)+(KALTIM2.SIGNAL.TC.20HAD01CT104)+(KALTIM2.SIGNAL.TC.20HAD01CT108)+(KALTIM2.SIGNAL.TC.20HAD01CT110))/4
46553 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF52AA101XQ12 |  | 10HDF52AA101XQ12 | A return material tank inlet control valve 1 position feedback | AI | 0 | 100 | %
46554 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF53AA101XQ12 |  | 10HDF53AA101XQ12 | A return material tank inlet control valve 2 position feedback | AI | 0 | 100 | %
46555 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AO.10HDF52AA101XQ11 |  | 10HDF52AA101XQ11 | A return material tank inlet control valve 1 control command | AO | 0 | 100 | %
46556 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AO.10HDF53AA101XQ11 |  | 10HDF53AA101XQ11 | A return material tank inlet control valve 2 control command | AO | 0 | 100 | %
46557 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT101 |  | 10HDF52CT101 | A cyclone separator upper wall temperature 1 | TC | 0 | 500 | °C
46558 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT102 |  | 10HDF52CT102 | A cyclone separator upper wall temperature 2 | TC | 0 | 500 | °C
46559 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT103 |  | 10HDF52CT103 | A cyclone separator upper wall temperature 3 | TC | 0 | 500 | °C
46560 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT104 |  | 10HDF52CT104 | A cyclone separator upper wall temperature 4 | TC | 0 | 500 | °C
46561 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT105 |  | 10HDF52CT105 | A cyclone separator upper wall temperature 5 | TC | 0 | 500 | °C
46562 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT106 |  | 10HDF52CT106 | A cyclone separator upper wall temperature 6 | TC | 0 | 500 | °C
46563 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT107 |  | 10HDF52CT107 | A cyclone separator lower wall temperature 1 | TC | 0 | 500 | °C
46564 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT108 |  | 10HDF52CT108 | A cyclone separator lower wall temperature 2 | TC | 0 | 500 | °C
46565 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT109 |  | 10HDF52CT109 | A cyclone separator lower wall temperature 3 | TC | 0 | 500 | °C
46566 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT110 |  | 10HDF52CT110 | A cyclone separator lower wall temperature 4 | TC | 0 | 500 | °C
46567 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT111 |  | 10HDF52CT111 | A cyclone separator lower wall temperature 5 | TC | 0 | 500 | °C
46568 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.TC.10HDF52CT112 |  | 10HDF52CT112 | A cyclone separator lower wall temperature 6 | TC | 0 | 500 | °C
46569 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.TC.10HDF11CT101 |  | 10HDF11CT101 | A cyclone separator inlet fule gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1 | 1
46570 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.TC.10HDF11CT102 |  | 10HDF11CT102 | A cyclone separator outlet fule gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1 | 1
46571 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.TC.10HDF11CT103 |  | 10HDF11CT103 | Side-A U valve outlet ash temperature | TC | 0 | 1200 | ℃
46572 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF111CP103 |  | 10HDF111CP103 | Side-A U valve inlet pressure | AI | -5 | 5 | kPa
46573 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CD101 |  | 10HDF11CD101 | Side-A U valve density | AI | -60 | 60 | kPa
46574 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP101 |  | 10HDF11CP101 | A cyclone separator differential pressure between outlet and inl | AI | -5 | 11 | kPa
46575 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP102 |  | 10HDF11CP102 | A cyclone separator outlet fule gas pressure | AI | -7 | 1 | kPa
46576 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP103 |  | 10HDF11CP103 | Side-A U valve inlet pressure | AI | -5 | 5 | kPa
46577 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP104 |  | 10HDF11CP104 | Side-A U valve outlet pressure (LP) | AI | 0 | 59 | kPa
46578 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP105 |  | 10HDF11CP105 | Side-A U valve sealing height | AI | -50 | 60 | kPa |  |  |  | 60 | [5 empty] | 1
46579 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-08 | KALTIM1.SIGNAL.AI.10HDF11CP106 |  | 10HDF11CP106 | Side-A U valve outlet pressure (HP) | AI | 0 | 70 | kPa
46580 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF52CP101 |  | 10HDF52CP101 | Side-A U valve bed pressure | AI | 0 | 80 | kPa
46581 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF52CP102 |  | 10HDF52CP102 | Side-A U valve chamber air pressure 1 | AI | 0 | 60 | kPa
46582 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 11 | #1 CYCLONE A | K0102-06 | KALTIM1.SIGNAL.AI.10HDF52CP103 |  | 10HDF52CP103 | Side-A U valve chamber air pressure 2 | AI | 0 | 60 | kPa
46583 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF44AA101XQ12 |  | 10HDF44AA101XQ12 | B return material tank inlet control valve 1 position feedback | AI | 0 | 100 | %
46584 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF45AA101XQ12 |  | 10HDF45AA101XQ12 | B return material tank inlet control valve 2 position feedback | AI | 0 | 100 | %
46585 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AO.10HDF44AA101XQ11 |  | 10HDF44AA101XQ11 | B return material tank inlet control valve 1 control command | AO | 0 | 100 | %
46586 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AO.10HDF45AA101XQ11 |  | 10HDF45AA101XQ11 | B return material tank inlet control valve 2 control command | AO | 0 | 100 | %
46587 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT101 |  | 10HDF44CT101 | B cyclone separator upper wall temperature 1 | TC | 0 | 500 | °C
46588 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT102 |  | 10HDF44CT102 | B cyclone separator upper wall temperature 2 | TC | 0 | 500 | °C
46589 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT103 |  | 10HDF44CT103 | B cyclone separator upper wall temperature 3 | TC | 0 | 500 | °C
46590 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT104 |  | 10HDF44CT104 | B cyclone separator upper wall temperature 4 | TC | 0 | 500 | °C
46591 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT105 |  | 10HDF44CT105 | B cyclone separator upper wall temperature 5 | TC | 0 | 500 | °C
46592 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT106 |  | 10HDF44CT106 | B cyclone separator upper wall temperature 6 | TC | 0 | 500 | °C
46593 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT107 |  | 10HDF44CT107 | B cyclone separator lower wall temperature 1 | TC | 0 | 500 | °C
46594 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT108 |  | 10HDF44CT108 | B cyclone separator lower wall temperature 2 | TC | 0 | 500 | °C
46595 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT109 |  | 10HDF44CT109 | B cyclone separator lower wall temperature 3 | TC | 0 | 500 | °C
46596 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT110 |  | 10HDF44CT110 | B cyclone separator lower wall temperature 4 | TC | 0 | 500 | °C
46597 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT111 |  | 10HDF44CT111 | B cyclone separator lower wall temperature 5 | TC | 0 | 500 | °C
46598 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.TC.10HDF44CT112 |  | 10HDF44CT112 | B cyclone separator lower wall temperature 6 | TC | 0 | 500 | °C
46599 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.TC.10HDF21CT101 |  | 10HDF21CT101 | B cyclone separator inlet flue gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1 | 1
46600 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.TC.10HDF21CT102 |  | 10HDF21CT102 | B cyclone separator outlet flue gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1 | 1
46601 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.TC.10HDF21CT103 |  | 10HDF21CT103 | Side-B U valve outlet ash temperature | TC | 0 | 1200 | ℃
46602 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CD101 |  | 10HDF21CD101 | Side-B U valve density | AI | -60 | 60 | kPa
46603 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP101 |  | 10HDF21CP101 | B cyclone separator differential pressure between outlet and inl | AI | -5 | 11 | kPa
46604 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP102 |  | 10HDF21CP102 | B cyclone separator outlet fule gas pressure | AI | -7 | 1 | kPa
46605 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP103 |  | 10HDF21CP103 | Side-B U valve inlet pressure | AI | -5 | 5 | kPa
46606 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP104 |  | 10HDF21CP104 | Side-B U valve outlet pressure (LP) | AI | 0 | 59 | kPa
46607 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP105 |  | 10HDF21CP105 | Side-B U valve sealing height | AI | -50 | 60 | kPa |  |  |  | 60 | [5 empty] | 1
46608 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-08 | KALTIM1.SIGNAL.AI.10HDF21CP106 |  | 10HDF21CP106 | Side-B U valve outlet pressure (HP) | AI | 0 | 70 | kPa
46609 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF44CP101 |  | 10HDF44CP101 | Side-B U valve bed pressure | AI | 0 | 80 | kPa
46610 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF44CP102 |  | 10HDF44CP102 | Side-B U valve chamber air pressure 1 | AI | 0 | 60 | kPa
46611 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF44CP103 |  | 10HDF44CP103 | Side-B U valve chamber air pressure 2 | AI | 0 | 60 | kPa
46612 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF44CF101 |  | 10HDF44CF101 | B return material tank inlet air flow 1 | AI | 0 | 3000 | Nm3/h
46613 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF45CF101 |  | 10HDF45CF101 | B return material tank inlet air flow 2 | AI | 0 | 3000 | Nm3/h
46614 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF46CF101 |  | 10HDF46CF101 | B return material tank inlet air flow 3 | AI | 0 | 1200 | Nm3/h
46615 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF47CF101 |  | 10HDF47CF101 | B return material tank inlet air flow 4 | AI | 0 | 1200 | Nm3/h
46616 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 12 | #1 CYCLONE B | K0102-06 | KALTIM1.SIGNAL.AI.10HDF48CF101 |  | 10HDF48CF101 | B return material tank inlet air flow 5 | AI | 0 | 1200 | Nm3/h
46617 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AI.10HCB10AA101XQ12 |  | 10HCB10AA101XQ12 | POSITION (Pressure Reduction Station) | AI | 0 | 100 | %
46618 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AO.10HCB10AA101XQ11 |  | 10HCB10AA101XQ11 | LOCALIZER (Pressure Reduction Station) | AO | 0 | 100 | %
46619 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AI.10HCB10XQ01 |  | 10HCB10XQ01 | VALVE WORKING CURRENT | AI | 0 | 10 | A
46620 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AI.10HCB11XQ01 |  | 10HCB11XQ01 | KR/ER GROUP WORKING CURRENT | AI | 0 | 10 | A
46621 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AI.10HCB12XQ01 |  | 10HCB12XQ01 | KL/EL GROUP WORKING CURRENT | AI | 0 | 10 | A
46622 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 13 | #1 SOOT BLOWER | K0102-15 | KALTIM1.SIGNAL.AI.10HCB10CP101 |  | 10HCB10CP101 | PRESSURE (Pressure Reduction Station) | AI | 0 | 13.7895 | MPa
46623 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL02AA101XQ12 |  | 10HHL02AA101XQ12 | A air duct ignitor inlet motor-driven control damper 1 position | AI | 0 | 100 | %
46624 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL02AA103XQ12 |  | 10HHL02AA103XQ12 | A air duct ignitor inlet motor-driven control damper 3 position | AI | 0 | 100 | %
46625 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL05AA102XQ12 |  | 10HHL05AA102XQ12 | Front wall upper bed burner hot primary air control damper 2 pos | AI | 0 | 100 | %
46626 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL02AA102XQ12 |  | 10HHL02AA102XQ12 | A air duct ignitor inlet motor-driven control damper 2 position | AI | 0 | 100 | %
46627 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL03AA101XQ12 |  | 10HHL03AA101XQ12 | B air duct ignitor inlet motor-driven control damper 1 position | AI | 0 | 100 | %
46628 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL03AA102XQ12 |  | 10HHL03AA102XQ12 | B air duct ignitor inlet motor-driven control damper 2 position | AI | 0 | 100 | %
46629 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL03AA103XQ12 |  | 10HHL03AA103XQ12 | B air duct ignitor inlet motor-driven control damper 3 position | AI | 0 | 100 | %
46630 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL05AA101XQ12 |  | 10HHL05AA101XQ12 | Front wall upper bed burner hot primary air control damper 1 pos | AI | 0 | 100 | %
46631 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL06AA101XQ12 |  | 10HHL06AA101XQ12 | Back wall upper bed burner hot primary air control damper 1 posi | AI | 0 | 100 | %
46632 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL06AA102XQ12 |  | 10HHL06AA102XQ12 | Back wall upper bed burner hot primary air control damper 2 posi | AI | 0 | 100 | %
46633 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL11AA101XQ12 |  | 10HHL11AA101XQ12 | Side-A front upper secondary air inlet control valve position fe | AI | 0 | 100 | %
46634 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL12AA101XQ12 |  | 10HHL12AA101XQ12 | Side-A back upper secondary air inlet control valve position fee | AI | 0 | 100 | %
46635 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL13AA101XQ12 |  | 10HHL13AA101XQ12 | Side-A front lower secondary air inlet control valve position fe | AI | 0 | 100 | %
46636 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL14AA101XQ12 |  | 10HHL14AA101XQ12 | Side-A back lower secondary air inlet control valve position fee | AI | 0 | 100 | %
46637 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL21AA101XQ12 |  | 10HHL21AA101XQ12 | Side-B front upper secondary air inlet control valve position fe | AI | 0 | 100 | %
46638 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL22AA101XQ12 |  | 10HHL22AA101XQ12 | Side-B back upper secondary air inlet control valve position fee | AI | 0 | 100 | %
46639 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL23AA101XQ12 |  | 10HHL23AA101XQ12 | Side-B front lower secondary air inlet control valve position fe | AI | 0 | 100 | %
46640 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL24AA101XQ12 |  | 10HHL24AA101XQ12 | Side-B back lower secondary air inlet control valve position fee | AI | 0 | 100 | %
46641 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL02AA101XQ11 |  | 10HHL02AA101XQ11 | A air duct ignitor inlet motor-driven control damper 1 control c | AO | 0 | 100 | %
46642 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL02AA102XQ11 |  | 10HHL02AA102XQ11 | A air duct ignitor inlet motor-driven control damper 2 control c | AO | 0 | 100 | %
46643 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL02AA103XQ11 |  | 10HHL02AA103XQ11 | A air duct ignitor inlet motor-driven control damper 3 control c | AO | 0 | 100 | %
46644 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL03AA101XQ11 |  | 10HHL03AA101XQ11 | B air duct ignitor inlet motor-driven control damper 1 control c | AO | 0 | 100 | %
46645 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL03AA102XQ11 |  | 10HHL03AA102XQ11 | B air duct ignitor inlet motor-driven control damper 2 control c | AO | 0 | 100 | %
46646 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL03AA103XQ11 |  | 10HHL03AA103XQ11 | B air duct ignitor inlet motor-driven control damper 3 control c | AO | 0 | 100 | %
46647 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL05AA101XQ11 |  | 10HHL05AA101XQ11 | Front wall upper bed burner hot primary air control damper 1 con | AO | 0 | 100 | %
46648 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL05AA102XQ11 |  | 10HHL05AA102XQ11 | Front wall upper bed burner hot primary air control damper 2 con | AO | 0 | 100 | %
46649 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL06AA101XQ11 |  | 10HHL06AA101XQ11 | Back wall upper bed burner hot primary air control damper 1 cont | AO | 0 | 100 | %
46650 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AO.10HHL06AA102XQ11 |  | 10HHL06AA102XQ11 | Back wall upper bed burner hot primary air control damper 2 cont | AO | 0 | 100 | %
46651 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL11AA101XQ11 |  | 10HHL11AA101XQ11 | Side-A front upper secondary air inlet control valve control com | AO | 0 | 100 | %
46652 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL12AA101XQ11 |  | 10HHL12AA101XQ11 | Side-A back upper secondary air inlet control valve control comm | AO | 0 | 100 | %
46653 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL13AA101XQ11 |  | 10HHL13AA101XQ11 | Side-A front lower secondary air inlet control valve control com | AO | 0 | 100 | %
46654 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL14AA101XQ11 |  | 10HHL14AA101XQ11 | Side-A back lower secondary air inlet control valve control comm | AO | 0 | 100 | %
46655 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL21AA101XQ11 |  | 10HHL21AA101XQ11 | Side-B front upper secondary air inlet control valve control com | AO | 0 | 100 | %
46656 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL22AA101XQ11 |  | 10HHL22AA101XQ11 | Side-B back upper secondary air inlet control valve control comm | AO | 0 | 100 | %
46657 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL23AA101XQ11 |  | 10HHL23AA101XQ11 | Side-B front lower secondary air inlet control valve control com | AO | 0 | 100 | %
46658 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AO.10HHL24AA101XQ11 |  | 10HHL24AA101XQ11 | Side-B back lower secondary air inlet control valve control comm | AO | 0 | 100 | %
46659 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.RTD.10HHL20CT101 |  | 10HHL20CT101 | Side-B hot secondary air temperature | RTD | 0 | 300 | ℃
46660 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT101 |  | 10HBK11CT101 | Side-A furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950 | [5 empty] | 1
46661 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT102 |  | 10HBK11CT102 | Side-A furnace internal temperature 1 | TC | 0 | 1200 | ℃
46662 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT103 |  | 10HBK11CT103 | Side-A furnace internal temperature 2 | TC | 0 | 1200 | ℃
46663 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT104 |  | 10HBK11CT104 | Side-A furnace internal temperature 3 | TC | 0 | 1200 | ℃
46664 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT105 |  | 10HBK11CT105 | Side-A furnace internal temperature 4 | TC | 0 | 1200 | ℃
46665 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT106 |  | 10HBK11CT106 | A start-up burner outlet flue gas temperature | TC | 0 | 2000 | ℃ |  |  |  | 980 | [5 empty] | 1
46666 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK11CT107 |  | 10HBK11CT107 | Side-A furnace air chamber inlet duct temperature | TC | 0 | 1500 | ℃
46667 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT101 |  | 10HBK21CT101 | Side-B furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950 | [5 empty] | 1
46668 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT102 |  | 10HBK21CT102 | Side-B furnace internal temperature 1 | TC | 0 | 1200 | ℃
46669 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT103 |  | 10HBK21CT103 | Side-B furnace internal temperature 2 | TC | 0 | 1200 | ℃
46670 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT104 |  | 10HBK21CT104 | Side-B furnace internal temperature 3 | TC | 0 | 1200 | ℃
46671 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT105 |  | 10HBK21CT105 | Side-B furnace internal temperature 4 | TC | 0 | 1200 | ℃
46672 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT106 |  | 10HBK21CT106 | B start-up burner outlet flue gas temperature | TC | 0 | 2000 | ℃ |  |  |  | 980 | [5 empty] | 1
46673 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK21CT107 |  | 10HBK21CT107 | Side-B furnace air chamber inlet duct temperature | TC | 0 | 1500 | ℃
46674 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT101 |  | 10HBK30CT101 | Boiler front wall burning chamber bed temperature 1 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46675 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT102 |  | 10HBK30CT102 | Boiler front wall burning chamber bed temperature 2 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46676 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT103 |  | 10HBK30CT103 | Boiler front wall burning chamber bed temperature 3 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46677 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT104 |  | 10HBK30CT104 | Boiler front wall burning chamber bed temperature 4 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46678 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT105 |  | 10HBK30CT105 | Boiler front wall burning chamber bed temperature 5 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46679 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT106 |  | 10HBK30CT106 | Boiler front wall burning chamber bed temperature 6 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46680 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT107 |  | 10HBK30CT107 | Boiler front wall burning chamber bed temperature 7 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46681 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK30CT108 |  | 10HBK30CT108 | Boiler front wall burning chamber bed temperature 8 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46682 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK40CT101 |  | 10HBK40CT101 | Boiler back wall burning chamber bed temperature 1 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46683 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK40CT102 |  | 10HBK40CT102 | Boiler back wall burning chamber bed temperature 2 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46684 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK40CT103 |  | 10HBK40CT103 | Boiler back wall burning chamber bed temperature 3 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46685 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.TC.10HBK40CT104 |  | 10HBK40CT104 | Boiler back wall burning chamber bed temperature 4 | TC | 0 | 1100 | ℃ |  |  | 760 | 990 | [5 empty] | 0 | 1
46686 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP105 |  | 10HBK11CP105 | Side-A furnace bed pressure 3 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46687 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP106 |  | 10HBK11CP106 | Side-A furnace bed pressure 2 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46688 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP107 |  | 10HBK11CP107 | Side-A furnace bed pressure 1 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46689 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP108 |  | 10HBK11CP108 | Side-A furnace air chamber inlet duct pressure | AI | 0 | 25 | kPa
46690 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP105 |  | 10HBK21CP105 | Side-B furnace bed pressure 3 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46691 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP106 |  | 10HBK21CP106 | Side-B furnace bed pressure 2 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46692 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP107 |  | 10HBK21CP107 | Side-B furnace bed pressure 1 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
46693 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP108 |  | 10HBK21CP108 | Side-B furnace air chamber inlet duct pressure | AI | 0 | 25 | kPa
46694 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL02CP101 |  | 10HHL02CP101 | Furnace air chamber pressure 1 | AI | 0 | 20 | kPa
46695 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL03CP101 |  | 10HHL03CP101 | Furnace air chamber pressure 2 | AI | 0 | 20 | kPa
46696 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL11CP101 |  | 10HHL11CP101 | Upper secondary air box pressure | AI | 0 | 10 | kPa
46697 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL13CP101 |  | 10HHL13CP101 | Lower secondary air box pressure | AI | 0 | 15 | kPa
46698 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL20CP101 |  | 10HHL20CP101 | Side-B hot secondary air pressure | AI | 0 | 15 | kPa
46699 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL21CP101 |  | 10HHL21CP101 | Upper secondary air box pressure | AI | 0 | 15 | kPa
46700 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL23CP101 |  | 10HHL23CP101 | Lower secondary air box pressure | AI | 0 | 15 | kPa
46701 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL02CF101 |  | 10HHL02CF101 | A air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
46702 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL03CF101 |  | 10HHL03CF101 | B air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
46703 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-04 | KALTIM1.SIGNAL.AI.10HHL04CF101 |  | 10HHL04CF101 | Upper bed burner hot primary air flow | AI | 0 | 999999 | Nm3/h
46704 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL11CF101 |  | 10HHL11CF101 | Side-A front upper secondary air flow | AI | 0 | 999999 | Nm3/h
46705 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL12CF101 |  | 10HHL12CF101 | Side-A back upper secondary air flow | AI | 0 | 999999 | Nm3/h
46706 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL13CF101 |  | 10HHL13CF101 | Side-A front lower secondary air flow | AI | 0 | 999999 | Nm3/h
46707 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL14CF101 |  | 10HHL14CF101 | Side-A back lower secondary air flow | AI | 0 | 999999 | Nm3/h
46708 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL21CF101 |  | 10HHL21CF101 | Side-B front upper secondary air flow | AI | 0 | 999999 | Nm3/h
46709 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL22CF101 |  | 10HHL22CF101 | Side-B back upper secondary air flow | AI | 0 | 999999 | Nm3/h
46710 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL23CF101 |  | 10HHL23CF101 | Side-B front lower secondary air flow | AI | 0 | 999999 | Nm3/h
46711 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-05 | KALTIM1.SIGNAL.AI.10HHL24CF101 |  | 10HHL24CF101 | Side-B back lower secondary air flow | AI | 0 | 999999 | Nm3/h
46712 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP103 |  | 10HBK11CP103 | Side-A furnace middle pressure | AI | 0 | 2000 | Pa
46713 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP103 |  | 10HBK21CP103 | Side-B furnace middle pressure | AI | 0 | 2000 | Pa
46714 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP101 |  | 10HBK11CP101 | Side-A furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
46715 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP102 |  | 10HBK11CP102 | Side-A furnace differencial pressure | AI | -500 | 4000 | Pa
46716 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK11CP401 |  | 10HBK11CP401 | Side-A furnace lower pressure | AI | 0 | 5000 | Pa
46717 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP101 |  | 10HBK21CP101 | Side-B furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000
46718 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP102 |  | 10HBK21CP102 | Side-B furnace differencial pressure | AI | -500 | 4000 | Pa
46719 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE | K0102-07 | KALTIM1.SIGNAL.AI.10HBK21CP401 |  | 10HBK21CP401 | Side-B furnace lower pressure | AI | 0 | 5000 | Pa
48884 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE |  | 10HFB10AF901XQ02 |  | 10HFB10AF901XQ02 | Total flow rate coal Fuel #1 | CALC | 0 | 100 | t/h | [8 empty] | (KALTIM1.SIGNAL.AI.10HFB10AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB20AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB30AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB40AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB50AF001XQ02)+(KALTIM1.SIGNAL.AI.10HFB60AF001XQ02)
48893 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #2 FURNACE |  | 20HFB10AF901XQ02 |  | 20HFB10AF901XQ02 | Total flow rate coal Fuel #2 | CALC | 0 | 100 | t/h | [8 empty] | (KALTIM2.SIGNAL.AI.20HFB10AF001XQ02)+(KALTIM2.SIGNAL.AI.20HFB20AF001XQ02)+(KALTIM2.SIGNAL.AI.20HFB30AF001XQ02)+(KALTIM2.SIGNAL.AI.20HFB40AF001XQ02)+(KALTIM2.SIGNAL.AI.20HFB50AF001XQ02)+(KALTIM2.SIGNAL.AI.20HFB60AF001XQ02)
49123 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 14 | #1 FURNACE |  | 10HBK11CT902 |  | 10HBK11CT902 | Boiler Bed Temperature | CALC | 0 | 1200 | ℃ | [8 empty] | AVG((KALTIM1.SIGNAL.TC.10HBK11CT102);( KALTIM1.SIGNAL.TC.10HBK11CT103);( KALTIM1.SIGNAL.TC.10HBK11CT104);( KALTIM1.SIGNAL.TC.10HBK11CT105);( KALTIM1.SIGNAL.TC.10HBK21CT102);( KALTIM1.SIGNAL.TC.10HBK21CT103);( KALTIM1.SIGNAL.TC.10HBK21CT104);( KALTIM1.SIGNAL.TC.10HBK21CT105))
46720 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJA21CB102 |  | 10HJA21CB102 | A lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46721 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJA21CB103 |  | 10HJA21CB103 | A lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46722 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJA21CB101 |  | 10HJA21CB101 | A lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46723 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20AA101XQ12 |  | 10HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
46724 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20AA101XQ12 |  | 10HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
46725 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJF20AA101XQ11 |  | 10HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
46726 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJS20AA101XQ11 |  | 10HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
46727 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.TC.10HJS20CT101 |  | 10HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
46728 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP101 |  | 10HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa |  |  |  | 50 | [5 empty] | 1
46729 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP102 |  | 10HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa |  |  |  | 50 | [5 empty] | 1
46730 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP102 |  | 10HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
46731 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20CP101 |  | 10HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
46735 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP101 |  | 10HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
48977 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJF20AA101XQ11 |  | 10HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
48978 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20AA101XQ12 |  | 10HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48979 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP101 |  | 10HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48980 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP102 |  | 10HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48981 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP101 |  | 10HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
48982 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP102 |  | 10HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
48983 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJS20AA101XQ11 |  | 10HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
48984 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20AA101XQ12 |  | 10HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48985 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20CP101 |  | 10HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48986 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.TC.10HJS20CT101 |  | 10HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
48987 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJF20AA101XQ11 |  | 10HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
48988 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20AA101XQ12 |  | 10HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48989 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP101 |  | 10HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48990 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP102 |  | 10HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48991 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP101 |  | 10HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
48992 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP102 |  | 10HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
48993 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJS20AA101XQ11 |  | 10HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
48994 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20AA101XQ12 |  | 10HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48995 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20CP101 |  | 10HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48996 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.TC.10HJS20CT101 |  | 10HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
48997 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJF20AA101XQ11 |  | 10HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
48998 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20AA101XQ12 |  | 10HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48999 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP101 |  | 10HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
49000 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJF20CP102 |  | 10HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
49001 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP101 |  | 10HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
49002 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJL20CP102 |  | 10HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
49003 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AO.10HJS20AA101XQ11 |  | 10HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
49004 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20AA101XQ12 |  | 10HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
49005 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.AI.10HJS20CP101 |  | 10HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
49006 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 15 | #1 LOWER BURNER A | K0102-13 | KALTIM1.SIGNAL.TC.10HJS20CT101 |  | 10HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
46732 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 16 | #1 LOWER BURNER B | K0102-13 | KALTIM1.SIGNAL.AI.10HJA22CB101 |  | 10HJA22CB101 | B lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46733 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 16 | #1 LOWER BURNER B | K0102-13 | KALTIM1.SIGNAL.AI.10HJA22CB102 |  | 10HJA22CB102 | B lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46734 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 16 | #1 LOWER BURNER B | K0102-13 | KALTIM1.SIGNAL.AI.10HJA22CB103 |  | 10HJA22CB103 | B lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46736 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 17 | #1 LOWER BURNER C | K0102-13 | KALTIM1.SIGNAL.AI.10HJA23CB101 |  | 10HJA23CB101 | C lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46737 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 17 | #1 LOWER BURNER C | K0102-13 | KALTIM1.SIGNAL.AI.10HJA23CB102 |  | 10HJA23CB102 | C lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46738 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 17 | #1 LOWER BURNER C | K0102-13 | KALTIM1.SIGNAL.AI.10HJA23CB103 |  | 10HJA23CB103 | C lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46739 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 18 | #1 LOWER BURNER D | K0102-13 | KALTIM1.SIGNAL.AI.10HJA24CB102 |  | 10HJA24CB102 | D lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
46740 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 18 | #1 LOWER BURNER D | K0102-13 | KALTIM1.SIGNAL.AI.10HJA24CB101 |  | 10HJA24CB101 | D lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
46741 | 1 | UJKTT #1 | 2 | #1 BOILER SYSTEM | 18 | #1 LOWER BURNER D | K0102-13 | KALTIM1.SIGNAL.AI.10HJA24CB103 |  | 10HJA24CB103 | D lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
46742 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 1 | #1 COAL BUNKER A | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA10CL101 |  | 10HFA10CL101 | #1 Boiler A coal hopper level | AI | 0 | 15 | m
46743 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 2 | #1 COAL BUNKER B | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA20CL101 |  | 10HFA20CL101 | #1 Boiler B coal hopper level | AI | 0 | 15 | m
46744 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 3 | #1 COAL BUNKER C | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA30CL101 |  | 10HFA30CL101 | #1 Boiler C coal hopper level | AI | 0 | 15 | m
46745 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 4 | #1 COAL BUNKER D | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA40CL101 |  | 10HFA40CL101 | #1 Boiler D coal hopper level | AI | 0 | 15 | m
46746 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 5 | #1 COAL BUNKER E | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA50CL101 |  | 10HFA50CL101 | #1 Boiler E coal hopper level | AI | 0 | 15 | m
46747 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 6 | #1 COAL BUNKER F | K0102-10 | KALTIM 0.SIGNAL.AI.10HFA60CL101 |  | 10HFA60CL101 | #1 Boiler F coal hopper level | AI | 0 | 15 | m
46748 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-10 | KALTIM1.SIGNAL.AI.10HFB10AF001XQ01 |  | 10HFB10AF001XQ01 | A coal feeder speed feedback | AI | 0 | 100 | %
46749 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-10 | KALTIM1.SIGNAL.AI.10HFB10AA002XQ12 |  | 10HFB10AA002XQ12 | A Coal Feeder Outlet Valve Feedback | AI | 0 | 100 | %
46750 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-10 | KALTIM1.SIGNAL.AO.10HFB10AF001XQ11 |  | 10HFB10AF001XQ11 | A coal feeder speed control | AO | 0 | 100 | %
46751 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
46752 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW11CF101 |  | 10HEW11CF101 | A coal feeder seal air flow | AI | 0 | 4000 | m3/h
46753 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE11CF101 |  | 10HFE11CF101 | A inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46754 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE12CF101 |  | 10HFE12CF101 | A inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46755 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-10 | KALTIM1.SIGNAL.AI.10HFB10AF001XQ02 |  | 10HFB10AF001XQ02 | A coal feeder flow feedback | AI | 0 | 30 | t/h
49037 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49038 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49039 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49040 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49041 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 7 | #1 COAL FEEDER A | K0102-04 | KALTIM1.SIGNAL.AI.10HEW10CP101 |  | 10HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
46756 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-10 | KALTIM1.SIGNAL.AI.10HFB20AF001XQ01 |  | 10HFB20AF001XQ01 | B coal feeder speed feedback | AI | 0 | 100 | %
46757 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-10 | KALTIM1.SIGNAL.AI.10HFB20AA002XQ12 |  | 10HFB20AA002XQ12 | B coal feeder outlet valve feedback | AI | 0 | 100 | %
46758 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-10 | KALTIM1.SIGNAL.AO.10HFB20AF001XQ11 |  | 10HFB20AF001XQ11 | B coal feeder speed control | AO | 0 | 100 | %
46759 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-04 | KALTIM1.SIGNAL.AI.10HEW12CF101 |  | 10HEW12CF101 | B coal feeder seal air flow | AI | 0 | 4000 | m3/h
46760 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE21CF101 |  | 10HFE21CF101 | B inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46761 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE22CF101 |  | 10HFE22CF101 | B inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46762 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 8 | #1 COAL FEEDER B | K0102-10 | KALTIM1.SIGNAL.AI.10HFB20AF001XQ02 |  | 10HFB20AF001XQ02 | B coal feeder flow feedback | AI | 0 | 30 | t/h
46763 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-10 | KALTIM1.SIGNAL.AI.10HFB30AA002XQ12 |  | 10HFB30AA002XQ12 | C coal feeder outlet valve feedback | AI | 0 | 100 | %
46764 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-10 | KALTIM1.SIGNAL.AI.10HFB30AF001XQ01 |  | 10HFB30AF001XQ01 | C coal feeder speed feedback | AI | 0 | 100 | %
46765 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-04 | KALTIM1.SIGNAL.AI.10HFE32CF101 |  | 10HFE32CF101 | C inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46766 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-04 | KALTIM1.SIGNAL.AI.10HEW13CF101 |  | 10HEW13CF101 | C coal feeder seal air flow | AI | 0 | 4000 | m3/h
46767 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-04 | KALTIM1.SIGNAL.AI.10HFE31CF101 |  | 10HFE31CF101 | C inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46768 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-10 | KALTIM1.SIGNAL.AI.10HFB30AF001XQ02 |  | 10HFB30AF001XQ02 | C coal feeder flow feedback | AI | 0 | 30 | t/h
46771 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 9 | #1 COAL FEEDER C | K0102-10 | KALTIM1.SIGNAL.AO.10HFB30AF001XQ11 |  | 10HFB30AF001XQ11 | C coal feeder speed control | AO | 0 | 100 | %
46769 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-10 | KALTIM1.SIGNAL.AI.10HFB40AF001XQ01 |  | 10HFB40AF001XQ01 | D coal feeder speed feedback | AI | 0 | 100 | %
46770 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-10 | KALTIM1.SIGNAL.AI.10HFB40AA002XQ12 |  | 10HFB40AA002XQ12 | D coal feeder outlet valve feedback | AI | 0 | 100 | %
46772 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-10 | KALTIM1.SIGNAL.AO.10HFB40AF001XQ11 |  | 10HFB40AF001XQ11 | D coal feeder speed control | AO | 0 | 100 | %
46773 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-04 | KALTIM1.SIGNAL.AI.10HEW14CF101 |  | 10HEW14CF101 | D coal feeder seal air flow | AI | 0 | 4000 | m3/h
46774 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-04 | KALTIM1.SIGNAL.AI.10HFE41CF101 |  | 10HFE41CF101 | D inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46775 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-04 | KALTIM1.SIGNAL.AI.10HFE42CF101 |  | 10HFE42CF101 | D inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46776 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 10 | #1 COAL FEEDER D | K0102-10 | KALTIM1.SIGNAL.AI.10HFB40AF001XQ02 |  | 10HFB40AF001XQ02 | D coal feeder flow feedback | AI | 0 | 30 | t/h
46777 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-10 | KALTIM1.SIGNAL.AI.10HFB50AF001XQ01 |  | 10HFB50AF001XQ01 | E coal feeder speed feedback | AI | 0 | 100 | %
46778 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-10 | KALTIM1.SIGNAL.AI.10HFB50AA002XQ12 |  | 10HFB50AA002XQ12 | E coal feeder outlet valve feedback | AI | 0 | 100 | %
46779 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-10 | KALTIM1.SIGNAL.AO.10HFB50AF001XQ11 |  | 10HFB50AF001XQ11 | E coal feeder speed control | AO | 0 | 100 | %
46780 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-04 | KALTIM1.SIGNAL.AI.10HEW15CF101 |  | 10HEW15CF101 | E coal feeder seal air flow | AI | 0 | 4000 | m3/h
46781 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-04 | KALTIM1.SIGNAL.AI.10HFE51CF101 |  | 10HFE51CF101 | E inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46782 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-04 | KALTIM1.SIGNAL.AI.10HFE52CF101 |  | 10HFE52CF101 | E inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46783 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 11 | #1 COAL FEEDER E | K0102-10 | KALTIM1.SIGNAL.AI.10HFB50AF001XQ02 |  | 10HFB50AF001XQ02 | E coal feeder flow feedback | AI | 0 | 30 | t/h
46784 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-10 | KALTIM1.SIGNAL.AI.10HFB60AA002XQ12 |  | 10HFB60AA002XQ12 | F coal feeder outlet valve feedback | AI | 0 | 100 | %
46785 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-10 | KALTIM1.SIGNAL.AI.10HFB60AF001XQ01 |  | 10HFB60AF001XQ01 | F coal feeder speed feedback | AI | 0 | 100 | %
46786 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-10 | KALTIM1.SIGNAL.AO.10HFB60AF001XQ11 |  | 10HFB60AF001XQ11 | F coal feeder speed control | AO | 0 | 100 | %
46787 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-04 | KALTIM1.SIGNAL.AI.10HEW16CF101 |  | 10HEW16CF101 | F coal feeder seal air flow | AI | 0 | 4000 | m3/h
46788 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-04 | KALTIM1.SIGNAL.AI.10HFE61CF101 |  | 10HFE61CF101 | F inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
46789 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-04 | KALTIM1.SIGNAL.AI.10HFE62CF101 |  | 10HFE62CF101 | F inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
46790 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 12 | #1 COAL FEEDER F | K0102-10 | KALTIM1.SIGNAL.AI.10HFB60AF001XQ02 |  | 10HFB60AF001XQ02 | F coal feeder flow feedback | AI | 0 | 30 | t/h
46791 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE10AA101XQ12 |  | 10HFE10AA101XQ12 | A coal spreading booster fan inlet control damper position feedb | AI | 0 | 100 | %
46792 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AO.10HFE10AA101XQ11 |  | 10HFE10AA101XQ11 | A coal spreading booster fan inlet control damper control comman | AO | 0 | 100 | %
46793 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE10AN001XQ01 |  | 10HFE10AN001XQ01 | A coal spreading booster fan current | AI | 0 | 75 | A
46794 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT101 |  | 10HFE10CT101 | A coal spreading booster fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46795 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT102 |  | 10HFE10CT102 | A coal spreading booster fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46796 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT103 |  | 10HFE10CT103 | A coal spreading booster fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46797 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT104 |  | 10HFE10CT104 | A coal spreading booster fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46798 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT105 |  | 10HFE10CT105 | A coal spreading booster fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46799 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT106 |  | 10HFE10CT106 | A coal spreading booster fan motor stator temperature 2 | RTD | 0 | 100 | ℃ | [10 empty] | 1
46800 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT107 |  | 10HFE10CT107 | A coal spreading booster fan motor stator temperature 3 | RTD | 0 | 100 | ℃ | [10 empty] | 1
46801 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT108 |  | 10HFE10CT108 | A coal spreading booster fan motor stator temperature 4 | RTD | 0 | 100 | ℃ | [10 empty] | 1
46802 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT109 |  | 10HFE10CT109 | A coal spreading booster fan motor stator temperature 5 | RTD | 0 | 100 | ℃ | [10 empty] | 1
46803 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE10CT110 |  | 10HFE10CT110 | A coal spreading booster fan motor stator temperature 6 | RTD | 0 | 100 | ℃ | [10 empty] | 1
46804 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE10CP101 |  | 10HFE10CP101 | A coal spreading booster fan outlet pressure | AI | 0 | 50 | kPa |  | 25
46805 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE30CP101 |  | 10HFE30CP101 | Coal spreading air main pipe pressure | AI | 0 | 50 | kPa
46806 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE10CY101 |  | 10HFE10CY101 | A coal spreading booster fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
46807 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE10CY102 |  | 10HFE10CY102 | A coal spreading booster fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
49047 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 13 | #1 CFB FAN A | K0102-04 | KALTIM1.SIGNAL.AI.10HFE30CP101 |  | 10HFE30CP101 | Coal spreading air main pipe pressure | AI | 0 | 50 | kPa
46808 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE20AA101XQ12 |  | 10HFE20AA101XQ12 | B coal spreading booster fan inlet control damper position feedb | AI | 0 | 100 | %
46809 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AO.10HFE20AA101XQ11 |  | 10HFE20AA101XQ11 | B coal spreading booster fan inlet control damper control comman | AO | 0 | 100 | %
46810 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE20AN001XQ01 |  | 10HFE20AN001XQ01 | B coal spreading booster fan current | AI | 0 | 75 | A
46811 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT101 |  | 10HFE20CT101 | B coal spreading booster fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46812 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT102 |  | 10HFE20CT102 | B coal spreading booster fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46813 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT103 |  | 10HFE20CT103 | B coal spreading booster fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46814 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT104 |  | 10HFE20CT104 | B coal spreading booster fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46815 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT105 |  | 10HFE20CT105 | B coal spreading booster fan motor stator temperature 1 | RTD | 0 | 200 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
46816 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT106 |  | 10HFE20CT106 | B coal spreading booster fan motor stator temperature 2 | RTD | 0 | 200 | ℃ | [10 empty] | 1
46817 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT107 |  | 10HFE20CT107 | B coal spreading booster fan motor stator temperature 3 | RTD | 0 | 200 | ℃ | [10 empty] | 1
46818 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT108 |  | 10HFE20CT108 | B coal spreading booster fan motor stator temperature 4 | RTD | 0 | 200 | ℃ | [10 empty] | 1
46819 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT109 |  | 10HFE20CT109 | B coal spreading booster fan motor stator temperature 5 | RTD | 0 | 200 | ℃ | [10 empty] | 1
46820 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.RTD.10HFE20CT110 |  | 10HFE20CT110 | B coal spreading booster fan motor stator temperature 6 | RTD | 0 | 200 | ℃ | [10 empty] | 1
46821 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE20CP101 |  | 10HFE20CP101 | B coal spreading booster fan outlet pressure | AI | 0 | 50 | kPa |  | 25
46822 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE20CY101 |  | 10HFE20CY101 | B coal spreading booster fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
46823 | 1 | UJKTT #1 | 3 | #1 COAL FEEDING SYSTEM | 14 | #1 CFB FAN B | K0102-04 | KALTIM1.SIGNAL.AI.10HFE20CY102 |  | 10HFE20CY102 | B coal spreading booster fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
46824 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB21AA101XQ12 |  | 10LAB21AA101XQ12 | A EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
46825 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20MK001XQ12 |  | 10LAC20MK001XQ12 | A EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
46826 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AO.10LAB21AA101XQ11 |  | 10LAB21AA101XQ11 | A EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
46827 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AO.10LAC20MK001XQ11 |  | 10LAC20MK001XQ11 | A EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
46828 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAC20AP001XQ01 |  | 10LAC20AP001XQ01 | A EFWP CURRENT | AI | 0 | 300 | A |  |  |  | 174 | [5 empty] | 1 | 1
46829 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB50CT101 |  | 10LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
46830 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT101 |  | 10LAC20CT101 | TEMP OF A EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46831 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT102 |  | 10LAC20CT102 | TEMP OF A EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46832 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT103 |  | 10LAC20CT103 | A EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46833 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT104 |  | 10LAC20CT104 | A EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46834 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT105 |  | 10LAC20CT105 | A EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46835 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT106 |  | 10LAC20CT106 | A EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46836 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT107 |  | 10LAC20CT107 | A EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46837 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT108 |  | 10LAC20CT108 | A EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46838 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT109 |  | 10LAC20CT109 | TEMP 1 OF A EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46839 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT110 |  | 10LAC20CT110 | TEMP 2 OF A EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46840 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT113 |  | 10LAC20CT113 | TEMP OF A EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46841 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT114 |  | 10LAC20CT114 | TEMP OF A EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46842 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT115 |  | 10LAC20CT115 | TEMP OF A EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46843 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT116 |  | 10LAC20CT116 | OIL TEMP OF A EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
46844 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT117 |  | 10LAC20CT117 | OIL TEMP OF A EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
46845 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT118 |  | 10LAC20CT118 | OIL TEMP OF A EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46846 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.RTD.10LAC20CT119 |  | 10LAC20CT119 | OIL TEMP OF A EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 110 | 130 |  |  |  |  | 1 | 1
46847 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAC20CP101 |  | 10LAC20CP101 | DIFF P OF A EFWP INLET FLTR | AI | 0 | 100 | kPa | 0.07 | 0.1 | 0.15 | [6 empty] | 2
46848 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CY105 |  | 10LAC20CY105 | AXIAL DISPLACEMENT OF TURB A EFWP | AI | -2 | 2 | mm |  |  |  | 0.2 | [5 empty] | 1 | 1
46849 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CY101 |  | 10LAC20CY101 | SHAFT VIBRATION OF A EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46850 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CY102 |  | 10LAC20CY102 | SHAFT VIBRATION OF A EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46851 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CY103 |  | 10LAC20CY103 | SHAFT VIBRATION OF A EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46852 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CY104 |  | 10LAC20CY104 | SHAFT VIBRATION OF A EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46853 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB20CP101 |  | 10LAB20CP101 | P OF A EFWP INLET | AI | 0 | 1 | MPa
46854 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB20CP102 |  | 10LAB20CP102 | P OF A EFWP OUTLET | AI | 0 | 20 | MPa
46855 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB50CP101 |  | 10LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
46856 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CP102 |  | 10LAC20CP102 | A EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa | 0.07 | 0.1 | 0.15 | [6 empty] | 2
46857 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM1.SIGNAL.AI.10LAC20CS101 |  | 10LAC20CS101 | A EFWP SPEED | AI | 0 | 4020 | rpm
49049 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB50CP101 |  | 10LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
49050 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB50CT101 |  | 10LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
49051 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.AI.10LAB50CP101 |  | 10LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
49052 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 1 | #1 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB50CT101 |  | 10LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
46858 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AI.10LAB31AA101XQ12 |  | 10LAB31AA101XQ12 | B EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
46859 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30MK001XQ12 |  | 10LAC30MK001XQ12 | B EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
46860 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AO.10LAB31AA101XQ11 |  | 10LAB31AA101XQ11 | B EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
46861 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AO.10LAC30MK001XQ11 |  | 10LAC30MK001XQ11 | B EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
46862 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AI.10LAC30AP001XQ01 |  | 10LAC30AP001XQ01 | B EFWP CURRENT | AI | 0 | 351 | A
46863 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT101 |  | 10LAC30CT101 | TEMP OF B EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46864 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT102 |  | 10LAC30CT102 | TEMP OF B EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46865 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT103 |  | 10LAC30CT103 | B EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46866 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT104 |  | 10LAC30CT104 | B EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46867 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT105 |  | 10LAC30CT105 | B EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46868 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT106 |  | 10LAC30CT106 | B EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46869 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT107 |  | 10LAC30CT107 | B EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46870 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT108 |  | 10LAC30CT108 | B EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46871 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT109 |  | 10LAC30CT109 | TEMP 1 OF B EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46872 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT110 |  | 10LAC30CT110 | TEMP 2 OF B EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46873 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT113 |  | 10LAC30CT113 | TEMP OF B EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46874 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT114 |  | 10LAC30CT114 | TEMP OF B EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46875 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT115 |  | 10LAC30CT115 | TEMP OF B EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46876 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT116 |  | 10LAC30CT116 | OIL TEMP OF B EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
46877 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT117 |  | 10LAC30CT117 | OIL TEMP OF B EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
46878 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT118 |  | 10LAC30CT118 | OIL TEMP OF B EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46879 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.RTD.10LAC30CT119 |  | 10LAC30CT119 | OIL TEMP OF B EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 110 | 130 |  |  |  |  | 1 | 1
46880 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AI.10LAC30CP101 |  | 10LAC30CP101 | DIFF P OF B EFWP INLET FLTR | AI | 0 | 100 | kPa | 0.07 | 0.1 | 0.15 | [6 empty] | 2
46881 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CY105 |  | 10LAC30CY105 | AXIAL DISPLACEMENT OF TURB B EFWP | AI | -2 | 2 | mm |  |  |  | 0.2 | 0.25 |  |  |  |  | 1 | 1
46882 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CY101 |  | 10LAC30CY101 | SHAFT VIBRATION OF B EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46883 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CY102 |  | 10LAC30CY102 | SHAFT VIBRATION OF B EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46884 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CY103 |  | 10LAC30CY103 | SHAFT VIBRATION OF B EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46885 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CY104 |  | 10LAC30CY104 | SHAFT VIBRATION OF B EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46886 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AI.10LAB30CP101 |  | 10LAB30CP101 | P OF B EFWP INLET | AI | 0 | 1 | MPa
46887 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM1.SIGNAL.AI.10LAB30CP102 |  | 10LAB30CP102 | P OF B EFWP OUTLET | AI | 0 | 20 | MPa
46888 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CP102 |  | 10LAC30CP102 | B EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa |  | 0.07 | 0.1 | [6 empty] | 2
46889 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM1.SIGNAL.AI.10LAC30CS101 |  | 10LAC30CS101 | B EFWP SPEED | AI | 0 | 4031 | rpm
47708 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.TC.20HJS10CT101 |  | 20HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
47713 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20HJS10CP101 |  | 20HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48953 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20HJS10CP101 |  | 20HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48954 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.TC.20HJS10CT101 |  | 20HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
48964 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20HJS10CP101 |  | 20HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48965 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.TC.20HJS10CT101 |  | 20HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
48975 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20HJS10CP101 |  | 20HJS10CP101 | Upper bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48976 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 2 | #1 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.TC.20HJS10CT101 |  | 20HJS10CT101 | Upper bed purging steam inlet temperature | TC | 0 | 300 | ℃
46890 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AI.10LAB41AA101XQ12 |  | 10LAB41AA101XQ12 | C EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
46891 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40MK001XQ12 |  | 10LAC40MK001XQ12 | C EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
46892 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AO.10LAB41AA101XQ11 |  | 10LAB41AA101XQ11 | C EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
46893 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AO.10LAC40MK001XQ11 |  | 10LAC40MK001XQ11 | C EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
46894 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AI.10LAC40AP001XQ01 |  | 10LAC40AP001XQ01 | C EFWP CURRENT | AI | 0 | 351 | A
46895 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT101 |  | 10LAC40CT101 | TEMP OF C EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46896 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT102 |  | 10LAC40CT102 | TEMP OF C EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
46897 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT103 |  | 10LAC40CT103 | C EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46898 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT104 |  | 10LAC40CT104 | C EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46899 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT105 |  | 10LAC40CT105 | C EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46900 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT106 |  | 10LAC40CT106 | C EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46901 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT107 |  | 10LAC40CT107 | C EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46902 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT108 |  | 10LAC40CT108 | C EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
46903 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT109 |  | 10LAC40CT109 | TEMP 1 OF C EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46904 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT110 |  | 10LAC40CT110 | TEMP 2 OF C EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
46905 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT113 |  | 10LAC40CT113 | TEMP OF C EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46906 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT114 |  | 10LAC40CT114 | TEMP OF C EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46907 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT115 |  | 10LAC40CT115 | TEMP OF C EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46908 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT116 |  | 10LAC40CT116 | OIL TEMP OF C EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
46909 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT117 |  | 10LAC40CT117 | OIL TEMP OF C EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
46910 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT118 |  | 10LAC40CT118 | OIL TEMP OF C EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
46911 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.RTD.10LAC40CT119 |  | 10LAC40CT119 | OIL TEMP OF C EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 110 | 130 |  |  |  |  | 1 | 1
46912 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AI.10LAC40CP101 |  | 10LAC40CP101 | DIFF P OF C EFWP INLET FLTR | AI | 0 | 100 | kPa | 0.07 | 0.1 | 0.15 | [6 empty] | 2
46913 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CY105 |  | 10LAC40CY105 | AXIAL DISPLACEMENT OF TURB C EFWP | AI | -2 | 2 | mm |  |  |  | 0.2 | 0.25 |  |  |  |  | 1 | 1
46914 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CY101 |  | 10LAC40CY101 | SHAFT VIBRATION OF C EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46915 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CY102 |  | 10LAC40CY102 | SHAFT VIBRATION OF C EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46916 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CY103 |  | 10LAC40CY103 | SHAFT VIBRATION OF C EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46917 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CY104 |  | 10LAC40CY104 | SHAFT VIBRATION OF C EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
46918 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AI.10LAB40CP101 |  | 10LAB40CP101 | P OF C EFWP INLET | AI | 0 | 1 | MPa
46919 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM1.SIGNAL.AI.10LAB40CP102 |  | 10LAB40CP102 | P OF C EFWP OUTLET | AI | 0 | 20 | MPa
46920 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CP102 |  | 10LAC40CP102 | C EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa |  |  | 0.1 | [6 empty] | 2
46921 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 3 | #1 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM1.SIGNAL.AI.10LAC40CS101 |  | 10LAC40CS101 | C EFWP SPEED | AI | 0 | 4045 | rpm
46922 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB51CT101 |  | 10LAB51CT101 | TEMP OF NO.2 HP HTR INLET | RTD | 0 | 300 | ℃
46923 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB51CT102 |  | 10LAB51CT102 | TEMP OF NO.2 HP HTR OUTLET | RTD | 0 | 300 | ℃
46924 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCH20CT101 |  | 10LCH20CT101 | NO.2 HP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
46925 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ20CT101 |  | 10LBQ20CT101 | UP WALL TEMP OF 2ND EXTR STM PIP | TC | 0 | 800 | ℃
46926 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ20CT102 |  | 10LBQ20CT102 | BTM WALL TEMP OF 2 EXTR STM PIP | TC | 0 | 800 | ℃
46927 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ20CT103 |  | 10LBQ20CT103 | TEMP OF 2ND EXTR STM PIP | TC | 0 | 800 | ℃
46931 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM1.SIGNAL.AI.10LBQ20CP101 |  | 10LBQ20CP101 | P OF 2ND EXTR STM PIP | AI | 0 | 2.5 | MPa
46943 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD20CL101 |  | 10LAD20CL101 | NO.2 HP HTR LEVEL 1 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46944 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD20CL102 |  | 10LAD20CL102 | NO.2 HP HTR LEVEL 2 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46945 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 4 | #1 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD20CL103 |  | 10LAD20CL103 | NO.2 HP HTR LEVEL 3 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46928 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD10CL101 |  | 10LAD10CL101 | NO.1 HP HTR LEVEL 1 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46929 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD10CL102 |  | 10LAD10CL102 | NO.1 HP HTR LEVEL 2 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46930 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM1.SIGNAL.AI.10LAD10CL103 |  | 10LAD10CL103 | NO.1 HP HTR LEVEL 3 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
46932 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AI.10LAB61AA101XQ12 |  | 10LAB61AA101XQ12 | Main feed water control valve position feedback | AI | 0 | 100 | %
46933 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AI.10LAB50AA101XQ12 |  | 10LAB50AA101XQ12 | Main Feed Water MOV Regulating Feedback | AI | 0 | 100 | %
46934 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AO.10LAB50AA101XQ11 |  | 10LAB50AA101XQ11 | Main Feed Water MOV Regulating Command | AO | 0 | 100 | %
46935 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AO.10LAB61AA101XQ11 |  | 10LAB61AA101XQ11 | Main feed water control valve control command | AO | 0 | 94 | %
46936 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB52CT101 |  | 10LAB52CT101 | TEMP OF NO.1 HP HTR INLET | RTD | 0 | 300 | ℃
46937 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-19 | KALTIM1.SIGNAL.RTD.10LAB52CT102 |  | 10LAB52CT102 | TEMP OF NO.1 HP HTR OUTLET | RTD | 0 | 300 | ℃
46938 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCH10CT101 |  | 10LCH10CT101 | NO.1 HP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
46939 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.TC.10LAB50CT102 |  | 10LAB50CT102 | Main boiler feed water temperature | TC | 0 | 400 | ℃
46940 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ10CT101 |  | 10LBQ10CT101 | UP WALL TEMP OF 1ST EXTR STM PIP | TC | 0 | 800 | ℃
46941 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ10CT102 |  | 10LBQ10CT102 | BTM WALL TEMP OF 1 EXTR STM PIP | TC | 0 | 800 | ℃
46942 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM1.SIGNAL.TC.10LBQ10CT103 |  | 10LBQ10CT103 | TEMP OF 1ST EXTR STM PIP | TC | 0 | 800 | ℃
46946 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM1.SIGNAL.AI.10LBQ10CP101 |  | 10LBQ10CP101 | P OF 1ST EXTR STM PIP | AI | 0 | 4 | MPa
46947 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AI.10LAB50CF101 |  | 10LAB50CF101 | Main boiler feed water flow 1 | AI | 0 | 1000 | t/h
46948 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM1.SIGNAL.AI.10LAB50CF102 |  | 10LAB50CF102 | Main boiler feed water flow 2 | AI | 0 | 1000 | t/h
48888 | 1 | UJKTT #1 | 4 | #1 FEED WATER SYSTEM | 5 | #1 HIGH PRESSURE HEATER 1 |  | 10LAB50CF901 |  | 10LAB50CF901 | Feedwater Flow | CALC | 0 | 1000 | t/h | [8 empty] | ((KALTIM1.SIGNAL.AI.10LAB50CF101)+(KALTIM1.SIGNAL.AI.10LAB50CF102))/2
48897 | 1 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 |  | 20LAB50CF901 |  | 20LAB50CF901 | Feedwater Flow | CALC | 0 | 1000 | t/h | [8 empty] | ((KALTIM2.SIGNAL.AI.20LAB50CF101)+(KALTIM2.SIGNAL.AI.20LAB50CF102))/2
46949 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNA10AA101XQ12 |  | 10HNA10AA101XQ12 | A iuduced draft fan inlet control damper position feedback | AI | 0 | 100 | %
46950 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AO.10HNA10AA101XQ11 |  | 10HNA10AA101XQ11 | A iuduced draft fan inlet control damper control command | AO | 0 | 100 | %
46951 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNC10AN001XQ01 |  | 10HNC10AN001XQ01 | A iuduced draft fan current | AI | 0 | 300 | A
46952 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA10CT103 |  | 10HNA10CT103 | A IDF outlet air temperature | RTD | 0 | 200 | ℃
46953 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA10CT101 |  | 10HNA10CT101 | Side-A boiler outlet flue gas temperature | RTD | 0 | 200 | ℃
46954 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA10CT102 |  | 10HNA10CT102 | A iuduced draft fan inlet flue gas temperature | RTD | 0 | 200 | ℃
46955 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT101 |  | 10HNC10CT101 | A IDF bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46956 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT102 |  | 10HNC10CT102 | A IDF bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46957 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT103 |  | 10HNC10CT103 | A IDF motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46958 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT104 |  | 10HNC10CT104 | A IDF motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46959 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT105 |  | 10HNC10CT105 | A IDF motor stator temperature 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46960 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT106 |  | 10HNC10CT106 | A IDF motor stator temperature 2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46961 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT107 |  | 10HNC10CT107 | A IDF motor stator temperature 3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46962 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT108 |  | 10HNC10CT108 | A IDF motor stator temperature 4 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46963 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT109 |  | 10HNC10CT109 | A IDF motor stator temperature 5 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46964 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC10CT110 |  | 10HNC10CT110 | A IDF motor stator temperature 6 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46965 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNA10CP101 |  | 10HNA10CP101 | A iuduced draft fan inlet flue gas pressure | AI | -10 | 0 | kPa
46966 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNA10CP102 |  | 10HNA10CP102 | A IDF outlet air pressure | AI | -1 | 10 | kPa
46967 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNC10CY101 |  | 10HNC10CY101 | A IDF front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46968 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 1 | #1 ID FAN A | K0102-09 | KALTIM1.SIGNAL.AI.10HNC10CY102 |  | 10HNC10CY102 | A IDF rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46969 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNA20AA101XQ12 |  | 10HNA20AA101XQ12 | B iuduced draft fan inlet control damper position feedback | AI | 0 | 100 | %
46970 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AO.10HNA20AA101XQ11 |  | 10HNA20AA101XQ11 | B iuduced draft fan inlet control damper control command | AO | 0 | 100 | %
46971 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA20CT101 |  | 10HNA20CT101 | Side-B boiler outlet flue gas temperature | RTD | 0 | 200 | °C
46972 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNC20AN001XQ01 |  | 10HNC20AN001XQ01 | B iuduced draft fan current | AI | 0 | 300 | A
46973 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA20CT102 |  | 10HNA20CT102 | B iuduced draft fan inlet flue gas temperature | RTD | 0 | 200 | ℃
46974 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNA20CT103 |  | 10HNA20CT103 | B IDF outlet air temperature | RTD | 0 | 200 | ℃
46975 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT101 |  | 10HNC20CT101 | B IDF bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46976 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT102 |  | 10HNC20CT102 | B IDF bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
46977 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT103 |  | 10HNC20CT103 | B IDF motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46978 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT104 |  | 10HNC20CT104 | B IDF motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
46979 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT105 |  | 10HNC20CT105 | B IDF motor stator temperature 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46980 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT106 |  | 10HNC20CT106 | B IDF motor stator temperature 2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46981 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT107 |  | 10HNC20CT107 | B IDF motor stator temperature 3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46982 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT108 |  | 10HNC20CT108 | B IDF motor stator temperature 4 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46983 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT109 |  | 10HNC20CT109 | B IDF motor stator temperature 5 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46984 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.RTD.10HNC20CT110 |  | 10HNC20CT110 | B IDF motor stator temperature 6 | RTD | 0 | 300 | ℃ |  |  |  | 110 | 90 |  |  |  |  | 1 | 1
46985 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNA20CP101 |  | 10HNA20CP101 | B iuduced draft fan inlet flue gas pressure | AI | -10 | 0 | kPa
46986 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNA20CP102 |  | 10HNA20CP102 | B IDF outlet air pressure | AI | -1 | 10 | kPa
46987 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNC20CY101 |  | 10HNC20CY101 | B IDF front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46988 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 2 | #1 ID FAN B | K0102-09 | KALTIM1.SIGNAL.AI.10HNC20CY102 |  | 10HNC20CY102 | B IDF rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
46989 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ106 |  | 10HNA30CQ106 | Chimney flue gas O2 concentration | AI | 0 | 25 | %
46990 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ106 |  | 10HNA30CQ106 | Flue gas 02 unit 1 | AI | 0 | 25 | %
46991 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ107 |  | 10HNA30CQ107 | Flue gas CO2 unit 1 | AI | 0 | 50 | %
46992 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ102 |  | 10HNA30CQ102 | Chimney flue gas humidity | AI | 0 | 100 | %
46993 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ102 |  | 10HNA30CQ102 | Flue Gas Humidiity Unit 1 | AI | 0 | 100 | %
46994 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ108 |  | 10HNA30CQ108 | Flue Gas Opacity Unit 1 | AI | 0 | 30 | %
46995 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CT101 |  | 10HNA30CT101 | Chimney flue gas temperature | AI | 0 | 700 | ℃
46996 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CT101 |  | 10HNA30CT101 | Flue Gas Temperature Unit 1 | AI | 0 | 200 | ℃
46997 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CP101 |  | 10HNA30CP101 | Chimney flue gas pressure | AI | -4 | 4 | kPa
46998 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CP101 |  | 10HNA30CP101 | Flue Gas Pressure Unit 1 | AI | 0 | 200 | KPa
46999 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM1.SIGNAL.AI.10HNA30CF101 |  | 10HNA30CF101 | Chimney flue gas flow | AI | 0 | 40 | m/s
47000 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ109 |  | 10HNA30CQ109 | Flue Gas Velocity Unit 1 | AI | 0 | 100 | m/s
47001 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM1.SIGNAL.AI.10HNA30CQ103XQ01 |  | 10HNA30CQ103XQ01 | Chimney flue gas SO2 concentration 1 | AI | 0 | 1500 | mg/Nm3
47002 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM1.SIGNAL.AI.10HNA30CQ103XQ02 |  | 10HNA30CQ103XQ02 | Chimney flue gas SO2 concentration 2 | AI | 0 | 500 | mg/Nm3
47003 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ104 |  | 10HNA30CQ104 | Chimney flue gas NOx concentration | AI | 0 | 500 | mg/Nm3
47004 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ105 |  | 10HNA30CQ105 | Chimney flue gas CO concentration | AI | 0 | 500 | mg/Nm3
47005 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ101 |  | 10HNA30CQ101 | Chimney flue gas dust concentration | AI | 0 | 500 | mg/Nm3
47006 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ104 |  | 10HNA30CQ104 | Flue gas NOX unit 1 | AI | 0 | 2000 | mg/m3
47007 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ105 |  | 10HNA30CQ105 | Flue gas CO unit 1 | AI | 0 | 500 | mg/m3
47008 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ103 |  | 10HNA30CQ103 | Flue gas SO2 unit 1 | AI | 0 | 1500 | mg/m3
47009 | 1 | UJKTT #1 | 5 | #1 FLUE GAS SYSTEM | 3 | #1 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.10HNA30CQ101 |  | 10HNA30CQ101 | Flue gas dust unit 1 | AI | 0 | 500
47010 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA70AA101XQ12 |  | 10LCA70AA101XQ12 | COND RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
47011 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AO.10LCA70AA101XQ11 |  | 10LCA70AA101XQ11 | COND RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
47012 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCB30AP001XQ01 |  | 10LCB30AP001XQ01 | A CONDENSATE PMP CURRENT | AI | 0 | 75 | A
47013 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA50CT101 |  | 10LCA50CT101 | TEMP OF CONDENSATE PMP OUTLET MAIN PIP | RTD | 0 | 200 | ℃
47014 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT101 |  | 10LCB30CT101 | A CONDENSATE PMP THRUST BEARING TEMP | RTD | 0 | 100 | ℃ | [10 empty] | 1
47015 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT102 |  | 10LCB30CT102 | A CONDENSATE PMP MTR BEARING TEMP 1 | RTD | 0 | 120 | ℃ |  |  |  | 85 | 90 |  |  |  |  | 1 | 1
47016 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT103 |  | 10LCB30CT103 | A CONDENSATE PMP MTR BEARING TEMP 2 | RTD | 0 | 120 | ℃ |  |  |  | 85 | 90 |  |  |  |  | 1 | 1
47017 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT104 |  | 10LCB30CT104 | A CONDENSATE PMP MTR STATOR TEMP 1 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47018 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT105 |  | 10LCB30CT105 | A CONDENSATE PMP MTR STATOR TEMP 2 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47019 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT106 |  | 10LCB30CT106 | A CONDENSATE PMP MTR STATOR TEMP 3 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47020 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT107 |  | 10LCB30CT107 | A CONDENSATE PMP MTR STATOR TEMP 4 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47021 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT108 |  | 10LCB30CT108 | A CONDENSATE PMP MTR STATOR TEMP 5 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47022 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB30CT109 |  | 10LCB30CT109 | A CONDENSATE PMP MTR STATOR TEMP 6 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
47023 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA30CP101 |  | 10LCA30CP101 | DIFF P OF A CONDENSATE PMP INLET FLTR | AI | 0 | 100 | kPa
47024 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCB30CY101 |  | 10LCB30CY101 | A CONDENSATE PMP BEARING VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
47025 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCB30CY102 |  | 10LCB30CY102 | A CONDENSATE PMP BEARING VIBRATION Y | AI | 0 | 20 | mm/s | [10 empty] | 1
47026 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA30CP102 |  | 10LCA30CP102 | A CONDENSATE PMP OUTLET P | AI | 0 | 2.5 | MPa
47027 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LAW10CP101 |  | 10LAW10CP101 | CONDENSATE PMP SEAL WTR P | AI | 0 | 1.2 | MPa |  |  | 0.25 | [6 empty] | 2
47028 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA50CP101 |  | 10LCA50CP101 | P OF CONDENSATE PMP OUTLET MAIN PIP | AI | 0 | 2.5 | MPa |  |  | 1.2 | [6 empty] | 2
47029 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.10GUC10CQ101 |  | 10GUC10CQ101 | Unit 1 Condensate pump outport O2 | AI | 0 | 1000
47030 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.10GUC10CQ102 |  | 10GUC10CQ102 | Unit 1 Condensate pump outport CC | AI | 0 | 20
49057 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA50CP101 |  | 10LCA50CP101 | P OF CONDENSATE PMP OUTLET MAIN PIP | AI | 0 | 2.5 | MPa
49058 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA50CT101 |  | 10LCA50CT101 | TEMP OF CONDENSATE PMP OUTLET MAIN PIP | RTD | 0 | 200 | ℃
49059 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AO.10LCA70AA101XQ11 |  | 10LCA70AA101XQ11 | COND RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
49060 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LCA70AA101XQ12 |  | 10LCA70AA101XQ12 | COND RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
49061 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.10GUC10CQ101 |  | 10GUC10CQ101 | Unit 1 Condensate pump outport O2 | AI | 0 | 1000
49062 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.10GUC10CQ102 |  | 10GUC10CQ102 | Unit 1 Condensate pump outport CC | AI | 0 | 20
49063 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 1 | #1 CONDENSATE PUMP A | K0102-20 | KALTIM1.SIGNAL.AI.10LAW10CP101 |  | 10LAW10CP101 | CONDENSATE PMP SEAL WTR P | AI | 0 | 1.2 | MPa
47031 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.AI.10LCB40AP001XQ01 |  | 10LCB40AP001XQ01 | B CONDENSATE PMP CURRENT | AI | 0 | 75 | A
47032 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT101 |  | 10LCB40CT101 | B CONDENSATE PMP THRUST BEARING TEMP | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
47033 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT102 |  | 10LCB40CT102 | B CONDENSATE PMP MTR BEARING TEMP 1 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47034 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT103 |  | 10LCB40CT103 | B CONDENSATE PMP MTR BEARING TEMP 2 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47035 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT104 |  | 10LCB40CT104 | B CONDENSATE PMP MTR STATOR TEMP 1 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47036 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT105 |  | 10LCB40CT105 | B CONDENSATE PMP MTR STATOR TEMP 2 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47037 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT106 |  | 10LCB40CT106 | B CONDENSATE PMP MTR STATOR TEMP 3 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47038 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT107 |  | 10LCB40CT107 | B CONDENSATE PMP MTR STATOR TEMP 4 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47039 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT108 |  | 10LCB40CT108 | B CONDENSATE PMP MTR STATOR TEMP 5 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47040 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.RTD.10LCB40CT109 |  | 10LCB40CT109 | B CONDENSATE PMP MTR STATOR TEMP 6 | RTD | 0 | 120 | ℃ | [10 empty] | 1
47041 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.AI.10LCA40CP101 |  | 10LCA40CP101 | DIFF P OF B CONDENSATE PMP INLET FLTR | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
47042 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.AI.10LCB40CY101 |  | 10LCB40CY101 | B CONDENSATE PMP BEARING VIBRATION X | AI | 0 | 20 | mm/s | [10 empty] | 1
47043 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.AI.10LCB40CY102 |  | 10LCB40CY102 | B CONDENSATE PMP BEARING VIBRATION Y | AI | 0 | 20 | mm/s | [10 empty] | 1
47044 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM1.SIGNAL.AI.10LCA40CP102 |  | 10LCA40CP102 | B CONDENSATE PMP OUTLET P | AI | 0 | 2.5 | MPa
47704 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10AA101XQ12 |  | 20HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
47705 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AO.20HJF10AA101XQ11 |  | 20HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
47709 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10CP101 |  | 20HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa |  |  |  | 50 | [5 empty] | 1
47710 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJS01CP101 |  | 20HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa |  |  | 0.4 | [6 empty] | 2 | 1
47711 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJF10CP102 |  | 20HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
47712 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJL10CP101 |  | 20HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48944 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AO.20HJF10AA101XQ11 |  | 20HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48945 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10AA101XQ12 |  | 20HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48946 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10CP101 |  | 20HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48947 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJF10CP102 |  | 20HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48948 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJL10CP101 |  | 20HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48949 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJS01CP101 |  | 20HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa
48955 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AO.20HJF10AA101XQ11 |  | 20HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48956 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10AA101XQ12 |  | 20HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48957 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10CP101 |  | 20HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48958 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJF10CP102 |  | 20HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48959 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJL10CP101 |  | 20HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48960 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJS01CP101 |  | 20HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa
48966 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AO.20HJF10AA101XQ11 |  | 20HJF10AA101XQ11 | Upper bed return igniting oil control valve control command | AO | 0 | 100 | %
48967 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10AA101XQ12 |  | 20HJF10AA101XQ12 | Upper bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48968 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJF10CP101 |  | 20HJF10CP101 | Upper bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
48969 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJF10CP102 |  | 20HJF10CP102 | Upper bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48970 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B |  | KALTIM2.SIGNAL.AI.20HJL10CP101 |  | 20HJL10CP101 | Upper bed oil gun flame detecting cooling air main pipe pressure | AI | 0 | 0.1 | MPa
48971 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 2 | #1 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20HJS01CP101 |  | 20HJS01CP101 | Purging steam pressure | AI | 0 | 2.5 | MPa
47045 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 3 | #1 GLAND STEAM CONDENSER | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA51CT101 |  | 10LCA51CT101 | CONDENSATE WTR TEMP OF GLD STM COND INLET | RTD | 0 | 300 | ℃
47046 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 3 | #1 GLAND STEAM CONDENSER | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA51CT102 |  | 10LCA51CT102 | CONDENSATE WTR TEMP OF GLD STM COND OUTLET | RTD | 0 | 300 | ℃
47047 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 3 | #1 GLAND STEAM CONDENSER | K0102-31 | KALTIM1.SIGNAL.TC.10MAW10CT101 |  | 10MAW10CT101 | STM TEMP OF GLD STM COND INLET | TC | 0 | 800 | ℃
47048 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 3 | #1 GLAND STEAM CONDENSER | K0102-31 | KALTIM1.SIGNAL.AI.10MAW10CP101 |  | 10MAW10CP101 | STM P OF GLD STM COND INLET | AI | -100 | 0 | kPa
47049 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 3 | #1 GLAND STEAM CONDENSER | K0102-21 | KALTIM1.SIGNAL.AI.10MAW10CL101 |  | 10MAW10CL101 | GLD STM COND LEVEL | AI | 0 | 300 | mm |  |  |  | 250 | [5 empty] | 1 | 1
47050 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ70AA102XQ12 |  | 10LCJ70AA102XQ12 | 7 LP HTR EMG DRN CTRL VLV 2 PSN | AI | 0 | 100 | %
47051 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ70AA101XQ12 |  | 10LCJ70AA101XQ12 | 7 LP HTR EMG DRN CTRL VLV 1 PSN | AI | 0 | 100 | %
47052 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ70AA101XQ11 |  | 10LCJ70AA101XQ11 | 7 LP HTR EMG DRN CTRL VLV 1 ADJ CMD | AO | 0 | 100 | %
47053 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ70AA102XQ11 |  | 10LCJ70AA102XQ11 | 7 LP HTR EMG DRN CTRL VLV 2 ADJ CMD | AO | 0 | 100 | %
47054 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA53CT101 |  | 10LCA53CT101 | TEMP OF NO.7 LP HTR WTR INLET | RTD | 0 | 300 | ℃
47055 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA53CT102 |  | 10LCA53CT102 | TEMP OF NO.7 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
47056 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCJ70CT101 |  | 10LCJ70CT101 | NO.7 LP heater emergency drainage temperature | RTD | 0 | 300 | ℃
47057 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT101 |  | 10LBS70CT101 | B SIDE UP WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47058 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT102 |  | 10LBS70CT102 | B SIDE BTM WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47059 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT103 |  | 10LBS70CT103 | B SIDE TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47060 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT104 |  | 10LBS70CT104 | A SIDE UP WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47061 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT105 |  | 10LBS70CT105 | A SIDE BTM WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47062 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS70CT106 |  | 10LBS70CT106 | A SIDE TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
47063 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM1.SIGNAL.AI.10LCC70CL102 |  | 10LCC70CL102 | NO.7 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
47064 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.AI.10LBS70CP101 |  | 10LBS70CP101 | B SIDE P OF 7TH EXTR STM PIP | AI | -0.1 | 0.06 | MPa
47065 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 4 | #1 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM1.SIGNAL.AI.10LBS70CP102 |  | 10LBS70CP102 | A SIDE P OF 7TH EXTR STM PIP | AI | -0.1 | 0.06 | MPa
47066 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ60AA101XQ12 |  | 10LCJ60AA101XQ12 | PNEUMATIC CTRL VLV OF LP DRAIN PMP OUTLET PSN | AI | 0 | 100 | %
47067 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ60AA102XQ12 |  | 10LCJ60AA102XQ12 | 6 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
47068 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ60AA101XQ11 |  | 10LCJ60AA101XQ11 | PNEUMATIC CTRL VLV OF LP DRAIN PMP OUTLET ADJ CMD | AO | 0 | 100 | %
47069 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ60AA102XQ11 |  | 10LCJ60AA102XQ11 | 6 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
47070 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ60AP001XQ01 |  | 10LCJ60AP001XQ01 | LP drain pump current | AI | 0 | 150 | A
47071 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA54CT101 |  | 10LCA54CT101 | TEMP OF NO.6 LP HTR WTR INLET | RTD | 0 | 300 | ℃
47072 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA54CT102 |  | 10LCA54CT102 | TEMP OF NO.6 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
47073 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCJ60CT101 |  | 10LCJ60CT101 | NO.6 LP heater emergency drainage temperature | RTD | 0 | 300 | ℃
47074 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS60CT101 |  | 10LBS60CT101 | UP WALL TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
47075 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS60CT102 |  | 10LBS60CT102 | BTM WALL TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
47076 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS60CT103 |  | 10LBS60CT103 | TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
47077 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM1.SIGNAL.AI.10LCC60CL102 |  | 10LCC60CL102 | NO.6 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
47078 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 5 | #1 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM1.SIGNAL.AI.10LBS60CP101 |  | 10LBS60CP101 | P OF 6TH EXTR STM PIP | AI | -0.1 | 0.2 | MPa
47079 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ50AA101XQ12 |  | 10LCJ50AA101XQ12 | 5 LP HTR NORMAL DRN CTRL VLV PSN | AI | 0 | 100 | %
47080 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ50AA102XQ12 |  | 10LCJ50AA102XQ12 | 5 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
47081 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ50AA101XQ11 |  | 10LCJ50AA101XQ11 | 5 LP HTR NORMAL DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
47082 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ50AA102XQ11 |  | 10LCJ50AA102XQ11 | 5 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
47083 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA55CT101 |  | 10LCA55CT101 | TEMP OF NO.5 LP HTR WTR INLET | RTD | 0 | 300 | ℃
47084 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA55CT102 |  | 10LCA55CT102 | TEMP OF NO.5 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
47085 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCJ50CT101 |  | 10LCJ50CT101 | NO.5 LP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
47086 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS50CT101 |  | 10LBS50CT101 | UP WALL TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
47087 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS50CT102 |  | 10LBS50CT102 | BTM WALL TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
47088 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS50CT103 |  | 10LBS50CT103 | TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
47089 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM1.SIGNAL.AI.10LCC50CL102 |  | 10LCC50CL102 | NO.5 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
47090 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 6 | #1 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM1.SIGNAL.AI.10LBS50CP101 |  | 10LBS50CP101 | P OF 5TH EXTR STM PIP | AI | -0.1 | 0.3 | MPa
47091 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ40AA101XQ12 |  | 10LCJ40AA101XQ12 | 4 LP HTR NORMAL DRN CTRL VLV PSN | AI | 0 | 100 | %
47092 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.AI.10LCJ40AA102XQ12 |  | 10LCJ40AA102XQ12 | 4 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
47093 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ40AA101XQ11 |  | 10LCJ40AA101XQ11 | 4 LP HTR NORMAL DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
47094 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.AO.10LCJ40AA102XQ11 |  | 10LCJ40AA102XQ11 | 4 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
47095 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA56CT101 |  | 10LCA56CT101 | TEMP OF NO.4 LP HTR WTR INLET | RTD | 0 | 300 | ℃
47096 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-20 | KALTIM1.SIGNAL.RTD.10LCA56CT102 |  | 10LCA56CT102 | TEMP OF NO.4 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
47097 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.RTD.10LCJ40CT101 |  | 10LCJ40CT101 | NO.4 LP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
47098 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS40CT101 |  | 10LBS40CT101 | UP WALL TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
47099 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS40CT102 |  | 10LBS40CT102 | BTM WALL TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
47100 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM1.SIGNAL.TC.10LBS40CT103 |  | 10LBS40CT103 | TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
47101 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM1.SIGNAL.AI.10LCC40CL102 |  | 10LCC40CL102 | NO.4 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
47102 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 7 | #1 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM1.SIGNAL.AI.10LBS40CP101 |  | 10LBS40CP101 | P OF 4TH EXTR STM PIP | AI | 0 | 0.8 | MPa
47103 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-23 | KALTIM1.SIGNAL.AI.10LBG26AA101XQ12 |  | 10LBG26AA101XQ12 | CTRL VLV ON THE PIP FROM AUX STM TO DEAE PSN | AI | 0 | 100 | %
47104 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.AI.10LBS30AA101XQ12 |  | 10LBS30AA101XQ12 | CTRL VLV OF 3RD EXTR STM TO DEAE POSITION | AI | 0 | 100 | %
47105 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-20 | KALTIM1.SIGNAL.AI.10LCA50AA101XQ12 |  | 10LCA50AA101XQ12 | DEAE LEVEL CTRL VLV POSITION | AI | 0 | 100 | %
47106 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-23 | KALTIM1.SIGNAL.AO.10LBG26AA101XQ11 |  | 10LBG26AA101XQ11 | CTRL VLV ON THE PIP FROM AUX STM TO DEAE ADJ CMD | AO | 0 | 100 | %
47107 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.AO.10LBS30AA101XQ11 |  | 10LBS30AA101XQ11 | Control valve of 3rd extraction steam to deaerator adjust comman | AO | 0 | 100 | %
47108 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-20 | KALTIM1.SIGNAL.AO.10LCA50AA101XQ11 |  | 10LCA50AA101XQ11 | DEAE LEVEL CTRL VLV ADJ CMD | AO | 0 | 100 | %
47109 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.RTD.10LAA01CT101 |  | 10LAA01CT101 | TEMP OF DEAE WTR TANK | RTD | 0 | 200 | ℃
47110 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-23 | KALTIM1.SIGNAL.TC.10LBG26CT101 |  | 10LBG26CT101 | TEMP OF THE STM FROM AUX STM TO DEAE | TC | 0 | 800 | ℃
47111 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.TC.10LBS30CT101 |  | 10LBS30CT101 | UP WALL TEMP OF 3RD EXTR STM PIP | TC | 0 | 800 | ℃
47112 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.TC.10LBS30CT102 |  | 10LBS30CT102 | BTM WALL TEMP OF 3 EXTR STM PIP | TC | 0 | 800 | ℃
47113 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.TC.10LBS30CT103 |  | 10LBS30CT103 | TEMP OF 3RD EXTR STM PIP | TC | 0 | 800 | ℃
47114 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-20 | KALTIM1.SIGNAL.AI.10LAA01CL101 |  | 10LAA01CL101 | DEAE WTR TANK LEVEL 1 | AI | 0 | 2400 | mm |  | -1300 | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
47115 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-20 | KALTIM1.SIGNAL.AI.10LAA01CL102 |  | 10LAA01CL102 | DEAE WTR TANK LEVEL 2 | AI | 0 | 2400 | mm |  | -1300 | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
47116 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-20 | KALTIM1.SIGNAL.AI.10LAA01CL103 |  | 10LAA01CL103 | DEAE WTR TANK LEVEL 3 | AI | 0 | 2400 | mm |  | -1300 | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
47117 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.AI.10LAA01CP101 |  | 10LAA01CP101 | P 1 OF DEAE | AI | 0 | 1.2 | MPa
47118 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.AI.10LAA01CP102 |  | 10LAA01CP102 | P 2 OF DEAE | AI | 0 | 1.2 | MPa
47119 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-23 | KALTIM1.SIGNAL.AI.10LBG26CP101 |  | 10LBG26CP101 | P OF THE STM FROM AUX STM TO DEAE | AI | 0 | 1.6 | MPa
47120 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR | K0102-18 | KALTIM1.SIGNAL.AI.10LBS30CP101 |  | 10LBS30CP101 | P OF 3RD EXTR STM PIP | AI | 0 | 1.5 | MPa
47121 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR |  | KALTIM 0.SIGNAL.AI.10GUB10CQ101 |  | 10GUB10CQ101 | Unit 1 Deaerator import O2 | AI | 0 | 1000
47122 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR |  | KALTIM 0.SIGNAL.AI.10GUB10CQ102 |  | 10GUB10CQ102 | Unit 1 Deaerator import PH | AI | 0 | 14
47123 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR |  | KALTIM 0.SIGNAL.AI.10GUB10CQ103 |  | 10GUB10CQ103 | Unit 1 Deaerator import CC | AI | 0 | 20
47124 | 1 | UJKTT #1 | 6 | #1 CONDENSATE WATER SYSTEM | 8 | #1 DEARATOR |  | KALTIM 0.SIGNAL.AI.10GUB20CQ101 |  | 10GUB20CQ101 | Unit 1 Deaerator outport O2 | AI | 0 | 1000
47125 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT101 |  | 10MAA01CT101 | TEMP OF STM AFR MAIN STM VLV | TC | 0 | 800 | ℃
47126 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT102 |  | 10MAA01CT102 | EXTERNAL WALL TEMP BFR MAIN STM VLV | TC | 0 | 800 | ℃
47127 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT103 |  | 10MAA01CT103 | EXTERNAL WALL TEMP OF STM CHEST COVER FLANGE OF MAIN STM VLV | TC | 0 | 800 | ℃
47128 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT104 |  | 10MAA01CT104 | MAIN STM VLV BOLT TEMP | TC | 0 | 800 | ℃
47129 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT105 |  | 10MAA01CT105 | EXTERNAL WALL TEMP 1 OF MAIN STM PIP | TC | 0 | 800 | ℃
47130 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT106 |  | 10MAA01CT106 | EXTERNAL WALL TEMP 2 OF MAIN STM PIP | TC | 0 | 800 | ℃
47131 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT107 |  | 10MAA01CT107 | EXTERNAL WALL TEMP 3 OF MAIN STM PIP | TC | 0 | 800 | ℃
47132 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT108 |  | 10MAA01CT108 | EXTERNAL WALL TEMP 4 OF MAIN STM PIP | TC | 0 | 800 | ℃
47133 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP101 |  | 10MAA01CP101 | P OF STM BFR MAIN STM VLV | AI | 0 | 16 | MPa
47134 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 1 | #1 MAIN STEAM VALVE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP102 |  | 10MAA01CP102 | P OF STM AFR MAIN STM VLV | AI | 0 | 16 | MPa
47135 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 2 | #1 GOVERNOR VALVE L1 | K0102-31 | KALTIM1.SIGNAL.AI.10MAW31AA101XQ12 |  | 10MAW31AA101XQ12 | CTRL VLV OF SHAFT SEALING STM POSITION | AI | 0 | 100 | %
47136 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 2 | #1 GOVERNOR VALVE L1 |  | KALTIM1.SIGNAL.AO.10CBA01XQ12 |  | 10CBA01XQ12 | Remote control main steam pressure set value | AO | 0 | 100 | %
47137 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 2 | #1 GOVERNOR VALVE L1 | K0102-31 | KALTIM1.SIGNAL.AO.10MAW31AA101XQ11 |  | 10MAW31AA101XQ11 | CTRL VLV OF SHAFT SEALING STM ADJ CMD | AO | 0 | 100 | %
47138 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 2 | #1 GOVERNOR VALVE L1 | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP103 |  | 10MAA01CP103 | P OF STM AFR NO.1 CTRL VLV | AI | 0 | 16 | MPa
47139 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 3 | #1 GOVERNOR VALVE L2 | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP104 |  | 10MAA01CP104 | P OF STM AFR NO.2 CTRL VLV | AI | 0 | 16 | MPa
47140 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 4 | #1 GOVERNOR VALVE R1 | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP105 |  | 10MAA01CP105 | P OF STM AFR NO.3 CTRL VLV | AI | 0 | 16 | MPa
47141 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 5 | #1 GOVERNOR VALVE R2 | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP106 |  | 10MAA01CP106 | P OF STM AFR NO.4 CTRL VLV | AI | 0 | 16 | MPa
47142 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA11CT151 |  | 10MAA11CT151 | TEMP OF THE NO.1 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1
47143 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA51CT153 |  | 10MAA51CT153 | Temperature of the NO.1 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47144 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD11CY101 |  | 10MAD11CY101 | SHAFT VIBRATION OF NO.1 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
47145 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD11CY102 |  | 10MAD11CY102 | SHAFT VIBRATION OF NO.1 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
47146 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD11CY103 |  | 10MAD11CY103 | Vibration of NO.1 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
47147 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 6 | #1 TURBINE BEARING NO. 1 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD11CY104 |  | 10MAD11CY104 | Vibration of NO.1 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
47148 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT119 |  | 10MAA01CT119 | EXTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
47149 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT109 |  | 10MAA01CT109 | EXTERNAL WALL TEMP OF TOP HALF OF HP CYLINDER REAR | TC | 0 | 800 | ℃
47150 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT110 |  | 10MAA01CT110 | TEMP OF STM BFR GOVERNING STAGE | TC | 0 | 800 | ℃
47151 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT111 |  | 10MAA01CT111 | EXTERNAL WALL TEMP OF TOP HALF OF STM CYLINDER | TC | 0 | 800 | ℃
47152 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT113 |  | 10MAA01CT113 | EXTERNAL WALL TEMP OF BTM HALF OF STM CYLINDER | TC | 0 | 800 | ℃
47153 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT115 |  | 10MAA01CT115 | EXTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
47154 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT116 |  | 10MAA01CT116 | INTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
47155 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT117 |  | 10MAA01CT117 | EXTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
47156 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT118 |  | 10MAA01CT118 | INTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
47157 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT120 |  | 10MAA01CT120 | INTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
47158 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT121 |  | 10MAA01CT121 | EXTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
47159 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT122 |  | 10MAA01CT122 | INTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
47160 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT123 |  | 10MAA01CT123 | TEMP OF STM AFR NO.5 STAGE | TC | 0 | 800 | ℃
47161 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT124 |  | 10MAA01CT124 | TEMP OF STM AFR NO.8 STAGE | TC | 0 | 800 | ℃
47162 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT125 |  | 10MAA01CT125 | TEMP OF STM AFR NO.11 STAGE | TC | 0 | 800 | ℃
47163 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT126 |  | 10MAA01CT126 | TEMP OF STM AFR NO.14 STAGE | TC | 0 | 800 | ℃
47164 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT127 |  | 10MAA01CT127 | TEMP OF STM AFR NO.16 STAGE | TC | 0 | 800 | ℃
47165 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT128 |  | 10MAA01CT128 | TEMP OF CYLINDER LEFT SIDE BOLT AFR GOVERNING STAGE | TC | 0 | 800 | ℃
47166 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAA01CT129 |  | 10MAA01CT129 | TEMP OF CYLINDER RIGHT SIDE BOLT AFR GOVERNING STAGE | TC | 0 | 800 | ℃
47167 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-31 | KALTIM1.SIGNAL.TC.10MAW20CT101 |  | 10MAW20CT101 | TEMP OF THE GATE ROD LEAKAGE STM AND HP CYLINDER SHAFT SEALING S | TC | 0 | 800 | ℃
47168 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP113 |  | 10MAA01CP113 | P OF GLD STM BFR ENTERING HP CYLINDER | AI | -100 | 150 | kPa
47169 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP114 |  | 10MAA01CP114 | P OF GLD STM AFR ENTERING HP CYLINDER | AI | -100 | 150 | kPa
47170 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CY103 |  | 10MAD10CY103 | AXIAL DISPLACEMENT 1 OF TURB | AI | -2 | 2 | mm |  | -1.2 | -1 | 0.8 | 1 |  |  |  |  | 0 | 1
47171 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CY104 |  | 10MAD10CY104 | AXIAL DISPLACEMENT 2 OF TURB | AI | -2 | 2 | mm |  | -1.2 | -1 | 0.8 | 1 |  |  |  |  | 0 | 1
47172 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAD10CY105 |  | 10MAD10CY105 | Thermal expansion 1 of turbine | AI | 0 | 35 | mm
47173 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAD10CY106 |  | 10MAD10CY106 | Thermal expansion 2 of turbine | AI | 0 | 35 | mm
47174 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD21CY104 |  | 10MAD21CY104 | THERMAL EXPANSION OF HP CYLINDER | AI | -4 | 6 | mm |  | -1.8 | -1 | 2.5 | 3 |  |  |  |  | 0 | 1
47175 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP107 |  | 10MAA01CP107 | Pressure of steam after governing stage | AI | 0 | 16 | MPa
47176 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP108 |  | 10MAA01CP108 | P OF STM AFR NO.5 STAGE | AI | 0 | 6 | MPa
47177 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP109 |  | 10MAA01CP109 | P OF STM AFR NO.8 STAGE | AI | 0 | 4 | MPa
47178 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP110 |  | 10MAA01CP110 | P OF STM AFR NO.11 STAGE | AI | 0 | 16 | MPa
47179 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP111 |  | 10MAA01CP111 | P OF STM AFR NO.14 STAGE | AI | 0 | 6 | MPa
47180 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CP112 |  | 10MAA01CP112 | P OF STM AFR NO.16 STAGE | AI | -0.1 | 0.25 | MPa
47181 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-31 | KALTIM1.SIGNAL.AI.10MAW20CP101 |  | 10MAW20CP101 | P OF THE GATE ROD LEAKAGE STM AND HP CYLINDER SHAFT SEALING STM | AI | 0 | 1 | MPa
47182 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CS101 |  | 10MAD10CS101 | TURB SPEED 1 | AI | 0 | 5000 | rpm |  |  |  | 3200 | 3300 |  |  |  |  | 1 | 1
47183 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CS102 |  | 10MAD10CS102 | TURB SPEED 2 | AI | 0 | 5000 | rpm |  |  |  | 3200 | 3300 |  |  |  |  | 1 | 1
47184 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CS103 |  | 10MAD10CS103 | TURB SPEED 3 | AI | 0 | 5000 | rpm |  |  |  | 3200 | 3300 |  |  |  |  | 1 | 1
47185 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CS104 |  | 10MAD10CS104 | TURB ZERO SPEED | AI | 0 | 100 | rpm
47186 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD10CY102 |  | 10MAD10CY102 | ECCENTRICITY RATIO OF TURB | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
48883 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE |  | 10MAD10CS901 |  | 10MAD10CS901 | STEAM TURBINE SPEED OUTPUT | CALC | 0 | 500 | rpm | [8 empty] | AVG((KALTIM1.SIGNAL.AI.10MAD10CS101);(KALTIM1.SIGNAL.AI.10MAD10CS102);(KALTIM1.SIGNAL.AI.10MAD10CS103))
48892 | 1 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE |  | 20MAD10CS901 |  | 20MAD10CS901 | STEAM TURBINE SPEED OUTPUT | CALC | 0 | 500 | rpm | [8 empty] | AVG((KALTIM2.SIGNAL.AI.20MAD10CS101);(KALTIM2.SIGNAL.AI.20MAD10CS102);(KALTIM2.SIGNAL.AI.20MAD10CS103))
49119 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 7 | #1 HP TURBINE | K0102-36 | 10MAA01CT911 |  | 10MAA01CT911 | DELTA EXTERNAL WALL TEMP OF TOP BTM HALF OF STM CYLINDER | CALC | 0 | 800 | C
47187 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT151 |  | 10MAA12CT151 | TEMP 1 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47188 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT152 |  | 10MAA12CT152 | TEMP 2 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47189 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT153 |  | 10MAA12CT153 | TEMP 3 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47190 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT154 |  | 10MAA12CT154 | TEMP 4 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47191 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT155 |  | 10MAA12CT155 | TEMP 5 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47192 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT156 |  | 10MAA12CT156 | TEMP 6 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47193 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT157 |  | 10MAA12CT157 | TEMP 7 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47194 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT158 |  | 10MAA12CT158 | TEMP 8 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47195 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT159 |  | 10MAA12CT159 | TEMP 9 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47196 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAA12CT160 |  | 10MAA12CT160 | TEMP 10 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47197 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC11CT151 |  | 10MAC11CT151 | TEMP 1 OF THE NO.2 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47198 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC11CT152 |  | 10MAC11CT152 | TEMP 2 OF THE NO.2 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47199 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC52CT151 |  | 10MAC52CT151 | Temperature of the NO.2 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47200 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD21CY101 |  | 10MAD21CY101 | SHAFT VIBRATION OF NO.2 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47201 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD21CY102 |  | 10MAD21CY102 | SHAFT VIBRATION OF NO.2 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47202 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD21CY103 |  | 10MAD21CY103 | Vibration of NO.2 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47203 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 8 | #1 TURBINE BEARING NO. 2 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD21CY105 |  | 10MAD21CY105 | Vibration of NO.2 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47204 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC12CT151 |  | 10MAC12CT151 | TEMP 1 OF THE NO.3 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47205 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC12CT152 |  | 10MAC12CT152 | TEMP 2 OF THE NO.3 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47206 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC52CT152 |  | 10MAC52CT152 | Temperature of the NO.3 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47207 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD31CY101 |  | 10MAD31CY101 | SHAFT VIBRATION OF NO.3 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47208 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD31CY102 |  | 10MAD31CY102 | SHAFT VIBRATION OF NO.3 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
47209 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD31CY103 |  | 10MAD31CY103 | Vibration of NO.3 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47210 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 9 | #1 TURBINE BEARING NO. 3 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD31CY104 |  | 10MAD31CY104 | Vibration of NO.3 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47211 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAC01CT101 |  | 10MAC01CT101 | TEMP OF STM AFR NO.17 STAGE | TC | 0 | 800 | ℃
47212 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-36 | KALTIM1.SIGNAL.TC.10MAC01CT102 |  | 10MAC01CT102 | TEMP OF STM AFR NO.19 STAGE | TC | 0 | 800 | ℃
47213 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-20 | KALTIM1.SIGNAL.AI.10LCE11CP101 |  | 10LCE11CP101 | DIFF P OF LP CYLINDER WTR SPR FLTR | AI | 0 | 60 | kPa
47214 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-24 | KALTIM1.SIGNAL.AI.10MAD41CY104 |  | 10MAD41CY104 | THERMAL EXPANSION OF LP CYLINDER | AI | -4 | 6 | mm |  | -2 | -1.5 | 3 | 3.5 |  |  |  |  | 0
47215 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-20 | KALTIM1.SIGNAL.AI.10LCE11CP102 |  | 10LCE11CP102 | P OF LP CYLINDER WTR SPR | AI | 0 | 2.5 | MPa
47216 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAC01CP101 |  | 10MAC01CP101 | P OF STM AFR NO.17 STAGE | AI | -0.1 | 0.15 | MPa
47217 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 10 | #1 LP TURBINE | K0102-36 | KALTIM1.SIGNAL.AI.10MAC01CP102 |  | 10MAC01CP102 | P OF STM AFR NO.19 STAGE | AI | -0.1 | 0.1 | MPa
47218 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC13CT151 |  | 10MAC13CT151 | TEMP 1 OF THE NO.4 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47219 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC13CT152 |  | 10MAC13CT152 | TEMP 2 OF THE NO.4 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47220 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC53CT151 |  | 10MAC53CT151 | Temperature of the NO.4 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47221 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD41CY101 |  | 10MAD41CY101 | SHAFT VIBRATION OF NO.4 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47222 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD41CY102 |  | 10MAD41CY102 | SHAFT VIBRATION OF NO.4 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47223 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD41CY103 |  | 10MAD41CY103 | Vibration of NO.4 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47224 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 11 | #1 TURBINE BEARING NO. 4 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD41CY105 |  | 10MAD41CY105 | Vibration of NO.4 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47225 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB30AA001XQ12 |  | 10PAB30AA001XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR INLET POSITION | AI | 0 | 100 | %
47226 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB31AA001XQ12 |  | 10PAB31AA001XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR INLET POSITION | AI | 0 | 100 | %
47227 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB40AA001XQ12 |  | 10PAB40AA001XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET POSITION | AI | 0 | 100 | %
47228 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB41AA001XQ12 |  | 10PAB41AA001XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR OUTLET POSITION | AI | 0 | 100 | %
47229 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB30AA101XQ12 |  | 10PAB30AA101XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR INLET FEEDBACK | AI | 0 | 100 | %
47230 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB30AA102XQ12 |  | 10PAB30AA102XQ12 | B DEBRIS FLTR BLOWOFF VLV FEEDBACK | AI | 0 | 100 | %
47231 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB31AA101XQ12 |  | 10PAB31AA101XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR INLET FEEDBACK | AI | 0 | 100 | %
47232 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB31AA102XQ12 |  | 10PAB31AA102XQ12 | A debris filter blowoff valve feedback | AI | 0 | 100 | %
47233 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10LCR20AA101XQ12 |  | 10LCR20AA101XQ12 | COND LEVEL REGULATING VLV POSITION | AI | 0 | 100 | %
47234 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB40AA101XQ12 |  | 10PAB40AA101XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET FEEDBACK | AI | 0 | 100 | %
47235 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB41AA101XQ12 |  | 10PAB41AA101XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR OUTLET FEEDBACK | AI | 0 | 100 | %
47236 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AO.10LCR20AA101XQ11 |  | 10LCR20AA101XQ11 | COND LEVEL REGULATING VLV ADJ CMD | AO | 0 | 100 | %
47237 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB30AA101XQ11 |  | 10PAB30AA101XQ11 | MTR VLV OF COND B SIDE CIRCLE WTR INLET COMMAND | AO | 0 | 100 | %
47238 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB30AA102XQ11 |  | 10PAB30AA102XQ11 | B DEBRIS FLTR BLOWOFF VLV OPN CMD | AO | 0 | 100 | %
47239 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB31AA101XQ11 |  | 10PAB31AA101XQ11 | MTR VLV OF COND A SIDE CIRCLE WTR INLET COMMAND | AO | 0 | 100 | %
47240 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB31AA102XQ11 |  | 10PAB31AA102XQ11 | A debris filter blowoff valve command | AO | 0 | 100 | %
47241 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB40AA101XQ11 |  | 10PAB40AA101XQ11 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET COMMAND | AO | 0 | 100 | %
47242 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AO.10PAB41AA101XQ11 |  | 10PAB41AA101XQ11 | MTR VLV OF COND A SIDE CIRCLE WTR OUTLET COMMAND | AO | 0 | 100 | %
47243 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAJ30BN001XQ01 |  | 10MAJ30BN001XQ01 | A WTR-RING VACUM PMP CURRENT | AI | 0 | 150 | A
47244 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAJ31BN001XQ01 |  | 10MAJ31BN001XQ01 | B WTR-RING VACUM PMP CURRENT | AI | 0 | 150 | A
47245 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.RTD.10MAG10CT101 |  | 10MAG10CT101 | COND TEMP 1 | RTD | 0 | 300 | ℃
47246 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.RTD.10MAG10CT102 |  | 10MAG10CT102 | COND TEMP 2 | RTD | 0 | 300 | ℃
47247 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.RTD.10PAB30CT101 |  | 10PAB30CT101 | TEMP OF COND B SIDE CIRCLE WTR INLET | RTD | 0 | 300 | ℃
47248 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.RTD.10PAB31CT101 |  | 10PAB31CT101 | TEMP OF COND A SIDE CIRCLE WTR INLET | RTD | 0 | 300 | ℃
47249 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.RTD.10PAB40CT101 |  | 10PAB40CT101 | TEMP OF COND B SIDE CIRCLE WTR OUTLET | RTD | 0 | 300 | ℃
47250 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.RTD.10PAB41CT101 |  | 10PAB41CT101 | TEMP OF COND A SIDE CIRCLE WTR OUTLET | RTD | 0 | 300 | ℃
47251 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-32 | KALTIM1.SIGNAL.TC.10LCN10CT101 |  | 10LCN10CT101 | A DRAINS HEADER TEMP | TC | 0 | 300 | ℃
47252 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-32 | KALTIM1.SIGNAL.TC.10LCN10CT102 |  | 10LCN10CT102 | B DRAINS HEADER TEMP | TC | 0 | 800 | ℃
47253 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-32 | KALTIM1.SIGNAL.TC.10LCN20CT101 |  | 10LCN20CT101 | C DRAINS HEADER TEMP | TC | 0 | 800 | ℃
47254 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-32 | KALTIM1.SIGNAL.TC.10LCN20CT102 |  | 10LCN20CT102 | D DRAINS HEADER TEMP | TC | 0 | 800 | ℃
47255 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAJ30CP101 |  | 10MAJ30CP101 | DIFF P OF A WTR-RING VACUM PMP INLET PNEUMATIC VLV INLET AND OUT | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
47256 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAJ31CP101 |  | 10MAJ31CP101 | DIFF P OF B WTR-RING VACUM PMP INLET PNEUMATIC VLV INLET AND OUT | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
47257 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB30CP101 |  | 10PAB30CP101 | DIFF P BETWEEN B TWICE FLTR INLET AND OUTLET | AI | 0 | 200 | kPa |  |  |  | 30 | [5 empty] | 1
47258 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAG10CP101 |  | 10MAG10CP101 | COND P 1 | AI | -100 | 150 | kPa
47259 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAG10CP102 |  | 10MAG10CP102 | COND P 2 | AI | -100 | 150 | kPa
47260 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB30CP102 |  | 10PAB30CP102 | P OF COND B SIDE CIRCLE WTR INLET | AI | 0 | 400 | KPa
47261 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB31CP101 |  | 10PAB31CP101 | DIFF P BETWEEN A TWICE FLTR INLET AND OUTLET | AI | 0 | 200 | kPa |  |  |  | 30 | [5 empty] | 1
47262 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB31CP102 |  | 10PAB31CP102 | P OF COND A SIDE CIRCLE WTR INLET | AI | 0 | 400 | KPa |  |  | 0.03 | [6 empty] | 2
47263 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB40CP101 |  | 10PAB40CP101 | P OF COND B SIDE CIRCLE WTR OUTLET | AI | 0 | 400 | KPa
47264 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-35 | KALTIM1.SIGNAL.AI.10PAB41CP101 |  | 10PAB41CP101 | P OF COND A SIDE CIRCLE WTR OUTLET | AI | 0 | 400 | KPa
47265 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAG10CP101A |  | 10MAG10CP101A | Vacuum Pressure | AI | -100 | 0 | KPa
47266 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-22 | KALTIM1.SIGNAL.AI.10MAG10CP102A |  | 10MAG10CP102A | Vacuum Pressure 2 | AI | -100 | 0 | KPa
47267 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL101 |  | 10MAG10CL101 | Condenser hot well level 1 | AI | 0 | 1200 | mm | [10 empty] | 1
47268 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL102 |  | 10MAG10CL102 | Condenser hot well level 2 | AI | 0 | 1500 | mm |  | 400 | 600 | 1000 | 1200 |  |  |  |  | 0 | 1
47269 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL103 |  | 10MAG10CL103 | Condenser hot well level 3 | AI | 0 | 1200 | mm | [10 empty] | 1
47270 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL104 |  | 10MAG10CL104 | Condenser hot well level 4 | AI | 0 | 1500 | mm | [10 empty] | 1
47271 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL105 |  | 10MAG10CL105 | COND BACK WTR CHAMBER LEVEL 1 | AI | 0 | 1500 | mm
47272 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-20 | KALTIM1.SIGNAL.AI.10MAG10CL106 |  | 10MAG10CL106 | COND BACK WTR CHAMBER LEVEL 2 | AI | 0 | 1500 | mm
47273 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR | K0102-32 | KALTIM1.SIGNAL.AI.10LCN20CP101 |  | 10LCN20CP101 | B PROPER FLASH DRAIN TANK P | AI | 0 | 1.2 | MPa
48885 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR |  | 10PAB31CP902 |  | 10PAB31CP902 | Condenser Cooling Water Differential Pressure Side A | CALC | 0 | 400 | KPa | [8 empty] | (KALTIM1.SIGNAL.AI.10PAB31CP102)-(KALTIM1.SIGNAL.AI.10PAB41CP101)
48891 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR |  | 10PAB30CP902 |  | 10PAB30CP902 | Condenser Cooling Water Differential Pressure Side B | CALC | 0 | 400 | KPa | [8 empty] | (KALTIM1.SIGNAL.AI.10PAB30CP102)-(KALTIM1.SIGNAL.AI.10PAB40CP101)
48894 | 1 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR |  | 20PAB31CP902 |  | 20PAB31CP902 | Condenser Cooling Water Differential Pressure | CALC | 0 | 400 | KPa | [8 empty] | (KALTIM2.SIGNAL.AI.20PAB31CP102)-(KALTIM2.SIGNAL.AI.20PAB41CP101)
48900 | 1 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR |  | 20PAB30CP902 |  | 20PAB30CP902 | Condenser Cooling Water Differential Pressure Side B | CALC | 0 | 400 | KPa | [8 empty] | (KALTIM2.SIGNAL.AI.20PAB30CP102)-(KALTIM2.SIGNAL.AI.20PAB40CP101)
49121 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 12 | #1 CONDENSOR |  | 10MAG10CP901 |  | 10MAG10CP901 | Condenser Vacuum | CALC | -100 | 150 | kPa | [8 empty] | AVG((KALTIM1.SIGNAL.AI.10MAG10CP101);(KALTIM1.SIGNAL.AI.10MAG10CP102)
47275 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.AI.10MAW35AA101XQ12 |  | 10MAW35AA101XQ12 | Main steam to aux steam pressure relief valve position feedback | AI | 0 | 100 | %
47276 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.AO.10MAW35AA101XQ11 |  | 10MAW35AA101XQ11 | Main steam to aux steam pressure relief valve cmd | AO | 0 | 100 | %
47277 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-23 | KALTIM1.SIGNAL.TC.10LBG23CT101 |  | 10LBG23CT101 | TEMP OF THE STM FROM AUX STM TO GLD STM SYSTEM | TC | 0 | 800 | ℃
47278 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.TC.10MAW31CT101 |  | 10MAW31CT101 | TEMP OF SHAFT SEALING STM MAIN PIP | TC | 0 | 800 | ℃
47279 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.TC.10MAW33CT101 |  | 10MAW33CT101 | STM TEMP OF STM MIXER | TC | 0 | 800 | ℃
47280 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.AI.10MAW31CP101 |  | 10MAW31CP101 | P OF SHAFT SEALING STM MAIN PIP | AI | 0 | 250 | kPa
47281 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-23 | KALTIM1.SIGNAL.AI.10LBG23CP101 |  | 10LBG23CP101 | P OF THE STM FROM AUX STM TO GLD STM SYSTEM | AI | 0 | 1.6 | MPa
47282 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 13 | #1 STEAM SEAL SYSTEM | K0102-31 | KALTIM1.SIGNAL.AI.10MAW33CP101 |  | 10MAW33CP101 | STM P OF STM MIXER | AI | 0 | 0.4 | MPa
47283 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AI.10MAN10AA101XQ12 |  | 10MAN10AA101XQ12 | Turbine bypass temperature and pressure reduction valve position | AI | 0 | 100 | %
47284 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM1.SIGNAL.AI.10LCE18AA101XQ12 |  | 10LCE18AA101XQ12 | COND SECONDARY DTR WTR SPR CTRL VLV 1 POSITION | AI | 0 | 100 | %
47285 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM1.SIGNAL.AI.10LCE18AA102XQ12 |  | 10LCE18AA102XQ12 | COND SECONDARY DTR WTR SPR CTRL VLV 2 POSITION | AI | 0 | 100 | %
47286 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AI.10LCE19AA101XQ12 |  | 10LCE19AA101XQ12 | Turbine bypass water spray control valve position | AI | 0 | 100 | %
47287 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM1.SIGNAL.AO.10LCE18AA101XQ11 |  | 10LCE18AA101XQ11 | COND SECONDARY DTR WTR SPR CTRL VLV 1 ADJ CMD | AO | 0 | 100 | %
47288 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM1.SIGNAL.AO.10LCE18AA102XQ11 |  | 10LCE18AA102XQ11 | COND SECONDARY DTR WTR SPR CTRL VLV 2 ADJ CMD | AO | 0 | 100 | %
47289 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AO.10LCE19AA101XQ11 |  | 10LCE19AA101XQ11 | Turbine bypass water spray control valve adjust command | AO | 0 | 100 | %
47290 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AO.10MAN10AA101XQ11 |  | 10MAN10AA101XQ11 | Turbine bypass temperature and pressure reduction valve adjust c | AO | 0 | 100 | %
47291 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.RTD.10LCE18CT101 |  | 10LCE18CT101 | SECONDARY DTR OUTLET WTR TEMP 1 | RTD | 0 | 300 | ℃
47292 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.RTD.10LCE18CT102 |  | 10LCE18CT102 | SECONDARY DTR OUTLET WTR TEMP 2 | RTD | 0 | 300 | ℃
47293 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.TC.10MAN10CT101 |  | 10MAN10CT101 | STM TEMP AFR HP BYP VLV | TC | 0 | 800 | ℃
47294 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AI.10LCE19CP101 |  | 10LCE19CP101 | DTR WTR P OF HP BYP VLV | AI | 0 | 3 | MPa
47295 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 14 | #1 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM1.SIGNAL.AI.10MAN10CP101 |  | 10MAN10CP101 | STM P AFR HP BYP VLV | AI | 0 | 1 | MPa
47296 | 1 | UJKTT #1 | 7 | #1 TURBINE SYSTEM | 15 | #1 TURNING GEAR | K0102-36 | KALTIM1.SIGNAL.AI.10MAA01CS101XQ01 |  | 10MAA01CS101XQ01 | Emergency intercepter indicator current output | AI | 0 | 100 | %
47297 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC14CT151 |  | 10MAC14CT151 | TEMP 1 OF THE NO.5 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47298 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC14CT152 |  | 10MAC14CT152 | TEMP 2 OF THE NO.5 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47299 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM1.SIGNAL.RTD.10MAC53CT152 |  | 10MAC53CT152 | Temperature of the NO.5 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47300 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD51CY101 |  | 10MAD51CY101 | SHAFT VIBRATION OF NO.5 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47301 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD51CY102 |  | 10MAD51CY102 | SHAFT VIBRATION OF NO.5 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 156 | 250 |  |  |  |  | 1 | 1
47302 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD51CY103 |  | 10MAD51CY103 | Vibration of NO.5 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47303 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 1 | #1 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD51CY104 |  | 10MAD51CY104 | Vibration of NO.5 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47304 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE018 |  | 10MKA01CE018 | Gen. Active Power | AI | 0 | 100 | %
47305 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE021 |  | 10MKA01CE021 | Gen. Active Power | AI | 0 | 100 | %
47306 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AO.10CBA01XQ11 |  | 10CBA01XQ11 | Remote control load set value | AO | 0 | 100 | %
47307 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE001 |  | 10MKA01CE001 | #1 Gen. Current (A Phase) | AI | 0 | 8000 | A
47308 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE002 |  | 10MKA01CE002 | #1 Gen. Current (B Phase) | AI | 0 | 8000 | A
47309 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE003 |  | 10MKA01CE003 | #1 Gen. Current (C Phase) | AI | 0 | 8000 | A
47310 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE011 |  | 10MKA01CE011 | #1 Gen. Negative Sequence Current | AI | 0 | 100 | A
47311 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE012 |  | 10MKA01CE012 | #1 Gen. Zero Sequence Current | AI | 0 | 50 | A
47312 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKC01CE002 |  | 10MKC01CE002 | #1 Gen. Field Current | AI | 0 | 2500 | A
47313 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT101 |  | 10MKA10CT101 | GEN STATOR WINDING TEMP 1 | RTD | 0 | 300 | ℃
47314 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT102 |  | 10MKA10CT102 | GEN STATOR WINDING TEMP 2 | RTD | 0 | 300 | ℃
47315 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT103 |  | 10MKA10CT103 | GEN STATOR WINDING TEMP 3 | RTD | 0 | 300 | ℃
47316 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT104 |  | 10MKA10CT104 | GEN STATOR WINDING TEMP 4 | RTD | 0 | 300 | ℃
47317 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT105 |  | 10MKA10CT105 | GEN STATOR WINDING TEMP 5 | RTD | 0 | 300 | ℃
47318 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT106 |  | 10MKA10CT106 | GEN STATOR WINDING TEMP 6 | RTD | 0 | 300 | ℃
47319 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT107 |  | 10MKA10CT107 | GEN STATOR CORE TEMP 1 (TURB END) | RTD | 0 | 300 | ℃
47320 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT108 |  | 10MKA10CT108 | GEN STATOR CORE TEMP 2 (TURB END) | RTD | 0 | 300 | ℃
47321 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT109 |  | 10MKA10CT109 | GEN STATOR CORE TEMP 1 (MIDDLE) | RTD | 0 | 300 | ℃
47322 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT110 |  | 10MKA10CT110 | GEN STATOR CORE TEMP 2 (MIDDLE) | RTD | 0 | 300 | ℃
47323 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT111 |  | 10MKA10CT111 | GEN STATOR CORE TEMP 1 (EXCITER END) | RTD | 0 | 300 | ℃
47324 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA10CT112 |  | 10MKA10CT112 | GEN STATOR CORE TEMP 2 (EXCITER END) | RTD | 0 | 300 | ℃
47325 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA20CT101 |  | 10MKA20CT101 | TEMP OF GEN STATOR AIR INLET (TURB END) | RTD | 0 | 300 | ℃
47326 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA20CT102 |  | 10MKA20CT102 | TEMP OF GEN STATOR AIR INLET (EXCITER END) | RTD | 0 | 300 | ℃
47327 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA20CT103 |  | 10MKA20CT103 | TEMP OF GEN STATOR AIR OUTLET (TURB END) | RTD | 0 | 300 | ℃
47328 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR | K0102-36 | KALTIM1.SIGNAL.RTD.10MKA20CT104 |  | 10MKA20CT104 | TEMP OF GEN STATOR AIR OUTLET (EXCITER END) | RTD | 0 | 300 | ℃
47329 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10CBA01XQ03 |  | 10CBA01XQ03 | Frequency correction | AI | 0 | 100 | Hz
47330 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE009 |  | 10MKA01CE009 | #1 Gen. Frequency | AI | 48 | 52 | HZ
47331 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE006 |  | 10MKA01CE006 | #1 Gen. Stator Voltage(A-B) | AI | 0 | 17.94 | KV
47332 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE007 |  | 10MKA01CE007 | #1 Gen. Stator Voltage(B-C) | AI | 0 | 17.94 | KV
47333 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE008 |  | 10MKA01CE008 | #1 Gen. Stator Voltage(A-C) | AI | 0 | 17.94 | KV
47334 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE005 |  | 10MKA01CE005 | #1 Gen. Reactive Power | AI | -132 | 132 | MVAR
47335 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10CBA01XQ01 |  | 10CBA01XQ01 | Load reference | AI | 0 | 100 | MW
47336 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE004 |  | 10MKA01CE004 | #1 Gen. Active Power | AI | 0 | 132 | MW
47337 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE013 |  | 10MKA01CE013 | #1 Gen. Zero Sequence Voltage | AI | 0 | 100 | V
47338 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKC01CE001 |  | 10MKC01CE001 | #1 Gen. Field Voltage | AI | 0 | 350 | V
47339 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10AGC3026 |  | 10AGC3026 | GEN CURRENT B PHASE | AI | 0 | 100
47340 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10AGC3028 |  | 10AGC3028 | GEN VAR SET LOW | AI | 0 | 100
47341 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA01CE010 |  | 10MKA01CE010 | #1 Gen. Power Factor | AI | 0 | 1
47342 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10AGC3027 |  | 10AGC3027 | GEN VAR SET HIGH | AI | 0 | 100
47343 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10AGC3029 |  | 10AGC3029 | GENERATOR POWER FACTOR | AI | 0 | 100
47344 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10AGC5001 |  | 10AGC5001 | AGC DEMAND POWER | AI | 0 | 65535
47345 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA001LIMIT |  | 10MKA001LIMIT | GENERATOR VAR LIMIT HIGH | AI | 0 | 100
47346 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.10MKA002LIMIT |  | 10MKA002LIMIT | GENERATOR VAR LIMIT LOW | AI | -50 | 50
48879 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.AMDMDMW |  | AMDMDMW | LOAD DEMAND | AI | 0 | 150 | MW
48880 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 2 | #1 GENERATOR |  | KALTIM1.SIGNAL.AI.AM12MCS0004 |  | AM12MCS0004 | UNIT LODA CMD SET | AI | 0 | 150 | MW
47347 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-25 | KALTIM1.SIGNAL.RTD.10MKD11CT151 |  | 10MKD11CT151 | TEMP OF THE NO.6 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
47348 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-25 | KALTIM1.SIGNAL.RTD.10MKD12CT151 |  | 10MKD12CT151 | Temperature of the NO.6 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
47349 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD61CY101 |  | 10MAD61CY101 | SHAFT VIBRATION OF NO.6 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47350 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD61CY102 |  | 10MAD61CY102 | SHAFT VIBRATION OF NO.6 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | 250 |  |  |  |  | 1 | 1
47351 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD61CY103 |  | 10MAD61CY103 | Vibration of NO.6 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47352 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 3 | #1 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM1.SIGNAL.AI.10MAD61CY104 |  | 10MAD61CY104 | Vibration of NO.6 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 50 | [5 empty] | 1 | 1
47353 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 4 | #1 GENERATOR AIR COOLER SET | K0102-34 | KALTIM1.SIGNAL.AI.10PGB75AA101XQ12 |  | 10PGB75AA101XQ12 | CTRL VLV OF GEN AIR COOLER COOLING WTR OUTLET PSN | AI | 0 | 100 | %
47354 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 4 | #1 GENERATOR AIR COOLER SET | K0102-34 | KALTIM1.SIGNAL.AO.10PGB75AA101XQ11 |  | 10PGB75AA101XQ11 | CTRL VLV OF GEN AIR COOLER COOLING WTR OUTLET ADJ CMD | AO | 0 | 100 | %
47355 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 4 | #1 GENERATOR AIR COOLER SET | K0102-34 | KALTIM1.SIGNAL.RTD.10PGB75CT101 |  | 10PGB75CT101 | WTR TEMP OF GEN AIR COOLER COOLING WTR OUTLET | RTD | 0 | 300 | ℃
47356 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE001 |  | 10BAT01CE001 | #1 Gen. Tran. HV Side Current (A Phase) | AI | 0 | 800 | A
47357 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE002 |  | 10BAT01CE002 | #1 Gen. Tran. HV Side Current (B Phase) | AI | 0 | 800 | A
47358 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE003 |  | 10BAT01CE003 | #1 Gen. Tran. HV Side Current (C Phase) | AI | 0 | 800 | A
47359 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE011 |  | 10BAT01CE011 | #1 Gen. Tran. Oil Temperature 1 | AI | 0 | 150 | ℃
47360 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE012 |  | 10BAT01CE012 | #1 Gen. Tran. Oil Temperature 2 | AI | 0 | 150 | ℃
47361 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE013 |  | 10BAT01CE013 | #1 Gen. Tran. Winding Temperature | AI | 0 | 150 | ℃
47362 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE009 |  | 10BAT01CE009 | #1 Gen. Tran. HV Side Frequency | AI | 48 | 52 | HZ
47363 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE004 |  | 10BAT01CE004 | #1 Gen. Tran. HV Side Voltage(A-B) | AI | 0 | 195 | KV
47364 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE005 |  | 10BAT01CE005 | #1 Gen. Tran. HV Side Voltage(B-C) | AI | 0 | 195 | KV
47365 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE006 |  | 10BAT01CE006 | #1 Gen. Tran. HV Side Voltage(A-C) | AI | 0 | 195 | KV
47366 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE008 |  | 10BAT01CE008 | #1 Gen. Tran. HV Side Reactive Power | AI | -156 | 156 | MVAR
47367 | 1 | UJKTT #1 | 8 | #1 GENERATOR SYSTEM | 5 | #1 GENERATOR TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BAT01CE007 |  | 10BAT01CE007 | #1 Gen. Tran. HV Side Active Power | AI | -156 | 156 | MW
47368 | 1 | UJKTT #1 | 9 | #1 EXCITATION SYSTEM | 1 | #1 TRANSFORMER EXCITATION |  | KALTIM1.SIGNAL.AI.10MKT01CE001 |  | 10MKT01CE001 | #1 Excit. Tran. HV Side Current (B Phase) | AI | 0 | 100 | A
47369 | 1 | UJKTT #1 | 9 | #1 EXCITATION SYSTEM | 1 | #1 TRANSFORMER EXCITATION |  | KALTIM1.SIGNAL.AI.10MKT01CE003 |  | 10MKT01CE003 | #1 Excit. Tran. HV Side Reactive Power | AI | 0 | 1320 | KVAR
47370 | 1 | UJKTT #1 | 9 | #1 EXCITATION SYSTEM | 1 | #1 TRANSFORMER EXCITATION |  | KALTIM1.SIGNAL.AI.10MKT01CE002 |  | 10MKT01CE002 | #1 Excit. Tran. HV Side Active Power | AI | 0 | 1320 | KW
47371 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 1 | TRASH RACK | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB12LT101 |  | 10PAB12LT101 | Level of water before Trash rack B | AI | -7 | 5.3 | m
47372 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 1 | TRASH RACK | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB11LT101 |  | 10PAB11LT101 | Level of water before Trash rack A | AI | -7 | 5.3 | m
47373 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 2 | TRAVELING SCREEN A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB21LT101 |  | 10PAB21LT101 | Level of water before Traveling screen A | AI | 0 | 12 | m |  | 5 |  |  | 8.4
47374 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 2 | TRAVELING SCREEN A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB21LT102 |  | 10PAB21LT102 | Level of water after Traveling screen A | AI | 0 | 12 | m |  | 5 |  |  | 8.4
47375 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 3 | TRAVELING SCREEN B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB22LT101 |  | 10PAB22LT101 | Level of water before Traveling screen B | AI | 0 | 12 | m |  | 5 |  |  | 8.4
47376 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 3 | TRAVELING SCREEN B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB22LT102 |  | 10PAB22LT102 | Level of water after Traveling screen B | AI | 0 | 12 | m |  | 5 |  |  | 8.4
47377 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41AP001XQ01 |  | 10PAB41AP001XQ01 | #1 Unit Cwp A motor current | AI | 0 | 150 | A
47378 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT114 |  | 10PAB41CT114 | #1 Unit Cwp A motor widing temp. 4 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47379 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT111 |  | 10PAB41CT111 | #1 Unit Cwp A motor widing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47380 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT112 |  | 10PAB41CT112 | #1 Unit Cwp A motor widing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47381 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT113 |  | 10PAB41CT113 | #1 Unit Cwp A motor widing temp. 3 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47382 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT115 |  | 10PAB41CT115 | #1 Unit Cwp A motor widing temp. 5 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47383 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT116 |  | 10PAB41CT116 | #1 Unit Cwp A motor widing temp. 6 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47384 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT117 |  | 10PAB41CT117 | #1 Unit Cwp A thrust bearing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47385 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CT118 |  | 10PAB41CT118 | #1 Unit Cwp A thrust bearing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47386 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CF101 |  | 10PAB41CF101 | #1 Unit cwp A outlet flow | AI | 0 | 4 | m3/h
47387 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CY101X |  | 10PAB41CY101X | #1 Unit Cwp A bearing vibration (x direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47388 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CY101Y |  | 10PAB41CY101Y | #1 Unit Cwp A bearing vibration (y direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47389 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CP102 |  | 10PAB41CP102 | Pressure Hidraulic CWP #1 A | AI | 0 | 25 | MPa
47390 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 4 | CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB41CP111 |  | 10PAB41CP111 | #1 Unit Cwp A outlet press | AI | 0 | 0.3 | MPa
47391 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42AP001XQ01 |  | 10PAB42AP001XQ01 | #1 Unit cwp B motor current | AI | 0 | 150 | A
47392 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT116 |  | 10PAB42CT116 | #1 Unit cwp B motor widing temp. 6 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47393 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT111 |  | 10PAB42CT111 | #1 Unit cwp B motor widing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47394 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT112 |  | 10PAB42CT112 | #1 Unit cwp B motor widing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47395 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT113 |  | 10PAB42CT113 | #1 Unit cwp B motor widing temp. 3 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47396 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT114 |  | 10PAB42CT114 | #1 Unit cwp B motor widing temp. 4 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47397 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT115 |  | 10PAB42CT115 | #1 Unit cwp B motor widing temp. 5 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
47398 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT117 |  | 10PAB42CT117 | #1 Unit cwp B thrust bearing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47399 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CT118 |  | 10PAB42CT118 | #1 Unit cwp B thrust bearing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47400 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CF101 |  | 10PAB42CF101 | #1 Unit cwp B outlet flow | AI | 0 | 4 | m3/h
47401 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CY101X |  | 10PAB42CY101X | #1 Unit cwp B bearing vibration (x direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47402 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CY101Y |  | 10PAB42CY101Y | #1 Unit cwp B bearing vibration (y direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47403 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CP102 |  | 10PAB42CP102 | Pressure Hidraulic CWP #1 B | AI | 0 | 20 | MPa
47404 | 1 | UJKTT #1 | 10 | #1 CIRCULATING WATER SYSTEM | 5 | CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.10PAB42CP111 |  | 10PAB42CP111 | #1 Unit cwp B outlet press | AI | 0 | 0.3 | MPa
47405 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 1 | #1 220V DC SYSTEM 1 |  | KALTIM1.SIGNAL.AI.10BUD02CE002 |  | 10BUD02CE002 | #1 Unit 220V DC System No.1 Charge panel charger current | AI | 0 | 100 | A
47406 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 1 | #1 220V DC SYSTEM 1 |  | KALTIM1.SIGNAL.AI.10BUD03CE002 |  | 10BUD03CE002 | #1 Unit 220V DC System No.1 connect panel battery current | AI | 0 | 100 | A
47407 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 1 | #1 220V DC SYSTEM 1 |  | KALTIM1.SIGNAL.AI.10BUD02CE001 |  | 10BUD02CE001 | #1 Unit 220V DC System No.1 Charge panel charger voltage | AI | 0 | 100 | V
47408 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 1 | #1 220V DC SYSTEM 1 |  | KALTIM1.SIGNAL.AI.10BUD03CE001 |  | 10BUD03CE001 | #1 Unit 220V DC System No.1 connect panel battery voltage | AI | 0 | 100 | V
47409 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 1 | #1 220V DC SYSTEM 1 |  | KALTIM1.SIGNAL.AI.10BUD03CE003 |  | 10BUD03CE003 | #1 Unit 220V DC System No.1 connect panel bus I voltage | AI | 0 | 100 | V
47410 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 2 | #1 220V DC SYSTEM 2 |  | KALTIM1.SIGNAL.AI.10BUD04CE002 |  | 10BUD04CE002 | #1 Unit 220V DC System No.2 connect panel battery current | AI | 0 | 100 | A
47411 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 2 | #1 220V DC SYSTEM 2 |  | KALTIM1.SIGNAL.AI.10BUD05CE002 |  | 10BUD05CE002 | #1 Unit 220V DC System No.2 Charge panel charger current | AI | 0 | 100 | A
47412 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 2 | #1 220V DC SYSTEM 2 |  | KALTIM1.SIGNAL.AI.10BUD04CE001 |  | 10BUD04CE001 | #1 Unit 220V DC System No.2 connect panel battery voltage | AI | 0 | 100 | V
47413 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 2 | #1 220V DC SYSTEM 2 |  | KALTIM1.SIGNAL.AI.10BUD04CE003 |  | 10BUD04CE003 | #1 Unit 220V DC System No.2 connect panel bus II voltage | AI | 0 | 100 | V
47414 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 2 | #1 220V DC SYSTEM 2 |  | KALTIM1.SIGNAL.AI.10BUD05CE001 |  | 10BUD05CE001 | #1 Unit 220V DC System No.2 Charge panel charger voltage | AI | 0 | 100 | V
47415 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 3 | #1 UPS |  | KALTIM1.SIGNAL.AI.10BRA03CE002 |  | 10BRA03CE002 | #1 Unit UPS Output AC Current | AI | 0 | 100 | A
47416 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 3 | #1 UPS |  | KALTIM1.SIGNAL.AI.10BRA03CE003 |  | 10BRA03CE003 | #1 Unit UPS Output Frequency | AI | 0 | 100 | HZ
47417 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 3 | #1 UPS |  | KALTIM1.SIGNAL.AI.10BRA03CE001 |  | 10BRA03CE001 | #1 Unit UPS Output AC Voltage | AI | 0 | 100 | V
47418 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 4 | #1 LV AUXILIARY POWER TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BBA11CE001 |  | 10BBA11CE001 | #1 LV Auxiliary Power TR. A current at 6kV side | AI | 0 | 300 | A
47419 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 4 | #1 LV AUXILIARY POWER TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BBA12CE001 |  | 10BBA12CE001 | #1 LV Auxiliary Power TR. B current at 6kV side | AI | 0 | 300 | A
47420 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA02CE001 |  | 10BBA02CE001 | 6kV unit board bus-tie CB current | AI | 0 | 2000 | A
47421 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA04CE001 |  | 10BBA04CE001 | 6kV unit board I to 6kV common board No.1 power feeder CB curren | AI | 0 | 1000 | A
47422 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA01CE001 |  | 10BBA01CE001 | 6kV unit board I incoming PT voltage for AC phase | AI | 0 | 9.45 | KV
47423 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA15CE001 |  | 10BBA15CE001 | 6kV Unit Board I phase AB voltage | AI | 0 | 10.47 | KV
47424 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA15CE002 |  | 10BBA15CE002 | 6kV Unit Board I phase BC voltage | AI | 0 | 10.47 | KV
47425 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 5 | #1 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BBA15CE003 |  | 10BBA15CE003 | 6kV Unit Board I phase CA voltage | AI | 0 | 10.47 | KV
47426 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 6 | #1 CW AUXILIARY POWER TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BBA13CE001 |  | 10BBA13CE001 | #1 Circulating Water TR. current at 6kV side | AI | 0 | 100 | A
47427 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 7 | #1 ESP AUXILIARY POWER TRANSFORMER |  | KALTIM1.SIGNAL.AI.10BBA14CE001 |  | 10BBA14CE001 | #1 ESP TR. current at 6kV side | AI | 0 | 200 | A
47428 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE001 |  | 10BBT01CE001 | #1 Unit Aux. Tran. phase B current | AI | 0 | 1500 | A
47429 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE011 |  | 10BBT01CE011 | #1 Unit Aux. Tran. winding temperature | AI | 0 | 150 | ℃
47430 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE012 |  | 10BBT01CE012 | #1 Unit Aux. Tran. oil temperature 1 | AI | 0 | 160 | ℃
47431 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE013 |  | 10BBT01CE013 | #1 Unit Aux. Tran. oil temperature 2 | AI | 0 | 150 | ℃
47432 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE003 |  | 10BBT01CE003 | #1 Unit Aux. Tran. reactive power | AI | 0 | 34.8 | MVAR
47433 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 8 | #1 UNIT AUXILIARY TRANFORMER |  | KALTIM1.SIGNAL.AI.10BBT01CE002 |  | 10BBT01CE002 | #1 Unit Aux. Tran. active power | AI | 0 | 34.8 | MW
47434 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA02ACE001 |  | 10BFA02ACE001 | #1 Unit service PDC bus-tie CB current | AI | 0 | 100 | A
47435 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA03BCE001 |  | 10BFA03BCE001 | Unit service MCC I B board No.1 power feeder current | AI | 0 | 100 | A
47436 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA04ACE001 |  | 10BFA04ACE001 | Common service MCC A board No.1 power feeder current | AI | 0 | 100 | A
47437 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA05BCE001 |  | 10BFA05BCE001 | #1 emergency power supply IB board power 1 CB current | AI | 0 | 100 | A
47438 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB03ACE001 |  | 10BFB03ACE001 | Unit service MCC I A board No.2 power feeder current | AI | 0 | 100 | A
47439 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB04BCE001 |  | 10BFB04BCE001 | #1 emergency power supply IA board power 2 CB current | AI | 0 | 100 | A
47440 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMA01BCE001 |  | 10BMA01BCE001 | Incoming CB II of 400/230V emergency power supply IA board (K16) | AI | 0 | 100 | A
47441 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMA02ACE001 |  | 10BMA02ACE001 | Incoming CB III of 400/230V emergency power supply IA board (K13 | AI | 0 | 100 | A
47442 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMB01ACE001 |  | 10BMB01ACE001 | Incoming CB I of 400/230V emergency power supply IB board (K17) | AI | 0 | 100 | A
47443 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMB02ACE001 |  | 10BMB02ACE001 | Incoming CB III of 400/230V emergency power supply IB board (K14 | AI | 0 | 100 | A
47444 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM 0.SIGNAL.AI.10BHB02ACE001 |  | 10BHB02ACE001 | Circulating Water PDC PDC bus-tie CB current | AI | 0 | 100 | A
47445 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA03ACE001 |  | 10BFA03ACE001 | Unit service MCC I A board No.1 power feeder current | AI | 0 | 100 | A
47446 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA04BCE001 |  | 10BFA04BCE001 | #1 emergency power supply IA board power 1 CB current | AI | 0 | 100 | A
47447 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB02ACE001 |  | 10BFB02ACE001 | Coal bunkey belt conveyor MCC board No.1 power feeder current | AI | 0 | 100 | A
47448 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB03BCE001 |  | 10BFB03BCE001 | Unit service MCC I B board No.2 power feeder current | AI | 0 | 100 | A
47449 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB04ACE001 |  | 10BFB04ACE001 | Common service MCC B board No.1 power feeder current | AI | 0 | 100 | A
47450 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB05BCE001 |  | 10BFB05BCE001 | #1 emergency power supply IB board power 2 CB current | AI | 0 | 100 | A
47451 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMA01ACE001 |  | 10BMA01ACE001 | Incoming CB I of 400/230V emergency power supply IA board (K15) | AI | 0 | 100 | A
47452 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMB01BCE001 |  | 10BMB01BCE001 | Incoming CB II of 400/230V emergency power supply IB board (K18) | AI | 0 | 600 | A
47453 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BHA01BCE002 |  | 10BHA01BCE002 | #1 ESP. PDC A board incoming PT voltage for AC phase | AI | 0 | 100 | V
47454 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM 0.SIGNAL.AI.10BHB01BCE002 |  | 10BHB01BCE002 | Circulating Water PDC A board incoming PT voltage for AC phase | AI | 0 | 100 | V
47455 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMB02BCE001 |  | 10BMB02BCE001 | Emergency power supply IB board PT phase AC voltage | AI | 0 | 400 | V
47456 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFA01BCE002 |  | 10BFA01BCE002 | #1 Power house PDC A board incoming PT voltage for AC phase | AI | 0 | 400 | V
47457 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BFB01ACE002 |  | 10BFB01ACE002 | #1 Power house PDC B board incoming PT voltage for AC phase | AI | 0 | 400 | V
47458 | 1 | UJKTT #1 | 11 | #1 POWER TRANSFORMER SYSTEM | 9 | #1 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM1.SIGNAL.AI.10BMA02BCE001 |  | 10BMA02BCE001 | Emergency power supply IA board PT phase AC voltage | AI | 0 | 400 | V
47459 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 1 | #1 MAIN OIL TANK | K0102-25 | KALTIM1.SIGNAL.AI.10MAU12CL101 |  | 10MAU12CL101 | LUBE OIL TANK LEVEL 1 | AI | 0 | 600 | mm |  |  | -100 | 100 | [5 empty] | 0 | 1
47460 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 1 | #1 MAIN OIL TANK | K0102-25 | KALTIM1.SIGNAL.AI.10MAU12CL102 |  | 10MAU12CL102 | LUBE OIL TANK LEVEL 2 | AI | 0 | 600 | mm |  |  | -100 | 100 | [5 empty] | 0 | 1
47461 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 2 | #1 DC OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30AP004XQ01 |  | 10MAU30AP004XQ01 | DC LUBE OIL PMP CURRENT | AI | 0 | 100 | %
47462 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 2 | #1 DC OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30CP103 |  | 10MAU30CP103 | OIL P 6 OF DC LUBE OIL PMP OUTLET | AI | 0 | 0.6 | MPa
47463 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 3 | #1 AC OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30AP003XQ01 |  | 10MAU30AP003XQ01 | AC LUBE OIL PMP CURRENT | AI | 0 | 100 | A
47464 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 3 | #1 AC OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30CP102 |  | 10MAU30CP102 | OIL P 6 OF AC LUBE OIL PMP OUTLET | AI | 0 | 0.6 | MPa
47465 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 4 | #1 HP OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30AP002XQ01 |  | 10MAU30AP002XQ01 | HP START-UP OIL PMP CURRENT | AI | 0 | 300 | %
47466 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 4 | #1 HP OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU30CP101 |  | 10MAU30CP101 | OIL P 6 OF HP START-UP OIL PMP OUTLET | AI | 0 | 2.5 | MPa
47467 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 5 | #1 MAIN OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU20CP101 |  | 10MAU20CP101 | OIL P OF MAIN LUBE OIL PMP INLET | AI | 0 | 0.4 | MPa
47468 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 5 | #1 MAIN OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU20CP102 |  | 10MAU20CP102 | OIL P BFR CHK OF MAIN LUBE OIL PMP OUTLET | AI | 0 | 4 | MPa
47469 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 5 | #1 MAIN OIL PUMP | K0102-25 | KALTIM1.SIGNAL.AI.10MAU20CP103 |  | 10MAU20CP103 | OIL P AFR CHK OF MAIN LUBE OIL PMP OUTLET | AI | 0 | 4 | MPa
47470 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 5 | #1 MAIN OIL PUMP | K0102-36 | KALTIM1.SIGNAL.AI.10MAU20CP105 |  | 10MAU20CP105 | RESET OIL P | AI | 0 | 4 | MPa
47471 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB50AA101XQ12 |  | 10PGB50AA101XQ12 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER PSN | AI | 0 | 100 | %
47472 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.AO.10PGB50AA101XQ11 |  | 10PGB50AA101XQ11 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER ADJ CMD | AO | 0 | 100 | %
47473 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-25 | KALTIM1.SIGNAL.RTD.10MAV12CT101 |  | 10MAV12CT101 | OIL TEMP OF A LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃
47474 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-25 | KALTIM1.SIGNAL.RTD.10MAV12CT102 |  | 10MAV12CT102 | OIL TEMP OF A LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
47475 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB50CT101 |  | 10PGB50CT101 | WTR TEMP OF TURB LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
49105 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.AO.10PGB50AA101XQ11 |  | 10PGB50AA101XQ11 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER ADJ CMD | AO | 0 | 100 | %
49106 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB50AA101XQ12 |  | 10PGB50AA101XQ12 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER PSN | AI | 0 | 100 | %
49107 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 6 | #1 LUBE OIL COOLER A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB50CT101 |  | 10PGB50CT101 | WTR TEMP OF TURB LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
47476 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 7 | #1 LUBE OIL COOLER B | K0102-25 | KALTIM1.SIGNAL.RTD.10MAV13CT101 |  | 10MAV13CT101 | OIL TEMP OF B LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃
47477 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 7 | #1 LUBE OIL COOLER B | K0102-25 | KALTIM1.SIGNAL.RTD.10MAV13CT102 |  | 10MAV13CT102 | OIL TEMP OF B LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
47478 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 8 | #1 JACKING OIL PUMP A | K0102-25 | KALTIM1.SIGNAL.AI.10MAU40AP001XQ01 |  | 10MAU40AP001XQ01 | A JACKING OIL PMP CURRENT | AI | 0 | 100 | A |  |  |  |  | 58
47479 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 8 | #1 JACKING OIL PUMP A | K0102-25 | KALTIM1.SIGNAL.AI.10MAU40CP101 |  | 10MAU40CP101 | OIL P OF JACKING OIL MAIN PIP | AI | 0 | 25 | MPa |  |  | 8 | [6 empty] | 2 | 1
49111 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 8 | #1 JACKING OIL PUMP A | K0102-25 | KALTIM1.SIGNAL.AI.10MAU40CP101 |  | 10MAU40CP101 | OIL P OF JACKING OIL MAIN PIP | AI | 0 | 25 | MPa
47480 | 1 | UJKTT #1 | 12 | #1 LUBRICANT OIL SYSTEM | 9 | #1 JACKING OIL PUMP B | K0102-25 | KALTIM1.SIGNAL.AI.10MAU40AP002XQ01 |  | 10MAU40AP002XQ01 | B JACKING OIL PMP CURRENT | AI | 0 | 100 | A
47481 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 1 | #1 EXPANSION TANK | K0102-33 | KALTIM1.SIGNAL.AI.10PGB20AA101XQ12 |  | 10PGB20AA101XQ12 | LEVEL CTRL VLV OF EXPANSION TANK PSN | AI | 0 | 100 | %
47482 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 1 | #1 EXPANSION TANK | K0102-33 | KALTIM1.SIGNAL.AO.10PGB20AA101XQ11 |  | 10PGB20AA101XQ11 | LEVEL CTRL VLV OF EXPANSION TANK ADJ CMD | AO | 0 | 100 | %
47483 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 1 | #1 EXPANSION TANK | K0102-33 | KALTIM1.SIGNAL.AI.10PGB20CL101 |  | 10PGB20CL101 | LEVEL OF EXPANSION TANK | AI | 0 | 1200 | mm |  |  | 300 | 1100 | [5 empty] | 0 | 1
47484 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB30AP001XQ01 |  | 10PGB30AP001XQ01 | A CLSDCOOLING WTR PMP CURRENT | AI | 0 | 50 | A |  |  |  | 21.98 | [5 empty] | 1 | 1
47485 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB30CT101 |  | 10PGB30CT101 | A CLSDCOOLING WTR PMP DRIVEN END TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
47486 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB30CT102 |  | 10PGB30CT102 | A CLSDCOOLING WTR PMP NON-DRIVEN TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
47487 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB30CT103 |  | 10PGB30CT103 | A CLSDCOOLING WTR PMP WINDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47488 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB30CT104 |  | 10PGB30CT104 | A CLSDCOOLING WTR PMP WINDING TEMP2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47489 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB30CT105 |  | 10PGB30CT105 | A CLSDCOOLING WTR PMP WINDING TEMP3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47490 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB30CP101 |  | 10PGB30CP101 | DIFF P OF A CLSDCOOLING WTR PMP INLET FLTR | AI | 0 | 60 | kPa |  |  |  | 40 | [5 empty] | 1
47491 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB32CP101 |  | 10PGB32CP101 | P OF THE MAIN PIP OF CLSDCOOLING WTR PMPS | AI | 0 | 1 | MPa |  |  | 0.4 | [6 empty] | 2
47492 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.10GUP10CQ101 |  | 10GUP10CQ101 | Unit 1 Common header of Closed cooling water PH | AI | 0 | 14
47493 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.10GUP10CQ102 |  | 10GUP10CQ102 | Unit 1 Common header of Closed cooling water CC | AI | 0 | 20
49071 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.10GUP10CQ101 |  | 10GUP10CQ101 | Unit 1 Common header of Closed cooling water PH | AI | 0 | 14
49072 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.10GUP10CQ102 |  | 10GUP10CQ102 | Unit 1 Common header of Closed cooling water CC | AI | 0 | 20
49073 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 2 | #1 CCCW PUMP A | K0102-33 | KALTIM1.SIGNAL.AI.10PGB32CP101 |  | 10PGB32CP101 | P OF THE MAIN PIP OF CLSDCOOLING WTR PMPS | AI | 0 | 1 | MPa
47494 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.AI.10PGB31AP001XQ01 |  | 10PGB31AP001XQ01 | B CLSDCOOLING WTR PMP CURRENT | AI | 0 | 50 | A |  |  |  | 21.98 | [5 empty] | 1 | 1
47495 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB31CT101 |  | 10PGB31CT101 | B CLSDCOOLING WTR PMP DRIVEN END TEMP | RTD | 0 | 300 | ℃ |  |  |  | 80 | [5 empty] | 1 | 1
47496 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB31CT102 |  | 10PGB31CT102 | B CLSDCOOLING WTR PMP NON-DRIVEN TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
47497 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB31CT103 |  | 10PGB31CT103 | B CLSDCOOLING WTR PMP WINDING TEMP1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47498 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB31CT104 |  | 10PGB31CT104 | B CLSDCOOLING WTR PMP WINDING TEMP2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47499 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB31CT105 |  | 10PGB31CT105 | B CLSDCOOLING WTR PMP WINDING TEMP3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
47500 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 3 | #1 CCCW PUMP B | K0102-33 | KALTIM1.SIGNAL.AI.10PGB31CP101 |  | 10PGB31CP101 | DIFF P OF B CLSDCOOLING WTR PMP INLET FLTR | AI | 0 | 60 | kPa |  |  |  | 40 | [5 empty] | 1
47501 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB10CT101 |  | 10PCB10CT101 | TEMP OF THE MAIN PIP OF STRAINER CIRCLE WTR | RTD | 0 | 300 | ℃
47502 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB20CT101 |  | 10PCB20CT101 | WTR TEMP OF A CLSDWTR HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
47503 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB33CT101 |  | 10PGB33CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS INLET | RTD | 0 | 300 | ℃
47504 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB40CT101 |  | 10PGB40CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS OUTLET | RTD | 0 | 300 | ℃
47505 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-35 | KALTIM1.SIGNAL.AI.10PCB10CP101 |  | 10PCB10CP101 | P OF THE MAIN PIP OF STRAINER CIRCLE WTR | AI | 0 | 0.4 | MPa |  |  | 0.03 | [6 empty] | 2
49077 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-35 | KALTIM1.SIGNAL.AI.10PCB10CP101 |  | 10PCB10CP101 | P OF THE MAIN PIP OF STRAINER CIRCLE WTR | AI | 0 | 0.4 | MPa |  |  | 0.03 | [6 empty] | 2
49078 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB10CT101 |  | 10PCB10CT101 | TEMP OF THE MAIN PIP OF STRAINER CIRCLE WTR | RTD | 0 | 300 | ℃
49079 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB33CT101 |  | 10PGB33CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS INLET | RTD | 0 | 300 | ℃
49080 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 4 | #1 HE CCCW A | K0102-33 | KALTIM1.SIGNAL.RTD.10PGB40CT101 |  | 10PGB40CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS OUTLET | RTD | 0 | 300 | ℃
47506 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 5 | #1 HE CCCW B | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB20CT102 |  | 10PCB20CT102 | WTR TEMP OF B CLSDWTR HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
47507 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 6 | #1 HE VACUM PUMP A | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB40CT101 |  | 10PCB40CT101 | WTR TEMP OF A WTR-RING VACUM PMP HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
47508 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 6 | #1 HE VACUM PUMP A | K0102-35 | KALTIM1.SIGNAL.AI.10PCB30CP101 |  | 10PCB30CP101 | DIFF P OF A WTR-RING VACUM PMP HEAT EXCHANGER INLET FLTR | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
47509 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 7 | #1 HE VACUM PUMP B | K0102-35 | KALTIM1.SIGNAL.RTD.10PCB40CT102 |  | 10PCB40CT102 | WTR TEMP OF B WTR-RING VACUM PMP HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
47510 | 1 | UJKTT #1 | 13 | #1 CCCW SYSTEM | 7 | #1 HE VACUM PUMP B | K0102-35 | KALTIM1.SIGNAL.AI.10PCB30CP102 |  | 10PCB30CP102 | DIFF P OF B WTR-RING VACUM PMP HEAT EXCHANGER INLET FLTR | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
47511 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB20CP101 |  | 10QFB20CP101 | Pressure of boiler instrument air main pipe 1 | AI | 0 | 1 | MPa
47512 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB21CP101 |  | 10QFB21CP101 | Boiler #1 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
47513 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB22CP101 |  | 10QFB22CP101 | Boiler #2 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
47514 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB23CP101 |  | 10QFB23CP101 | Boiler #3 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
47515 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB24CP101 |  | 10QFB24CP101 | Boiler #4 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
47516 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM1.SIGNAL.AI.10QFB30CP101 |  | 10QFB30CP101 | Pressure of boiler instrument air main pipe 2 | AI | 0 | 1 | MPa
47517 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-06 | KALTIM1.SIGNAL.AI.10QFB40CP101 |  | 10QFB40CP101 | Pressure of turbine instrument air main pipe 1 | AI | 0 | 1 | MPa
47518 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-06 | KALTIM1.SIGNAL.AI.10QFB50CP101 |  | 10QFB50CP101 | Pressure of turbine instrument air main pipe 2 | AI | 0 | 1 | MPa
47519 | 1 | UJKTT #1 | 14 | #1 INSTRUMENT AIR SYSTEM | 1 | #1 INSTRUMENT AIR DISTRIBUTION | K0108-07 | KALTIM1.SIGNAL.AI.10QFB51CP101 |  | 10QFB51CP101 | Pressure of extraction steam check valve instrument air main pip | AI | 0 | 1 | MPa
47520 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 1 | #1 EH MAIN OIL TANK | K0102-27 | KALTIM1.SIGNAL.RTD.10MAX01CT101 |  | 10MAX01CT101 | OIL TEMP OF EH OIL TANK | RTD | 0 | 300 | ℃
47521 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 1 | #1 EH MAIN OIL TANK | K0102-27 | KALTIM1.SIGNAL.AI.10MAX01CL101 |  | 10MAX01CL101 | EH OIL TANK LEVEL | AI | 0 | 700 | mm |  | 280 | 410 | 580 | [5 empty] | 0 | 1
47522 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 2 | #1 EH MAIN OIL PUMP A | K0102-27 | KALTIM1.SIGNAL.AI.10MAX11AP001XQ01 |  | 10MAX11AP001XQ01 | A MAIN EH PMP CURRENT | AI | 0 | 100 | A
47523 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 2 | #1 EH MAIN OIL PUMP A | K0102-27 | KALTIM1.SIGNAL.AI.10MAX20CP101 |  | 10MAX20CP101 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 21 | MPa
47524 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 2 | #1 EH MAIN OIL PUMP A | K0102-27 | KALTIM1.SIGNAL.AI.10MAX20CP102 |  | 10MAX20CP102 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 25 | MPa
49113 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 2 | #1 EH MAIN OIL PUMP A | K0102-27 | KALTIM1.SIGNAL.AI.10MAX20CP101 |  | 10MAX20CP101 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 21 | MPa
49114 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 2 | #1 EH MAIN OIL PUMP A | K0102-27 | KALTIM1.SIGNAL.AI.10MAX20CP102 |  | 10MAX20CP102 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 25 | MPa
47525 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM1.SIGNAL.AI.10MAX12AP001XQ01 |  | 10MAX12AP001XQ01 | B MAIN EH PMP CURRENT | AI | 0 | 100 | A
47703 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AI.20HJS10AA101XQ12 |  | 20HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
47706 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AO.20HJS10AA101XQ11 |  | 20HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48951 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AO.20HJS10AA101XQ11 |  | 20HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48952 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AI.20HJS10AA101XQ12 |  | 20HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48962 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AO.20HJS10AA101XQ11 |  | 20HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48963 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AI.20HJS10AA101XQ12 |  | 20HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48973 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AO.20HJS10AA101XQ11 |  | 20HJS10AA101XQ11 | Upper bed purging steam inlet control valve control command | AO | 0 | 100 | %
48974 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 3 | #1 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AI.20HJS10AA101XQ12 |  | 20HJS10AA101XQ12 | Upper bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
47526 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 4 | #1 EH COOLER A | K0102-27 | KALTIM1.SIGNAL.RTD.10MAX14CT101 |  | 10MAX14CT101 | OIL TEMP OF A EH OIL COOLER OUTLET | RTD | 0 | 300 | ℃
47707 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 4 | #1 EH COOLER A | K0102-27 | KALTIM2.SIGNAL.TC.20HJS01CT101 |  | 20HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃ |  |  | 140 | [6 empty] | 2 | 1
48950 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 4 | #1 EH COOLER A | K0102-27 | KALTIM2.SIGNAL.TC.20HJS01CT101 |  | 20HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
48961 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 4 | #1 EH COOLER A | K0102-27 | KALTIM2.SIGNAL.TC.20HJS01CT101 |  | 20HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
48972 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 4 | #1 EH COOLER A | K0102-27 | KALTIM2.SIGNAL.TC.20HJS01CT101 |  | 20HJS01CT101 | Purging steam temperature | TC | 0 | 300 | ℃
47527 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 5 | #1 EH COOLER B | K0102-27 | KALTIM1.SIGNAL.RTD.10MAX60CT101 |  | 10MAX60CT101 | OIL TEMP OF B EH OIL COOLER INLET | RTD | 0 | 300 | ℃
47528 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 5 | #1 EH COOLER B | K0102-27 | KALTIM1.SIGNAL.RTD.10MAX60CT102 |  | 10MAX60CT102 | OIL TEMP OF B EH OIL COOLER OUTLET | RTD | 0 | 300 | ℃
49117 | 1 | UJKTT #1 | 15 | #1 ELECTRO HYDROLIC SYSTEM | 5 | #1 EH COOLER B | K0102-27 | KALTIM1.SIGNAL.RTD.10MAX60CT101 |  | 10MAX60CT101 | OIL TEMP OF A EH OIL COOLER INLET | RTD | 0 | 300 | ℃
47529 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.TC.10LBG20CT101 |  | 10LBG20CT101 | TEMP OF THE STM OF AUX STM MAIN PIP | TC | 0 | 800 | ℃
47530 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.TC.10LBG22CT101 |  | 10LBG22CT101 | TEMP OF THE STM FROM NO.3 EXTR STM TO AUX STM | TC | 0 | 800 | ℃
47531 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.TC.10LBG24CT101 |  | 10LBG24CT101 | TEMP OF THE STM FROM AUX STM TO BOILER BTM HEATING | TC | 0 | 800 | ℃
47532 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.TC.10LBG25CT101 |  | 10LBG25CT101 | TEMP OF THE STM FROM AUX STM TO OIL GUN ATOMIZATION | TC | 0 | 800 | ℃
47533 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.AI.10LBG20CP101 |  | 10LBG20CP101 | P OF THE STM OF AUX STM MAIN PIP | AI | 0 | 1.6 | MPa
47534 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.AI.10LBG22CP101 |  | 10LBG22CP101 | P OF THE STM FROM NO.3 EXTR STM TO AUX STM | AI | 0 | 1.6 | MPa
47535 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.AI.10LBG24CP101 |  | 10LBG24CP101 | P OF THE STM FROM AUX STM TO BOILER BTM HEATING | AI | 0 | 1.6 | MPa
47536 | 1 | UJKTT #1 | 16 | #1 AUXILIARY STEAM SYSTEM | 1 | #1 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM1.SIGNAL.AI.10LBG25CP101 |  | 10LBG25CP101 | P OF THE STM FROM AUX STM TO OIL GUN ATOMIZATION | AI | 0 | 1.6 | MPa
47537 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10HDA10AN001XQ12 |  | 10HDA10AN001XQ12 | A slag cooler speed feedback | AI | 0 | 100 | %
47538 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36AA101XQ12 |  | 10LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
47539 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AO.10HDA10AN001XQ11 |  | 10HDA10AN001XQ11 | A slag cooler control command | AO | 0 | 100 | %
47540 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AO.10LCE36AA101XQ11 |  | 10LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
47541 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.RTD.10LCE36CT101 |  | 10LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
47542 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-08 | KALTIM1.SIGNAL.TC.10HDA10CT101 |  | 10HDA10CT101 | Furnace to A slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
47543 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE30CP101 |  | 10LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa |  |  | 0.4 | [6 empty] | 2 | 1
47544 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36CP101 |  | 10LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49085 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE30CP101 |  | 10LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa |  |  | 0.4 | [6 empty] | 2
49086 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AO.10LCE36AA101XQ11 |  | 10LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
49087 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36AA101XQ12 |  | 10LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
49088 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36CP101 |  | 10LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49089 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.RTD.10LCE36CT101 |  | 10LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
49090 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE30CP101 |  | 10LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa |  |  | 0.4 | [6 empty] | 2
49091 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AO.10LCE36AA101XQ11 |  | 10LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
49092 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36AA101XQ12 |  | 10LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
49093 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.AI.10LCE36CP101 |  | 10LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49094 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 1 | #1 SLAG COOLER A | K0102-16 | KALTIM1.SIGNAL.RTD.10LCE36CT101 |  | 10LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
47545 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 2 | #1 SLAG COOLER B | K0102-16 | KALTIM1.SIGNAL.AI.10HDA20AN001XQ12 |  | 10HDA20AN001XQ12 | B slag cooler speed feedback | AI | 0 | 100 | %
47546 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 2 | #1 SLAG COOLER B | K0102-16 | KALTIM1.SIGNAL.AO.10HDA20AN001XQ11 |  | 10HDA20AN001XQ11 | B slag cooler control command | AO | 0 | 100 | %
47547 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 2 | #1 SLAG COOLER B | K0102-08 | KALTIM1.SIGNAL.TC.10HDA20CT101 |  | 10HDA20CT101 | Furnace to B slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
47548 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM1.SIGNAL.AI.10HDA30AN001XQ12 |  | 10HDA30AN001XQ12 | C slag cooler speed feedback | AI | 0 | 100 | %
47549 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM1.SIGNAL.AO.10HDA30AN001XQ11 |  | 10HDA30AN001XQ11 | C slag cooler control command | AO | 0 | 100 | %
47550 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-08 | KALTIM1.SIGNAL.TC.10HDA30CT101 |  | 10HDA30CT101 | Furnace to C slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
48035 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20AA101XQ12 |  | 20HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
48037 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AO.20HJF20AA101XQ11 |  | 20HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
48040 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20CP101 |  | 20HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa |  |  |  | 50 | [5 empty] | 1
49007 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AO.20HJF20AA101XQ11 |  | 20HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
49008 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20AA101XQ12 |  | 20HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
49009 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20CP101 |  | 20HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
49017 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AO.20HJF20AA101XQ11 |  | 20HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
49018 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20AA101XQ12 |  | 20HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
49019 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20CP101 |  | 20HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
49027 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AO.20HJF20AA101XQ11 |  | 20HJF20AA101XQ11 | Lower bed return igniting oil control valve control command | AO | 0 | 100 | %
49028 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20AA101XQ12 |  | 20HJF20AA101XQ12 | Lower bed return igniting oil control valve position feedback | AI | 0 | 100 | %
49029 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 3 | #1 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HJF20CP101 |  | 20HJF20CP101 | Lower bed oil gun inlet oil filter differential pressure | AI | 0 | 100 | kPa
47551 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 4 | #1 SLAG SILO | K0612-02 | KALTIM1.SIGNAL.AI.10EEA10CP101 |  | 10EEA10CP101 | 1#boiler conveying-bed material system transport gas pressure | AI | 0 | 1000 | kPa |  |  | 0.3 | [6 empty] | 2
47552 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 4 | #1 SLAG SILO | K0613-01 | KALTIM1.SIGNAL.AI.10ETE10CL101 |  | 10ETE10CL101 | #1 boiler ash silo Level | AI | 0 | 8.5 | m |  |  |  | 7.64 | [5 empty] | 1 | 1
47553 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 4 | #1 SLAG SILO | K0613-01 | KALTIM1.SIGNAL.AI.10ETE30CL101 |  | 10ETE30CL101 | #1 boiler ash silo Level | AI | 0 | 1.7 | m
47554 | 1 | UJKTT #1 | 17 | #1 ASH HANDLING SYSTEM | 4 | #1 SLAG SILO | K0612-02 | KALTIM1.SIGNAL.AI.10EEA10CP102 |  | 10EEA10CP102 | 1#boiler conveying-bed material system transport material pres | AI | 0 | 1 | MPa |  |  | 0.3 | [6 empty] | 2
47555 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.RTD.10ERB10CT101 |  | 10ERB10CT101 | Fuel oil main pipe temperature | RTD | 0 | 300 | ℃
47556 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.AI.10ERB10CP101 |  | 10ERB10CP101 | Fuel oil inlet pressure | AI | 0 | 3 | MPa
47557 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.AI.10ERB20CP101 |  | 10ERB20CP101 | Return fuel oil main pipe pressure | AI | 0 | 3 | MPa
47558 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.AI.10ERB10CP102 |  | 10ERB10CP102 | Fuel oil main pipe pressure | AI | 0 | 3 | MPa
47559 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.AI.10ERB10CF101 |  | 10ERB10CF101 | Fuel oil inlet main pipe flow | AI | 0 | 25 | t/h
47560 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM | K0102-11 | KALTIM1.SIGNAL.AI.10ERB20CF101 |  | 10ERB20CF101 | Return fuel oil main pipe flow | AI | 0 | 25 | t/h
48890 | 1 | UJKTT #1 | 18 | #1 FUEL OIL SYSTEM | 1 | #1 FUEL OIL SYSTEM |  | 10ERB10CF901 |  | 10ERB10CF901 | Oil Supply | CALC | 0 | 25 | t/h | [8 empty] | (KALTIM1.SIGNAL.AI.10ERB10CF101)-(KALTIM1.SIGNAL.AI.10ERB20CF101)
48899 | 1 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM |  | 20ERB10CF901 |  | 20ERB10CF901 | Oil Supply | CALC | 0 | 25 | t/h | [8 empty] | (KALTIM2.SIGNAL.AI.20ERB10CF101)-(KALTIM2.SIGNAL.AI.20ERB20CF101)
47561 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM1.SIGNAL.AI.10EQH10CL101 |  | 10EQH10CL101 | #1 Boiler Limestone storage level | AI | 0 | 100 | %
47562 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM |  | KALTIM 0.SIGNAL.AI.10BFA07ACE001 |  | 10BFA07ACE001 | A limestone transport aerification fan current | AI | 0 | 100 | A
47563 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM |  | KALTIM 0.SIGNAL.AI.10BFB07ACE001 |  | 10BFB07ACE001 | B limestone transport aerification fan current | AI | 0 | 100 | A
47564 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM1.SIGNAL.AI.10EQH10CP101 |  | 10EQH10CP101 | A Limestone duct pressure 1 | AI | 0 | 100 | kPa
47565 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM1.SIGNAL.AI.10EQH10CP102 |  | 10EQH10CP102 | A Limestone duct pressure 2 | AI | 0 | 100 | kPa
47566 | 1 | UJKTT #1 | 19 | #1 LIMESTONE INJECTION SYSTEM | 1 | #1 LIMESTONE INJECTION SYSTEM |  | KALTIM 0.SIGNAL.AI.10EDD10CP101 |  | 10EDD10CP101 | Pressure of conveying pipe for conveying-limestone 1# | AI | 0 | 100 | MPa
47567 | 1 | UJKTT #1 | 20 | #1 FLY ASH SYSTEM | 1 | #1 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.10ETG11CP101 |  | 10ETG11CP101 | pressure value of convying-ash main pipe in 1# boiler 1st ESP fi | AI | 0 | 1 | MPa
47568 | 1 | UJKTT #1 | 20 | #1 FLY ASH SYSTEM | 1 | #1 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.10ETG21CP101 |  | 10ETG21CP101 | pressure value of conveying-ash main pipe in 1# boiler 2nd&3rd E | AI | 0 | 1 | MPa
47569 | 1 | UJKTT #1 | 20 | #1 FLY ASH SYSTEM | 1 | #1 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.10ETG41CP101 |  | 10ETG41CP101 | pressure value of conveying-ash main pipe in 1# boiler air prehe | AI | 0 | 1 | MPa
47570 | 1 | UJKTT #1 | 20 | #1 FLY ASH SYSTEM | 1 | #1 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.10ETG10CP101 |  | 10ETG10CP101 | pressure conveying-ash 1# boiler | AI | 0 | 100
47571 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HLB10AA101XQ12 |  | 20HLB10AA101XQ12 | A primary air fan inlet control valve position feedback | AI | 0 | 100 | %
47572 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AO.20HLB10AA101XQ11 |  | 20HLB10AA101XQ11 | A primary air fan inlet control valve control command | AO | 0 | 100 | %
47573 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HLB10AN001XQ01 |  | 20HLB10AN001XQ01 | A primary air fan current | AI | 0 | 200 | A
47574 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLA10CT101 |  | 20HLA10CT101 | A primary air fan outlet temperature | RTD | 0 | 100 | ℃
47575 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT101 |  | 20HLB10CT101 | A primary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47576 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT102 |  | 20HLB10CT102 | A primary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47577 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT103 |  | 20HLB10CT103 | A primary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47578 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT104 |  | 20HLB10CT104 | A primary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47579 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT105 |  | 20HLB10CT105 | A primary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47580 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT106 |  | 20HLB10CT106 | A primary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47581 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT107 |  | 20HLB10CT107 | A primary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47582 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT108 |  | 20HLB10CT108 | A primary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47583 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT109 |  | 20HLB10CT109 | A primary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47584 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB10CT110 |  | 20HLB10CT110 | A primary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47585 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HLA10CP101 |  | 20HLA10CP101 | A primary air fan outlet pressure | AI | 0 | 25 | kPa
47587 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HLB10CY102 |  | 20HLB10CY102 | A primary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47588 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 1 | #2 PA FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HLB10CY101 |  | 20HLB10CY101 | A primary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47589 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HLB20AA101XQ12 |  | 20HLB20AA101XQ12 | B primary air fan inlet control valve position feedback | AI | 0 | 100 | %
47590 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AO.20HLB20AA101XQ11 |  | 20HLB20AA101XQ11 | B primary air fan inlet control valve control command | AO | 0 | 100 | %
47591 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HLB20AN001XQ01 |  | 20HLB20AN001XQ01 | B primary air fan current | AI | 0 | 218 | A
47592 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLA20CT101 |  | 20HLA20CT101 | B primary air fan outlet temperature | RTD | 0 | 100 | ℃
47593 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT101 |  | 20HLB20CT101 | B primary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47594 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT102 |  | 20HLB20CT102 | B primary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47595 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT103 |  | 20HLB20CT103 | B primary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47596 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT104 |  | 20HLB20CT104 | B primary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47597 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT105 |  | 20HLB20CT105 | B primary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47598 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT106 |  | 20HLB20CT106 | B primary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47599 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT107 |  | 20HLB20CT107 | B primary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47600 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT108 |  | 20HLB20CT108 | B primary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47601 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT109 |  | 20HLB20CT109 | B primary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47602 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HLB20CT110 |  | 20HLB20CT110 | B primary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47603 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HLA20CP101 |  | 20HLA20CP101 | B primary air fan outlet pressure | AI | 0 | 25 | kPa
47604 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HLB20CY101 |  | 20HLB20CY101 | B primary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1
47605 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 2 | #2 PA FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HLB20CY102 |  | 20HLB20CY102 | B primary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1
47606 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AI.20HLB30AA101XQ12 |  | 20HLB30AA101XQ12 | A secondary air fan inlet control valve position feedback | AI | 0 | 100 | %
47607 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AO.20HLB30AA101XQ11 |  | 20HLB30AA101XQ11 | A secondary air fan inlet control valve control command | AO | 0 | 100 | %
47608 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AI.20HLB30AN001XQ01 |  | 20HLB30AN001XQ01 | A secondary air fan current | AI | 0 | 150 | A
47609 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT105 |  | 20HLB30CT105 | A secondary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47610 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT106 |  | 20HLB30CT106 | A secondary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47611 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT107 |  | 20HLB30CT107 | A secondary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47612 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT108 |  | 20HLB30CT108 | A secondary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47613 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT109 |  | 20HLB30CT109 | A secondary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47614 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT110 |  | 20HLB30CT110 | A secondary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  |  | 120 | [5 empty] | 1
47615 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLA30CT101 |  | 20HLA30CT101 | A secondary air fan outlet temperature | RTD | 0 | 100 | ℃
47616 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT101 |  | 20HLB30CT101 | A secondary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47617 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT102 |  | 20HLB30CT102 | A secondary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47618 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT103 |  | 20HLB30CT103 | A secondary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47619 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB30CT104 |  | 20HLB30CT104 | A secondary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  |  | 80 | [5 empty] | 1
47620 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AI.20HLA30CP101 |  | 20HLA30CP101 | A secondary air fan outlet pressure | AI | 0 | 15 | kPa
47621 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AI.20HLB30CY101 |  | 20HLB30CY101 | A secondary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47622 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 3 | #2 SA FAN A | K0102-05 | KALTIM2.SIGNAL.AI.20HLB30CY102 |  | 20HLB30CY102 | A secondary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47623 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.AI.20HLB40AA101XQ12 |  | 20HLB40AA101XQ12 | B secondary air fan inlet control valve position feedback | AI | 0 | 100 | %
47624 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B |  | KALTIM2.SIGNAL.AO.20HLB40AA101XQ11B |  | 20HLB40AA101XQ11B | B secondary air fan inlet control valve control command, | AO | 0 | 100 | %
47625 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.AI.20HLB40AN001XQ01 |  | 20HLB40AN001XQ01 | B secondary air fan current | AI | 0 | 150 | A
47626 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLA40CT101 |  | 20HLA40CT101 | B secondary air fan outlet temperature | RTD | 0 | 100 | ℃
47627 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT105 |  | 20HLB40CT105 | B secondary air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47628 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT106 |  | 20HLB40CT106 | B secondary air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47629 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT107 |  | 20HLB40CT107 | B secondary air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47630 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT108 |  | 20HLB40CT108 | B secondary air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47631 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT109 |  | 20HLB40CT109 | B secondary air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47632 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT110 |  | 20HLB40CT110 | B secondary air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47633 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT101 |  | 20HLB40CT101 | B secondary air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47634 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT102 |  | 20HLB40CT102 | B secondary air fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47635 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT103 |  | 20HLB40CT103 | B secondary air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47636 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.RTD.20HLB40CT104 |  | 20HLB40CT104 | B secondary air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
47637 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.AI.20HLA40CP101 |  | 20HLA40CP101 | B secondary air fan outlet pressure | AI | 0 | 15 | kPa
47638 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.AI.20HLB40CY101 |  | 20HLB40CY101 | B secondary air fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47639 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 4 | #2 SA FAN B | K0102-05 | KALTIM2.SIGNAL.AI.20HLB40CY102 |  | 20HLB40CY102 | B secondary air fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
47640 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-06 | KALTIM2.SIGNAL.AI.20HDF49AA101XQ12 |  | 20HDF49AA101XQ12 | Control valve for fluidizing air to air preheater outlet positio | AI | 0 | 100 | %
47641 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CQ101 |  | 20HBK31CQ101 | Side-A air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
47642 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CQ101 |  | 20HBK41CQ101 | Side-B air preheater inlet flue gas oxygen content | AI | 0 | 25 | %
47643 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-09 | KALTIM2.SIGNAL.AI.20HNA10AA102XQ12 |  | 20HNA10AA102XQ12 | Motor-driven control damper for side-A boiler outlet flue gas to | AI | 0 | 100 | %
47644 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-09 | KALTIM2.SIGNAL.AI.20HNA20AA102XQ12 |  | 20HNA20AA102XQ12 | Motor-driven control damper for side-B boiler outlet flue gas to | AI | 0 | 100 | %
47645 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-06 | KALTIM2.SIGNAL.AO.20HDF49AA101XQ11 |  | 20HDF49AA101XQ11 | Control valve for fluidizing air to air preheater outlet control | AO | 0 | 100 | %
47646 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-09 | KALTIM2.SIGNAL.AO.20HNA10AA102XQ11 |  | 20HNA10AA102XQ11 | Motor-driven control damper for side-A boiler outlet flue gas to | AO | 0 | 100 | %
47647 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-09 | KALTIM2.SIGNAL.AO.20HNA20AA102XQ11 |  | 20HNA20AA102XQ11 | Motor-driven control damper for side-B boiler outlet flue gas to | AO | 0 | 100 | %
47648 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-04 | KALTIM2.SIGNAL.RTD.20HHL01CT101 |  | 20HHL01CT101 | Air preheater primary air outlet temperature | RTD | 0 | 100 | ℃
47649 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-05 | KALTIM2.SIGNAL.RTD.20HHL10CT101 |  | 20HHL10CT101 | Side-A hot secondary air temperature | RTD | 0 | 300 | ℃
47650 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT105 |  | 20HBK31CT105 | Side-A air preheater outlet flue gas temperautre 1 | TC | 0 | 800 | ℃
47651 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT106 |  | 20HBK31CT106 | Side-A air preheater outlet flue gas temperautre 2 | TC | 0 | 800 | ℃
47652 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT105 |  | 20HBK41CT105 | Side-B air preheater outlet flue gas temperautre 1 | TC | 0 | 800 | ℃
47653 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT106 |  | 20HBK41CT106 | Side-B air preheater outlet flue gas temperautre 2 | TC | 0 | 800 | ℃
47654 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP106 |  | 20HBK31CP106 | Differential pressure between side-A air preheater outlet and ec | AI | 0 | 10 | kPa
47655 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-04 | KALTIM2.SIGNAL.AI.20HHL01CP101 |  | 20HHL01CP101 | Air preheater primary air outlet pressure | AI | 0 | 25 | kPa
47656 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-04 | KALTIM2.SIGNAL.AI.20HHL01CP102 |  | 20HHL01CP102 | Air preheater primary air differencial pressure | AI | 0 | 6 | kPa
47657 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-05 | KALTIM2.SIGNAL.AI.20HHL10CP101 |  | 20HHL10CP101 | Side-A hot secondary air pressure | AI | 0 | 15 | kPa
47658 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-05 | KALTIM2.SIGNAL.AI.20HLA30CP102 |  | 20HLA30CP102 | Air preheater secondary air differencial pressure | AI | 0 | 15 | kPa
47659 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP105 |  | 20HBK31CP105 | Side-A air preheater outlet flue gas pressure | AI | -9 | 0 | kPa
47660 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP105 |  | 20HBK41CP105 | Side-B air preheater outlet flue gas pressure | AI | -9 | 0 | kPa
47661 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 5 | #2 AIR HEATER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP106 |  | 20HBK41CP106 | Differential pressure between side-B air preheater outlet and ec | AI | 0 | 10 | kPa
47662 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF10AN001XQ01 |  | 20HDF10AN001XQ01 | A HP fluidizing air fan current | AI | 0 | 50 | A
47663 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT111 |  | 20HDF10CT111 | A HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
47664 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT101 |  | 20HDF10CT101 | A HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47665 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT103 |  | 20HDF10CT103 | A HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47666 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT104 |  | 20HDF10CT104 | A HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47667 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT105 |  | 20HDF10CT105 | A HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47668 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT106 |  | 20HDF10CT106 | A HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47669 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT107 |  | 20HDF10CT107 | A HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47670 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT108 |  | 20HDF10CT108 | A HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47671 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT109 |  | 20HDF10CT109 | A HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47672 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF10CT110 |  | 20HDF10CT110 | A HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47674 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 6 | #2 HPFB A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF10CP101 |  | 20HDF10CP101 | A HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
47676 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF20AN001XQ01 |  | 20HDF20AN001XQ01 | B HP fluidizing air fan current | AI | 0 | 50 | A
47677 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT101 |  | 20HDF20CT101 | B HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47678 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT103 |  | 20HDF20CT103 | B HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47679 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT104 |  | 20HDF20CT104 | B HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47680 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT105 |  | 20HDF20CT105 | B HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47681 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT106 |  | 20HDF20CT106 | B HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47682 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT107 |  | 20HDF20CT107 | B HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47683 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT108 |  | 20HDF20CT108 | B HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47684 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT109 |  | 20HDF20CT109 | B HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47685 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT110 |  | 20HDF20CT110 | B HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47686 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF20CT111 |  | 20HDF20CT111 | B HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
47687 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 7 | #2 HPFB B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF20CP101 |  | 20HDF20CP101 | B HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
47688 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.AI.20HDF30AN001XQ01 |  | 20HDF30AN001XQ01 | C HP fluidizing air fan current | AI | 0 | 50 | A
47689 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT101 |  | 20HDF30CT101 | C HP fluidizing air fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  |  |  |  | 1 | 1
47690 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT103 |  | 20HDF30CT103 | C HP fluidizing air fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47691 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT104 |  | 20HDF30CT104 | C HP fluidizing air fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ | [10 empty] | 1
47692 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT105 |  | 20HDF30CT105 | C HP fluidizing air fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47693 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT106 |  | 20HDF30CT106 | C HP fluidizing air fan motor stator temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47694 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT107 |  | 20HDF30CT107 | C HP fluidizing air fan motor stator temperature 3 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47695 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT108 |  | 20HDF30CT108 | C HP fluidizing air fan motor stator temperature 4 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47696 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT109 |  | 20HDF30CT109 | C HP fluidizing air fan motor stator temperature 5 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47697 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT110 |  | 20HDF30CT110 | C HP fluidizing air fan motor stator temperature 6 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
47698 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.RTD.20HDF30CT111 |  | 20HDF30CT111 | C HP fluidizing air fan outlet temperature | RTD | 0 | 100 | ℃
47699 | 2 | UJKTT #2 | 1 | #2 AIR SYSTEM | 8 | #2 HPFB C | K0102-06 | KALTIM2.SIGNAL.AI.20HDF30CP101 |  | 20HDF30CP101 | C HP fluidizing air fan outlet pressure | AI | 0 | 100 | kPa
47700 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 1 | #2 BURNER A | K0102-12 | KALTIM2.SIGNAL.AI.20HJA11CB101 |  | 20HJA11CB101 | A upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
47701 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 1 | #2 BURNER A | K0102-12 | KALTIM2.SIGNAL.AI.20HJA11CB102 |  | 20HJA11CB102 | A upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
47702 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 1 | #2 BURNER A | K0102-12 | KALTIM2.SIGNAL.AI.20HJA11CB103 |  | 20HJA11CB103 | A upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
47714 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 2 | #2 BURNER B | K0102-12 | KALTIM2.SIGNAL.AI.20HJA12CB102 |  | 20HJA12CB102 | B upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
47715 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 2 | #2 BURNER B | K0102-12 | KALTIM2.SIGNAL.AI.20HJA12CB101 |  | 20HJA12CB101 | B upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
47716 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 2 | #2 BURNER B | K0102-12 | KALTIM2.SIGNAL.AI.20HJA12CB103 |  | 20HJA12CB103 | B upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
47717 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 3 | #2 BURNER C | K0102-12 | KALTIM2.SIGNAL.AI.20HJA13CB101 |  | 20HJA13CB101 | C upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
47718 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 3 | #2 BURNER C | K0102-12 | KALTIM2.SIGNAL.AI.20HJA13CB103 |  | 20HJA13CB103 | C upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
47719 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 3 | #2 BURNER C | K0102-12 | KALTIM2.SIGNAL.AI.20HJA13CB102 |  | 20HJA13CB102 | C upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
47720 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 4 | #2 BURNER D | K0102-12 | KALTIM2.SIGNAL.AI.20HJA14CB102 |  | 20HJA14CB102 | D upper igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
47721 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 4 | #2 BURNER D | K0102-12 | KALTIM2.SIGNAL.AI.20HJA14CB101 |  | 20HJA14CB101 | D upper igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
47722 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 4 | #2 BURNER D | K0102-12 | KALTIM2.SIGNAL.AI.20HJA14CB103 |  | 20HJA14CB103 | D upper igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
47723 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT101 |  | 20HAH11CT101 | Steam temperature of connection pipe 1 between Side-A seperator | TC | 0 | 400 | °C
47724 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT102 |  | 20HAH11CT102 | Steam temperature of connection pipe 2 between Side-A seperator | TC | 0 | 400 | °C
47725 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT103 |  | 20HAH11CT103 | Steam temperature of connection pipe 3 between Side-A seperator | TC | 0 | 400 | °C
47726 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT104 |  | 20HAH11CT104 | Steam temperature of connection pipe 4 between Side-A seperator | TC | 0 | 400 | °C
47727 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT105 |  | 20HAH11CT105 | Steam temperature of connection pipe 5 between Side-A seperator | TC | 0 | 400 | °C
47728 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH11CT106 |  | 20HAH11CT106 | Steam temperature of connection pipe 6 between Side-A seperator | TC | 0 | 400 | °C
47729 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT101 |  | 20HAH12CT101 | Steam temperature of connection pipe 1 between Side-B seperator | TC | 0 | 400 | °C
47730 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT102 |  | 20HAH12CT102 | Steam temperature of connection pipe 2 between Side-B seperator | TC | 0 | 400 | °C
47731 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT103 |  | 20HAH12CT103 | Steam temperature of connection pipe 3 between Side-B seperator | TC | 0 | 400 | °C
47732 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT104 |  | 20HAH12CT104 | Steam temperature of connection pipe 4 between Side-B seperator | TC | 0 | 400 | °C
47733 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT105 |  | 20HAH12CT105 | Steam temperature of connection pipe 5 between Side-B seperator | TC | 0 | 400 | °C
47734 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 5 | #2 WATERWALL | K0102-03 | KALTIM2.SIGNAL.TC.20HAH12CT106 |  | 20HAH12CT106 | Steam temperature of connection pipe 6 between Side-B seperator | TC | 0 | 400 | °C
47735 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH |  | KALTIM2.SIGNAL.AI.20LAE10AA101XQ12 |  | 20LAE10AA101XQ12 | Main steam to aux steam desuperheating water valve feedback | AI | 0 | 100 | %
47736 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE21AA101XQ12 |  | 20LAE21AA101XQ12 | Side-A primary desuperheater water control valve position feedba | AI | 0 | 100 | %
47737 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE22AA101XQ12 |  | 20LAE22AA101XQ12 | Side-B primary desuperheater water control valve position feedba | AI | 0 | 100 | %
47738 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH |  | KALTIM2.SIGNAL.AO.20LAE10AA101XQ11 |  | 20LAE10AA101XQ11 | Main steam to aux steam desuperheating water valve cmd | AO | 0 | 100 | %
47739 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AO.20LAE21AA101XQ11 |  | 20LAE21AA101XQ11 | Side-A primary desuperheater water control valve control command | AO | 0 | 100 | %
47740 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AO.20LAE22AA101XQ11 |  | 20LAE22AA101XQ11 | Side-B primary desuperheater water control valve control command | AO | 0 | 100 | %
47741 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT101 |  | 20HAH20CT101 | LT superheater outlet pipe wall temperature 1 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47742 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT102 |  | 20HAH20CT102 | LT superheater outlet pipe wall temperature 2 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47743 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT103 |  | 20HAH20CT103 | LT superheater outlet pipe wall temperature 3 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47744 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT104 |  | 20HAH20CT104 | LT superheater outlet pipe wall temperature 4 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47745 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT105 |  | 20HAH20CT105 | LT superheater outlet pipe wall temperature 5 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47746 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH20CT106 |  | 20HAH20CT106 | LT superheater outlet pipe wall temperature 6 | TC | 0 | 500 | °C |  |  |  | 450 | [5 empty] | 1
47747 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.RTD.20LAE20CT101 |  | 20LAE20CT101 | Desuperheater water filter outlet temperature | RTD | 0 | 200 | ℃
47748 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH21CT101 |  | 20HAH21CT101 | Temperature of steam before Side-A primary desuperheater | TC | 0 | 500 | ℃
47749 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH21CT102 |  | 20HAH21CT102 | Temperature 1 of steam after Side-A primary desuperheater | TC | 0 | 500 | ℃
47750 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH21CT103 |  | 20HAH21CT103 | Temperature 2 of steam after Side-A primary desuperheater | TC | 0 | 500 | ℃
47751 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH22CT101 |  | 20HAH22CT101 | Temperature of steam before Side-B primary desuperheater | TC | 0 | 500 | ℃
47752 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH22CT102 |  | 20HAH22CT102 | Temperature 1 of steam after Side-B primary desuperheater | TC | 0 | 500 | ℃
47753 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH22CT103 |  | 20HAH22CT103 | Temperature 2 of steam after Side-B primary desuperheater | TC | 0 | 500 | ℃
47754 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT102 |  | 20HBK31CT102 | Side-A low temperature super heater inlet flue gas temperature | TC | 0 | 800 | ℃
47755 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT103 |  | 20HBK31CT103 | Side-A low temperature super heater outlet flue gas temperature | TC | 0 | 800 | ℃
47756 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT102 |  | 20HBK41CT102 | Side-B low temperature super heater inlet flue gas temperature | TC | 0 | 940 | ℃
47757 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT103 |  | 20HBK41CT103 | Side-B low temperature super heater outlet flue gas temperature | TC | 0 | 700 | ℃
47758 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP102 |  | 20HBK31CP102 | Side-A low temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
47759 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP103 |  | 20HBK31CP103 | Side-A low temperature super heater outlet flue gas pressure | AI | -8 | 1 | kPa
47760 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP102 |  | 20HBK41CP102 | Side-B low temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
47761 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP103 |  | 20HBK41CP103 | Side-B low temperature super heater outlet flue gas pressure | AI | -8 | 1 | kPa
47762 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE20CP101 |  | 20LAE20CP101 | Desuperheater water filter outlet pressure | AI | 0 | 15 | MPa
47763 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH |  | KALTIM 0.SIGNAL.AI.20GUA10CQ101 |  | 20GUA10CQ101 | Unit 2 Left/right side of Saturated steam CC | AI | 0 | 20
47764 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH |  | KALTIM 0.SIGNAL.AI.20GUA20CQ103 |  | 20GUA20CQ103 | Unit 2 Left/right side of Saturated steam SiO2 | AI | 0 | 100
47765 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 6 | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE21CF101 |  | 20LAE21CF101 | Side-A primary desuperheater water flow | AI | 0 | 100
47766 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE23AA101XQ12 |  | 20LAE23AA101XQ12 | Side-A secondary desuperheater water control valve position feed | AI | 0 | 100 | %
47767 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE24AA101XQ12 |  | 20LAE24AA101XQ12 | Side-B secondary desuperheater water control valve position feed | AI | 0 | 100 | %
47768 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AO.20LAE23AA101XQ11 |  | 20LAE23AA101XQ11 | Side-A secondary desuperheater water control valve control comma | AO | 0 | 100 | %
47769 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AO.20LAE24AA101XQ11 |  | 20LAE24AA101XQ11 | Side-B secondary desuperheater water control valve control | AO | 0 | 100 | %
47770 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT101 |  | 20HAH31CT101 | Side-A platen superheater outlet #1 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47771 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT102 |  | 20HAH31CT102 | Side-A platen superheater outlet #1 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47772 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT103 |  | 20HAH31CT103 | Side-A platen superheater outlet #1 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47773 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT104 |  | 20HAH31CT104 | Side-A platen superheater outlet #1 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47774 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT105 |  | 20HAH31CT105 | Side-A platen superheater outlet #2 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47775 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT106 |  | 20HAH31CT106 | Side-A platen superheater outlet #2 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47776 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT107 |  | 20HAH31CT107 | Side-A platen superheater outlet #2 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47777 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT108 |  | 20HAH31CT108 | Side-A platen superheater outlet #2 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47778 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT109 |  | 20HAH31CT109 | Side-A platen superheater outlet #3 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47779 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT110 |  | 20HAH31CT110 | Side-A platen superheater outlet #3 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47780 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT111 |  | 20HAH31CT111 | Side-A platen superheater outlet #3 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47781 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH31CT112 |  | 20HAH31CT112 | Side-A platen superheater outlet #3 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47782 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT101 |  | 20HAH32CT101 | Side-B platen superheater outlet #1 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47783 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT102 |  | 20HAH32CT102 | Side-B platen superheater outlet #1 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47784 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT103 |  | 20HAH32CT103 | Side-B platen superheater outlet #1 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47785 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT104 |  | 20HAH32CT104 | Side-B platen superheater outlet #1 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47786 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT105 |  | 20HAH32CT105 | Side-B platen superheater outlet #2 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47787 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT106 |  | 20HAH32CT106 | Side-B platen superheater outlet #2 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47788 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT107 |  | 20HAH32CT107 | Side-B platen superheater outlet #2 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47789 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT108 |  | 20HAH32CT108 | Side-B platen superheater outlet #2 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47790 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT109 |  | 20HAH32CT109 | Side-B platen superheater outlet #3 platen wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47791 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT110 |  | 20HAH32CT110 | Side-B platen superheater outlet #3 platen wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47792 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT111 |  | 20HAH32CT111 | Side-B platen superheater outlet #3 platen wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47793 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH32CT112 |  | 20HAH32CT112 | Side-B platen superheater outlet #3 platen wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47794 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH41CT101 |  | 20HAH41CT101 | Temperature of steam before Side-A secondary desuperheater | TC | 0 | 500 | ℃
47795 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH41CT102 |  | 20HAH41CT102 | Temperature 1 of steam after Side-A secondary desuperheater | TC | 0 | 500 | ℃
47796 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH41CT103 |  | 20HAH41CT103 | Temperature 2 of steam after Side-A secondary desuperheater | TC | 0 | 500 | ℃
47797 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH42CT101 |  | 20HAH42CT101 | Temperature of steam before Side-B secondary desuperheater | TC | 0 | 500 | ℃
47798 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH42CT102 |  | 20HAH42CT102 | Temperature 1 of steam after Side-B secondary desuperheater | TC | 0 | 500 | ℃
47799 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH42CT103 |  | 20HAH42CT103 | Temperature 2 of steam after Side-B secondary desuperheater | TC | 0 | 500 | ℃
47800 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 7 | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE23CF101 |  | 20LAE23CF101 | Side-A secondary desuperheater water flow | AI | 0 | 100
47801 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT101 |  | 20HAH50CT101 | HT superheater outlet pipe wall temperature 1 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47802 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT102 |  | 20HAH50CT102 | HT superheater outlet pipe wall temperature 2 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47803 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT103 |  | 20HAH50CT103 | HT superheater outlet pipe wall temperature 3 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47804 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT104 |  | 20HAH50CT104 | HT superheater outlet pipe wall temperature 4 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47805 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT105 |  | 20HAH50CT105 | HT superheater outlet pipe wall temperature 5 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47806 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT106 |  | 20HAH50CT106 | HT superheater outlet pipe wall temperature 6 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47807 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT107 |  | 20HAH50CT107 | HT superheater outlet pipe wall temperature 7 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47808 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT108 |  | 20HAH50CT108 | HT superheater outlet pipe wall temperature 8 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47809 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH50CT109 |  | 20HAH50CT109 | HT superheater outlet pipe wall temperature 9 | TC | 0 | 600 | °C |  |  |  | 560 | [5 empty] | 1
47810 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-17 | KALTIM2.SIGNAL.TC.20LBA10CT103 |  | 20LBA10CT103 | MAIN STEAM TEMP | TC | 0 | 800 | °C
47811 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20HAH60CT102 |  | 20HAH60CT102 | Side-B HT superheater outlet header temperature | TC | 0 | 600 | ℃
47812 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT101 |  | 20HBK31CT101 | Side-A high temperature super heater inlet flue gas temperature | TC | 0 | 1200 | ℃
47813 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA01CT101 |  | 20LBA01CT101 | Side-A HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47814 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA01CT102 |  | 20LBA01CT102 | Side-A HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47815 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA01CT103 |  | 20LBA01CT103 | Side-A HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47816 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA02CT101 |  | 20LBA02CT101 | Side-B HT superheater outlet pipe steam temperature 1 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47817 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA02CT102 |  | 20LBA02CT102 | Side-B HT superheater outlet pipe steam temperature 2 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47818 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.TC.20LBA02CT103 |  | 20LBA02CT103 | Side-B HT superheater outlet pipe steam temperature 3 | TC | 0 | 600 | ℃ |  |  |  | 545 | [5 empty] | 1
47819 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT101 |  | 20HBK41CT101 | Side-B high temperature super heater inlet flue gas temperature | TC | 0 | 1200 | ℃
47820 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP101 |  | 20HBK31CP101 | Side-A high temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
47821 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP101 |  | 20HBK41CP101 | Side-B high temperature super heater inlet flue gas pressure | AI | -7 | 1 | kPa
47822 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LBA01CP101 |  | 20LBA01CP101 | Side-A HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10 | [5 empty] | 1
47823 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LBA02CP101 |  | 20LBA02CP101 | Side-B HT superheater outlet pipe steam pressure | AI | 0 | 10 | MPa |  |  |  | 10 | [5 empty] | 1
47824 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-17 | KALTIM2.SIGNAL.AI.20LBA10CP103 |  | 20LBA10CP103 | P OF MAIN STM MAIN PIP | AI | 0 | 16 | MPa
47825 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH | K0102-17 | KALTIM2.SIGNAL.AO.20LBA10CF101 |  | 20LBA10CF101 | Main steam flow | AO | 0 | 500 | t/h
47826 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH |  | KALTIM 0.SIGNAL.AI.20GUA20CQ101 |  | 20GUA20CQ101 | Unit 2 Left/right side of Superheated steam SiO2 | AI | 0 | 20
47827 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 8 | #2 HTSH |  | KALTIM 0.SIGNAL.AI.20GUA20CQ102 |  | 20GUA20CQ102 | Unit 2 Left/right side of Superheated steam SiO2 | AI | 0 | 100
47828 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-02 | KALTIM2.SIGNAL.TC.20LAB50CT103 |  | 20LAB50CT103 | Economizer inlet water temperature | TC | 0 | 400 | ℃
47829 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-02 | KALTIM2.SIGNAL.TC.20LAB50CT104 |  | 20LAB50CT104 | Temperature of water from economizer to drum | TC | 0 | 400 | ℃
47830 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK31CT104 |  | 20HBK31CT104 | Side-A economiser outlet flue gas temperature | TC | 0 | 800 | ℃
47831 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-08 | KALTIM2.SIGNAL.TC.20HBK41CT104 |  | 20HBK41CT104 | Side-B economiser outlet flue gas temperature | TC | 0 | 370 | ℃
47832 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-23 | KALTIM2.SIGNAL.TC.20LBG21CT101 |  | 20LBG21CT101 | TEMP OF THE STM FROM AUX STM TO ECONOMIZER START-UP BLOW | TC | 0 | 800 | ℃
47833 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK31CP104 |  | 20HBK31CP104 | Side-A economiser outlet flue gas pressure | AI | -8 | 0.5 | kPa
47834 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-08 | KALTIM2.SIGNAL.AI.20HBK41CP104 |  | 20HBK41CP104 | Side-B economiser outlet flue gas pressure | AI | -8 | 0.5 | kPa
47835 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-02 | KALTIM2.SIGNAL.AI.20LAB50CP102 |  | 20LAB50CP102 | Economizer inlet water pressure | AI | 0 | 15 | MPa
47836 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER | K0102-23 | KALTIM2.SIGNAL.AI.20LBG21CP101 |  | 20LBG21CP101 | P OF THE STM FROM AUX STM TO ECONOMIZER START-UP BLOW | AI | 0 | 1.6 | MPa
47837 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.20GUB30CQ101 |  | 20GUB30CQ101 | Unit 2 Economizer import N2H4 | AI | 0 | 100
47838 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.20GUB30CQ102 |  | 20GUB30CQ102 | Unit 2 Economizer import PH | AI | 0 | 14
47839 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 9 | #2 ECONOMIZER |  | KALTIM 0.SIGNAL.AI.20GUB30CQ103 |  | 20GUB30CQ103 | Unit 2 Economizer import CC | AI | 0 | 20
47840 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AI.20HAN11AA101XQ12 |  | 20HAN11AA101XQ12 | Side-B drum continuous blowdown control valve position feedback | AI | 0 | 100 | %
47841 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AI.20HAN13AA101XQ12 |  | 20HAN13AA101XQ12 | Side-A drum continuous blowdown control valve position feedback | AI | 0 | 100 | %
47842 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AI.20LCQ20AA101XQ12 |  | 20LCQ20AA101XQ12 | Control valve for continuous blowdown flash tank to periodic blo | AI | 0 | 100 | %
47843 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AO.20HAN11AA101XQ11 |  | 20HAN11AA101XQ11 | Side-B drum continuous blowdown control valve control command | AO | 0 | 100 | %
47844 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AO.20HAN13AA101XQ11 |  | 20HAN13AA101XQ11 | Side-A drum continuous blowdown control valve control command | AO | 0 | 100 | %
47845 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AO.20LCQ20AA101XQ11 |  | 20LCQ20AA101XQ11 | Control valve for continuous blowdown flash tank to periodic blo | AO | 0 | 100 | %
47846 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT101 |  | 20HAD01CT101 | Drum wall temperature 1 | TC | 0 | 350 | °C
47847 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT102 |  | 20HAD01CT102 | Drum wall temperature 2 | TC | 0 | 350 | °C
47848 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT103 |  | 20HAD01CT103 | Drum wall temperature 3 | TC | 0 | 350 | °C
47849 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT104 |  | 20HAD01CT104 | Drum wall temperature 4 | TC | 0 | 350 | °C
47850 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT105 |  | 20HAD01CT105 | Drum wall temperature 5 | TC | 0 | 350 | °C
47851 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT106 |  | 20HAD01CT106 | Drum wall temperature 6 | TC | 0 | 350 | °C
47852 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT107 |  | 20HAD01CT107 | Drum wall temperature 7 | TC | 0 | 350 | °C
47853 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT108 |  | 20HAD01CT108 | Drum wall temperature 8 | TC | 0 | 350 | °C
47854 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT109 |  | 20HAD01CT109 | Drum wall temperature 9 | TC | 0 | 350 | °C
47855 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT110 |  | 20HAD01CT110 | Drum wall temperature 10 | TC | 0 | 350 | °C
47856 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT111 |  | 20HAD01CT111 | Drum wall temperature 11 | TC | 0 | 350 | °C
47857 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT112 |  | 20HAD01CT112 | Drum wall temperature 12 | TC | 0 | 350 | °C
47858 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT113 |  | 20HAD01CT113 | Wall temperature of guide pipe after balance container 1 | TC | 0 | 350 | ℃
47859 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT114 |  | 20HAD01CT114 | Wall temperature of guide pipe after balance container 2 | TC | 0 | 350 | ℃
47860 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.TC.20HAD01CT115 |  | 20HAD01CT115 | Wall temperature of guide pipe after balance container 3 | TC | 0 | 350 | ℃
47861 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-14 | KALTIM2.SIGNAL.AI.20LCQ20CL102 |  | 20LCQ20CL102 | Continuous blowdown flash tank water level | AI | 0 | 400 | mm
47862 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.U2AM12MCS02A05 |  | 20HAD01CL101 | Drum water level 1 | AI | -600 | 660 | mm |  | -280 | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
47863 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.U2AM12MCS02A06 |  | 20HAD01CL102 | Drum water level 2 | AI | -600 | 660 | mm |  | -280 | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
47864 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.U2AM12MCS02A07 |  | 20HAD01CL103 | Drum water level 3 | AI | -600 | 660 | mm |  | -280 | -50 | 50 | 125 | 200 |  |  |  | 0 | 1
47865 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.20HAD01CP101 |  | 20HAD01CP101 | Drum pressure 1 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
47866 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.20HAD01CP102 |  | 20HAD01CP102 | Drum pressure 2 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
47867 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM | K0102-02 | KALTIM2.SIGNAL.AI.20HAD01CP103 |  | 20HAD01CP103 | Drum pressure 3 | AI | 0 | 16 | MPa |  |  |  | 11 | [5 empty] | 1 | 1
47868 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.20GUE10CQ101 |  | 20GUE10CQ101 | Unit 2 Left/right side of Drum boiler water PH | AI | 0 | 14
47869 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.20GUE10CQ102 |  | 20GUE10CQ102 | Unit 2 Left/right side of Drum boiler water SC | AI | 0 | 200
47870 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 10 | #2 STEAM DRUM |  | KALTIM 0.SIGNAL.AI.20GUE10CQ103 |  | 20GUE10CQ103 | Unit 2 Left/right side of Drum boiler water SiO2 | AI | 0 | 100
47871 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF52AA101XQ12 |  | 20HDF52AA101XQ12 | A return material tank inlet control valve 1 position feedback | AI | 0 | 100 | %
47872 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF53AA101XQ12 |  | 20HDF53AA101XQ12 | A return material tank inlet control valve 2 position feedback | AI | 0 | 100 | %
47873 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AO.20HDF52AA101XQ11 |  | 20HDF52AA101XQ11 | A return material tank inlet control valve 1 control command | AO | 0 | 100 | %
47874 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AO.20HDF53AA101XQ11 |  | 20HDF53AA101XQ11 | A return material tank inlet control valve 2 control command | AO | 0 | 100 | %
47875 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT112 |  | 20HDF52CT112 | A cyclone separator lower wall temperature 6 | TC | 0 | 500 | °C
47876 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT101 |  | 20HDF52CT101 | A cyclone separator upper wall temperature 1 | TC | 0 | 500 | °C
47877 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT102 |  | 20HDF52CT102 | A cyclone separator upper wall temperature 2 | TC | 0 | 500 | °C
47878 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT103 |  | 20HDF52CT103 | A cyclone separator upper wall temperature 3 | TC | 0 | 500 | °C
47879 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT104 |  | 20HDF52CT104 | A cyclone separator upper wall temperature 4 | TC | 0 | 500 | °C
47880 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT105 |  | 20HDF52CT105 | A cyclone separator upper wall temperature 5 | TC | 0 | 500 | °C
47881 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT106 |  | 20HDF52CT106 | A cyclone separator upper wall temperature 6 | TC | 0 | 500 | °C
47882 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT107 |  | 20HDF52CT107 | A cyclone separator lower wall temperature 1 | TC | 0 | 500 | °C
47883 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT108 |  | 20HDF52CT108 | A cyclone separator lower wall temperature 2 | TC | 0 | 500 | °C
47884 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT109 |  | 20HDF52CT109 | A cyclone separator lower wall temperature 3 | TC | 0 | 500 | °C
47885 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT110 |  | 20HDF52CT110 | A cyclone separator lower wall temperature 4 | TC | 0 | 500 | °C
47886 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.TC.20HDF52CT111 |  | 20HDF52CT111 | A cyclone separator lower wall temperature 5 | TC | 0 | 500 | °C
47887 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.TC.20HDF11CT101 |  | 20HDF11CT101 | A cyclone separator inlet fule gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1
47888 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.TC.20HDF11CT102 |  | 20HDF11CT102 | A cyclone separator outlet fule gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1
47889 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.TC.20HDF11CT103 |  | 20HDF11CT103 | Side-A U valve outlet ash temperature | TC | 0 | 1200 | ℃
47890 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP104 |  | 20HDF11CP104 | Side-A U valve outlet pressure (LP) | AI | 0 | 59 | kPa
47891 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP106 |  | 20HDF11CP106 | Side-A U valve outlet pressure (HP) | AI | 0 | 70 | kPa
47892 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF52CP101 |  | 20HDF52CP101 | Side-A U valve bed pressure | AI | 0 | 20 | KPa
47893 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF52CP102 |  | 20HDF52CP102 | Side-A U valve chamber air pressure 1 | AI | 0 | 60 | kPa
47894 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-06 | KALTIM2.SIGNAL.AI.20HDF52CP103 |  | 20HDF52CP103 | Side-A U valve chamber air pressure 2 | AI | 0 | 60 | kPa
47895 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CD101 |  | 20HDF11CD101 | Side-A U valve density | AI | -60 | 60 | kPa
47896 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP101 |  | 20HDF11CP101 | A cyclone separator differential pressure between outlet and inl | AI | -5 | 11 | kPa
47897 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP102 |  | 20HDF11CP102 | A cyclone separator outlet fule gas pressure | AI | -7 | 1 | kPa
47898 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP103 |  | 20HDF11CP103 | Side-A U valve inlet pressure | AI | -5 | 5 | kPa
47899 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 11 | #2 CYCLONE A | K0102-08 | KALTIM2.SIGNAL.AI.20HDF11CP105 |  | 20HDF11CP105 | Side-A U valve sealing height | AI | -50 | 60 | kPa |  |  |  | 60 | [5 empty] | 1
47900 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF44AA101XQ12 |  | 20HDF44AA101XQ12 | B return material tank inlet control valve 1 position feedback | AI | 0 | 100 | %
47901 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF45AA101XQ12 |  | 20HDF45AA101XQ12 | B return material tank inlet control valve 2 position feedback | AI | 0 | 100 | %
47902 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AO.20HDF44AA101XQ11 |  | 20HDF44AA101XQ11 | B return material tank inlet control valve 1 control command | AO | 0 | 100 | %
47903 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AO.20HDF45AA101XQ11 |  | 20HDF45AA101XQ11 | B return material tank inlet control valve 2 control command | AO | 0 | 100 | %
47904 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT101 |  | 20HDF44CT101 | B cyclone separator upper wall temperature 1 | TC | 0 | 500 | °C
47905 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT102 |  | 20HDF44CT102 | B cyclone separator upper wall temperature 2 | TC | 0 | 500 | °C
47906 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT103 |  | 20HDF44CT103 | B cyclone separator upper wall temperature 3 | TC | 0 | 500 | °C
47907 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT104 |  | 20HDF44CT104 | B cyclone separator upper wall temperature 4 | TC | 0 | 500 | °C
47908 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT105 |  | 20HDF44CT105 | B cyclone separator upper wall temperature 5 | TC | 0 | 500 | °C
47909 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT106 |  | 20HDF44CT106 | B cyclone separator upper wall temperature 6 | TC | 0 | 500 | °C
47910 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT107 |  | 20HDF44CT107 | B cyclone separator lower wall temperature 1 | TC | 0 | 500 | °C
47911 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT108 |  | 20HDF44CT108 | B cyclone separator lower wall temperature 2 | TC | 0 | 500 | °C
47912 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT109 |  | 20HDF44CT109 | B cyclone separator lower wall temperature 3 | TC | 0 | 500 | °C
47913 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT110 |  | 20HDF44CT110 | B cyclone separator lower wall temperature 4 | TC | 0 | 500 | °C
47914 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT111 |  | 20HDF44CT111 | B cyclone separator lower wall temperature 5 | TC | 0 | 500 | °C
47915 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.TC.20HDF44CT112 |  | 20HDF44CT112 | B cyclone separator lower wall temperature 6 | TC | 0 | 500 | °C
47916 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.TC.20HDF21CT101 |  | 20HDF21CT101 | B cyclone separator inlet flue gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1
47917 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.TC.20HDF21CT102 |  | 20HDF21CT102 | B cyclone separator outlet flue gas temperature | TC | 0 | 1200 | ℃ |  |  |  | 980 | [5 empty] | 1
47918 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.TC.20HDF21CT103 |  | 20HDF21CT103 | Side-B U valve outlet ash temperature | TC | 0 | 1200 | ℃
47919 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF44CP101 |  | 20HDF44CP101 | Side-B U valve bed pressure | AI | 0 | 80 | kPa
47920 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF44CP102 |  | 20HDF44CP102 | Side-B U valve chamber air pressure 1 | AI | 0 | 60 | kPa
47921 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF44CP103 |  | 20HDF44CP103 | Side-B U valve chamber air pressure 2 | AI | 0 | 60 | kPa
47922 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CD101 |  | 20HDF21CD101 | Side-B U valve density | AI | -60 | 60 | kPa
47923 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP101 |  | 20HDF21CP101 | B cyclone separator differential pressure between outlet and inl | AI | -5 | 11 | kPa
47924 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP102 |  | 20HDF21CP102 | B cyclone separator outlet fule gas pressure | AI | -7 | 1 | kPa
47925 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP103 |  | 20HDF21CP103 | Side-B U valve inlet pressure | AI | -5 | 5 | kPa
47926 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP104 |  | 20HDF21CP104 | Side-B U valve outlet pressure (LP) | AI | 0 | 59 | kPa
47927 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP105 |  | 20HDF21CP105 | Side-B U valve sealing height | AI | -50 | 60 | kPa |  |  |  | 60 | [5 empty] | 1
47928 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-08 | KALTIM2.SIGNAL.AI.20HDF21CP106 |  | 20HDF21CP106 | Side-B U valve outlet pressure (HP) | AI | 0 | 70 | kPa
47929 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF44CF101 |  | 20HDF44CF101 | B return material tank inlet air flow 1 | AI | 0 | 100 | Nm3/h
47930 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF45CF101 |  | 20HDF45CF101 | B return material tank inlet air flow 2 | AI | 0 | 999999 | Nm3/h
47931 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF46CF101 |  | 20HDF46CF101 | B return material tank inlet air flow 3 | AI | 0 | 999999 | Nm3/h
47932 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF47CF101 |  | 20HDF47CF101 | B return material tank inlet air flow 4 | AI | 0 | 999999 | Nm3/h
47933 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 12 | #2 CYCLONE B | K0102-06 | KALTIM2.SIGNAL.AI.20HDF48CF101 |  | 20HDF48CF101 | B return material tank inlet air flow 5 | AI | 0 | 999999 | Nm3/h
47934 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AI.20HCB10AA101XQ12 |  | 20HCB10AA101XQ12 | POSITION (Pressure Reduction Station) | AI | 0 | 100 | %
47935 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AO.20HCB10AA101XQ11 |  | 20HCB10AA101XQ11 | LOCALIZER (Pressure Reduction Station) | AO | 0 | 100 | %
47936 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AI.20HCB10XQ01 |  | 20HCB10XQ01 | VALVE WORKING CURRENT | AI | 0 | 10 | A
47937 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AI.20HCB11XQ01 |  | 20HCB11XQ01 | KR/ER GROUP WORKING CURRENT | AI | 0 | 10 | A
47938 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AI.20HCB12XQ01 |  | 20HCB12XQ01 | KL/EL GROUP WORKING CURRENT | AI | 0 | 10 | A
47939 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 13 | #2 SOOT BLOWER | K0102-15 | KALTIM2.SIGNAL.AI.20HCB10CP101 |  | 20HCB10CP101 | PRESSURE (Pressure Reduction Station) | AI | 0 | 100 | MPa
47940 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL03AA102XQ12 |  | 20HHL03AA102XQ12 | B air duct ignitor inlet motor-driven control damper 2 position | AI | 0 | 100 | %
47941 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL21AA101XQ12 |  | 20HHL21AA101XQ12 | Side-B front upper secondary air inlet control valve position fe | AI | 0 | 100 | %
47942 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL02AA102XQ12 |  | 20HHL02AA102XQ12 | A air duct ignitor inlet motor-driven control damper 2 position | AI | 0 | 100 | %
47943 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL02AA101XQ12 |  | 20HHL02AA101XQ12 | A air duct ignitor inlet motor-driven control damper 1 position | AI | 0 | 100 | %
47944 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL02AA103XQ12 |  | 20HHL02AA103XQ12 | A air duct ignitor inlet motor-driven control damper 3 position | AI | 0 | 100 | %
47945 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL03AA101XQ12 |  | 20HHL03AA101XQ12 | B air duct ignitor inlet motor-driven control damper 1 position | AI | 0 | 100 | %
47946 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL03AA103XQ12 |  | 20HHL03AA103XQ12 | B air duct ignitor inlet motor-driven control damper 3 position | AI | 0 | 100 | %
47947 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL05AA101XQ12 |  | 20HHL05AA101XQ12 | Front wall upper bed burner hot primary air control damper 1 pos | AI | 0 | 100 | %
47948 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL05AA102XQ12 |  | 20HHL05AA102XQ12 | Front wall upper bed burner hot primary air control damper 2 pos | AI | 0 | 100 | %
47949 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL06AA101XQ12 |  | 20HHL06AA101XQ12 | Back wall upper bed burner hot primary air control damper 1 posi | AI | 0 | 100 | %
47950 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL06AA102XQ12 |  | 20HHL06AA102XQ12 | Back wall upper bed burner hot primary air control damper 2 posi | AI | 0 | 100 | %
47951 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL11AA101XQ12 |  | 20HHL11AA101XQ12 | Side-A front upper secondary air inlet control valve position fe | AI | 0 | 100 | %
47952 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL12AA101XQ12 |  | 20HHL12AA101XQ12 | Side-A back upper secondary air inlet control valve position fee | AI | 0 | 100 | %
47953 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL13AA101XQ12 |  | 20HHL13AA101XQ12 | Side-A front lower secondary air inlet control valve position fe | AI | 0 | 100 | %
47954 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL14AA101XQ12 |  | 20HHL14AA101XQ12 | Side-A back lower secondary air inlet control valve position fee | AI | 0 | 100 | %
47955 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL22AA101XQ12 |  | 20HHL22AA101XQ12 | Side-B back upper secondary air inlet control valve position fee | AI | 0 | 100 | %
47956 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL23AA101XQ12 |  | 20HHL23AA101XQ12 | Side-B front lower secondary air inlet control valve position fe | AI | 0 | 100 | %
47957 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL24AA101XQ12 |  | 20HHL24AA101XQ12 | Side-B back lower secondary air inlet control valve position fee | AI | 0 | 100 | %
47958 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL02AA101XQ11 |  | 20HHL02AA101XQ11 | A air duct ignitor inlet motor-driven control damper 1 control c | AO | 0 | 100 | %
47959 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL02AA102XQ11 |  | 20HHL02AA102XQ11 | A air duct ignitor inlet motor-driven control damper 2 control c | AO | 0 | 100 | %
47960 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL02AA103XQ11 |  | 20HHL02AA103XQ11 | A air duct ignitor inlet motor-driven control damper 3 control c | AO | 0 | 100 | %
47961 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL03AA101XQ11 |  | 20HHL03AA101XQ11 | B air duct ignitor inlet motor-driven control damper 1 control c | AO | 0 | 100 | %
47962 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL03AA102XQ11 |  | 20HHL03AA102XQ11 | B air duct ignitor inlet motor-driven control damper 2 control c | AO | 0 | 100 | %
47963 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL03AA103XQ11 |  | 20HHL03AA103XQ11 | B air duct ignitor inlet motor-driven control damper 3 control c | AO | 0 | 100 | %
47964 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL05AA101XQ11 |  | 20HHL05AA101XQ11 | Front wall upper bed burner hot primary air control damper 1 con | AO | 0 | 100 | %
47965 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL05AA102XQ11 |  | 20HHL05AA102XQ11 | Front wall upper bed burner hot primary air control damper 2 con | AO | 0 | 100 | %
47966 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL06AA101XQ11 |  | 20HHL06AA101XQ11 | Back wall upper bed burner hot primary air control damper 1 cont | AO | 0 | 100 | %
47967 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AO.20HHL06AA102XQ11 |  | 20HHL06AA102XQ11 | Back wall upper bed burner hot primary air control damper 2 cont | AO | 0 | 100 | %
47968 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL11AA101XQ11 |  | 20HHL11AA101XQ11 | Side-A front upper secondary air inlet control valve control com | AO | 0 | 100 | %
47969 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL12AA101XQ11 |  | 20HHL12AA101XQ11 | Side-A back upper secondary air inlet control valve control comm | AO | 0 | 100 | %
47970 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL13AA101XQ11 |  | 20HHL13AA101XQ11 | Side-A front lower secondary air inlet control valve control com | AO | 0 | 100 | %
47971 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL14AA101XQ11 |  | 20HHL14AA101XQ11 | Side-A back lower secondary air inlet control valve control comm | AO | 0 | 100 | %
47972 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL21AA101XQ11 |  | 20HHL21AA101XQ11 | Side-B front upper secondary air inlet control valve control com | AO | 0 | 100 | %
47973 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL22AA101XQ11 |  | 20HHL22AA101XQ11 | Side-B back upper secondary air inlet control valve control comm | AO | 0 | 100 | %
47974 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL23AA101XQ11 |  | 20HHL23AA101XQ11 | Side-B front lower secondary air inlet control valve control com | AO | 0 | 100 | %
47975 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AO.20HHL24AA101XQ11 |  | 20HHL24AA101XQ11 | Side-B back lower secondary air inlet control valve control comm | AO | 0 | 100 | %
47976 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.RTD.20HHL20CT101 |  | 20HHL20CT101 | Side-B hot secondary air temperature | RTD | 0 | 300 | ℃
47977 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT101 |  | 20HBK11CT101 | Side-A furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950 | [5 empty] | 1
47978 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT102 |  | 20HBK11CT102 | Side-A furnace internal temperature 1 | TC | 0 | 1200 | ℃
47979 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT103 |  | 20HBK11CT103 | Side-A furnace internal temperature 2 | TC | 0 | 1200 | ℃
47980 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT104 |  | 20HBK11CT104 | Side-A furnace internal temperature 3 | TC | 0 | 1200 | ℃
47981 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT105 |  | 20HBK11CT105 | Side-A furnace internal temperature 4 | TC | 0 | 1200 | ℃
47982 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT106 |  | 20HBK11CT106 | A start-up burner outlet flue gas temperature | TC | 0 | 2000 | ℃ |  |  |  | 980 | [5 empty] | 1
47983 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK11CT107 |  | 20HBK11CT107 | Side-A furnace air chamber inlet duct temperature | TC | 0 | 1500 | ℃
47984 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT101 |  | 20HBK21CT101 | Side-B furnace outlet temperature | TC | 0 | 1200 | ℃ |  |  |  | 950 | [5 empty] | 1
47985 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT102 |  | 20HBK21CT102 | Side-B furnace internal temperature 1 | TC | 0 | 1200 | ℃
47986 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT103 |  | 20HBK21CT103 | Side-B furnace internal temperature 2 | TC | 0 | 1200 | ℃
47987 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT104 |  | 20HBK21CT104 | Side-B furnace internal temperature 3 | TC | 0 | 1200 | ℃
47988 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT105 |  | 20HBK21CT105 | Side-B furnace internal temperature 4 | TC | 0 | 1200 | ℃
47989 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT106 |  | 20HBK21CT106 | B start-up burner outlet flue gas temperature | TC | 0 | 2000 | ℃ |  |  |  | 980 | [5 empty] | 1
47990 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK21CT107 |  | 20HBK21CT107 | Side-B furnace air chamber inlet duct temperature | TC | 0 | 1500 | ℃
47991 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT101 |  | 20HBK30CT101 | Boiler front wall burning chamber bed temperature 1 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47992 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT102 |  | 20HBK30CT102 | Boiler front wall burning chamber bed temperature 2 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47993 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT103 |  | 20HBK30CT103 | Boiler front wall burning chamber bed temperature 3 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47994 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT104 |  | 20HBK30CT104 | Boiler front wall burning chamber bed temperature 4 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47995 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT105 |  | 20HBK30CT105 | Boiler front wall burning chamber bed temperature 5 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47996 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT106 |  | 20HBK30CT106 | Boiler front wall burning chamber bed temperature 6 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47997 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT107 |  | 20HBK30CT107 | Boiler front wall burning chamber bed temperature 7 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47998 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK30CT108 |  | 20HBK30CT108 | Boiler front wall burning chamber bed temperature 8 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
47999 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK40CT101 |  | 20HBK40CT101 | Boiler back wall burning chamber bed temperature 1 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
48000 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK40CT102 |  | 20HBK40CT102 | Boiler back wall burning chamber bed temperature 2 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
48001 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK40CT103 |  | 20HBK40CT103 | Boiler back wall burning chamber bed temperature 3 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
48002 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.TC.20HBK40CT104 |  | 20HBK40CT104 | Boiler back wall burning chamber bed temperature 4 | TC | 0 | 1100 | ℃ |  |  |  | 760 | 990 |  |  |  |  | 1 | 1
48003 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP103 |  | 20HBK11CP103 | Side-A furnace middle pressure | AI | 0 | 2 | kPa
48004 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP103 |  | 20HBK21CP103 | Side-B furnace middle pressure | AI | 0 | 2 | kPa
48005 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP107 |  | 20HBK11CP107 | Side-A furnace bed pressure 2 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48006 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL02CP101 |  | 20HHL02CP101 | Furnace air chamber pressure 1 | AI | 0 | 20 | kPa
48007 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL03CP101 |  | 20HHL03CP101 | Furnace air chamber pressure 2 | AI | 0 | 20 | kPa
48008 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL11CP101 |  | 20HHL11CP101 | Upper secondary air box pressure | AI | 0 | 15 | kPa
48009 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL13CP101 |  | 20HHL13CP101 | Lower secondary air box pressure | AI | 0 | 15 | kPa
48010 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL20CP101 |  | 20HHL20CP101 | Side-B hot secondary air pressure | AI | 0 | 15 | kPa
48011 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL21CP101 |  | 20HHL21CP101 | Upper secondary air box pressure | AI | 0 | 15 | kPa
48012 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL23CP101 |  | 20HHL23CP101 | Lower secondary air box pressure | AI | 0 | 15 | kPa
48013 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP105 |  | 20HBK11CP105 | Side-A furnace bed pressure 3 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48014 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP106 |  | 20HBK11CP106 | Side-A furnace bed pressure 1 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48015 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP108 |  | 20HBK11CP108 | Side-A furnace air chamber inlet duct pressure | AI | 0 | 25 | kPa
48016 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP105 |  | 20HBK21CP105 | Side-B furnace bed pressure 1 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48017 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP106 |  | 20HBK21CP106 | Side-B furnace bed pressure 3 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48018 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP107 |  | 20HBK21CP107 | Side-B furnace bed pressure 2 | AI | 0 | 12 | kPa |  |  | 4 | [6 empty] | 2 | 1
48019 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP108 |  | 20HBK21CP108 | Side-B furnace air chamber inlet duct pressure | AI | 0 | 25 | kPa
48020 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL02CF101 |  | 20HHL02CF101 | A air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
48021 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL03CF101 |  | 20HHL03CF101 | B air duct ignitor inlet hot primary air flow | AI | 0 | 999999 | Nm3/h
48022 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL21CF101 |  | 20HHL21CF101 | Side-B front upper secondary air flow | AI | 0 | 999999 | Nm3/h
48023 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL22CF101 |  | 20HHL22CF101 | Side-B back upper secondary air flow | AI | 0 | 999999 | Nm3/h
48024 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL23CF101 |  | 20HHL23CF101 | Side-B front lower secondary air flow | AI | 0 | 999999 | Nm3/h
48025 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL24CF101 |  | 20HHL24CF101 | Side-B back lower secondary air flow | AI | 0 | 999999 | Nm3/h
48026 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP401 |  | 20HBK11CP401 | Side-A furnace lower pressure | AI | 0 | 5000 | Pa | [10 empty] | 1
48027 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP401 |  | 20HBK21CP401 | Side-B furnace lower pressure | AI | 0 | 5000 | Pa | [10 empty] | 1
48028 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP101 |  | 20HBK11CP101 | Side-A furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000 | [5 empty] | 1
48029 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK11CP102 |  | 20HBK11CP102 | Side-A furnace differencial pressure | AI | -500 | 4000 | Pa | [10 empty] | 1
48030 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP101 |  | 20HBK21CP101 | Side-B furnace upper pressure | AI | -4000 | 4000 | Pa |  |  |  |  | 3000 | [5 empty] | 1
48031 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE | K0102-07 | KALTIM2.SIGNAL.AI.20HBK21CP102 |  | 20HBK21CP102 | Side-B furnace differencial pressure | AI | -500 | 4000 | Pa | [10 empty] | 1
49124 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 14 | #2 FURNACE |  | 20HBK11CT902 |  | 20HBK11CT902 | Boiler Bed Temperature | CALC | 0 | 1200 | ℃ | [8 empty] | AVG((KALTIM2.SIGNAL.TC.20HBK11CT102);( KALTIM2.SIGNAL.TC.20HBK11CT103);( KALTIM2.SIGNAL.TC.20HBK11CT104);( KALTIM2.SIGNAL.TC.20HBK11CT105);( KALTIM2.SIGNAL.TC.20HBK21CT102);( KALTIM2.SIGNAL.TC.20HBK21CT103);( KALTIM2.SIGNAL.TC.20HBK21CT104);( KALTIM2.SIGNAL.TC.20HBK21CT105))
48032 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJA21CB101 |  | 20HJA21CB101 | A lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
48033 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJA21CB102 |  | 20HJA21CB102 | A lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
48034 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJA21CB103 |  | 20HJA21CB103 | A lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
48036 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20AA101XQ12 |  | 20HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
48038 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AO.20HJS20AA101XQ11 |  | 20HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
48039 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.TC.20HJS20CT101 |  | 20HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
48041 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP102 |  | 20HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
48042 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJF20CP102 |  | 20HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
48043 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20CP101 |  | 20HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
48047 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP101 |  | 20HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
49010 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJF20CP102 |  | 20HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
49011 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP101 |  | 20HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
49012 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP102 |  | 20HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
49013 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AO.20HJS20AA101XQ11 |  | 20HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
49014 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20AA101XQ12 |  | 20HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
49015 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20CP101 |  | 20HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
49016 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.TC.20HJS20CT101 |  | 20HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
49020 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJF20CP102 |  | 20HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
49021 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP101 |  | 20HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
49022 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP102 |  | 20HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
49023 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AO.20HJS20AA101XQ11 |  | 20HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
49024 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20AA101XQ12 |  | 20HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
49025 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20CP101 |  | 20HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
49026 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.TC.20HJS20CT101 |  | 20HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
49030 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJF20CP102 |  | 20HJF20CP102 | Lower bed igniting oil main pipe pressure | AI | 0 | 3 | MPa
49031 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP101 |  | 20HJL20CP101 | Left lower bed oil gun flame detecting cooling air main pipe pre | AI | 0 | 0.1 | MPa
49032 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJL20CP102 |  | 20HJL20CP102 | Right lower bed oil gun flame detecting cooling air main pipe pr | AI | 0 | 0.1 | MPa
49033 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AO.20HJS20AA101XQ11 |  | 20HJS20AA101XQ11 | Lower bed purging steam inlet control valve control command | AO | 0 | 100 | %
49034 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20AA101XQ12 |  | 20HJS20AA101XQ12 | Lower bed purging steam inlet control valve position feedback | AI | 0 | 100 | %
49035 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.AI.20HJS20CP101 |  | 20HJS20CP101 | Lower bed purging steam inlet pressure | AI | 0 | 2.5 | MPa
49036 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 15 | #2 LOWER BURNER A | K0102-13 | KALTIM2.SIGNAL.TC.20HJS20CT101 |  | 20HJS20CT101 | Lower bed purging steam inlet temperature | TC | 0 | 300 | ℃
48044 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 16 | #2 LOWER BURNER B | K0102-13 | KALTIM2.SIGNAL.AI.20HJA22CB101 |  | 20HJA22CB101 | B lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
48045 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 16 | #2 LOWER BURNER B | K0102-13 | KALTIM2.SIGNAL.AI.20HJA22CB102 |  | 20HJA22CB102 | B lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
48046 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 16 | #2 LOWER BURNER B | K0102-13 | KALTIM2.SIGNAL.AI.20HJA22CB103 |  | 20HJA22CB103 | B lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
48048 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 17 | #2 LOWER BURNER C | K0102-13 | KALTIM2.SIGNAL.AI.20HJA23CB101 |  | 20HJA23CB101 | C lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
48049 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 17 | #2 LOWER BURNER C | K0102-13 | KALTIM2.SIGNAL.AI.20HJA23CB103 |  | 20HJA23CB103 | C lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
48050 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 17 | #2 LOWER BURNER C | K0102-13 | KALTIM2.SIGNAL.AI.20HJA23CB102 |  | 20HJA23CB102 | C lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
48051 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 18 | #2 LOWER BURNER D | K0102-13 | KALTIM2.SIGNAL.AI.20HJA24CB101 |  | 20HJA24CB101 | D lower igniting burner #1 flame detector flame intensity | AI | 0 | 100 | %
48052 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 18 | #2 LOWER BURNER D | K0102-13 | KALTIM2.SIGNAL.AI.20HJA24CB102 |  | 20HJA24CB102 | D lower igniting burner #2 flame detector flame intensity | AI | 0 | 100 | %
48053 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | 18 | #2 LOWER BURNER D | K0102-13 | KALTIM2.SIGNAL.AI.20HJA24CB103 |  | 20HJA24CB103 | D lower igniting burner #3 flame detector flame intensity | AI | 0 | 100 | %
48872 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 FURNACE | K0102-04 | KALTIM2.SIGNAL.AI.20HHL04CF101 |  | 20HHL04CF101 | Upper bed burner hot primary air flow | AI | 0 | 999999 | Nm3/h
48873 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL11CF101 |  | 20HHL11CF101 | Side-A front upper secondary air flow | AI | 0 | 999999 | Nm3/h
48874 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL12CF101 |  | 20HHL12CF101 | Side-A back upper secondary air flow | AI | 0 | 999999 | Nm3/h
48875 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL13CF101 |  | 20HHL13CF101 | Side-A front lower secondary air flow | AI | 0 | 999999 | Nm3/h
48876 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 FURNACE | K0102-05 | KALTIM2.SIGNAL.AI.20HHL14CF101 |  | 20HHL14CF101 | Side-A back lower secondary air flow | AI | 0 | 999999 | Nm3/h
48877 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 LTSH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE22CF101 |  | 20LAE22CF101 | Side-B primary desuperheater water flow | AI | 0 | 100 | t/h
48878 | 2 | UJKTT #2 | 2 | #2 BOILER SYSTEM | #N/A | #2 PLATEN SH | K0102-03 | KALTIM2.SIGNAL.AI.20LAE24CF101 |  | 20LAE24CF101 | Side-B secondary desuperheater water flow | AI | 0 | 999999 | t/h
48054 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 1 | #2 COAL BUNKER A | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA10CL101 |  | 20HFA10CL101 | #2 Boiler A coal hopper level | AI | 0 | 100
48055 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 2 | #2 COAL BUNKER B | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA20CL101 |  | 20HFA20CL101 | #2 Boiler B coal hopper level | AI | 0 | 100
48056 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 3 | #2 COAL BUNKER C | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA30CL101 |  | 20HFA30CL101 | #2 Boiler C coal hopper level | AI | 0 | 100
48057 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 4 | #2 COAL BUNKER D | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA40CL101 |  | 20HFA40CL101 | #2 Boiler D coal hopper level | AI | 0 | 100
48058 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 5 | #2 COAL BUNKER E | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA50CL101 |  | 20HFA50CL101 | #2 Boiler E coal hopper level | AI | 0 | 100
48059 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 6 | #2 COAL BUNKER F | K0102-10 | KALTIM 0.SIGNAL.AI.20HFA60CL101 |  | 20HFA60CL101 | #2 Boiler F coal hopper level | AI | 0 | 100
48060 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-10 | KALTIM2.SIGNAL.AI.20HFB10AF001XQ01 |  | 20HFB10AF001XQ01 | A coal feeder speed feedback | AI | 0 | 100 | %
48061 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-10 | KALTIM2.SIGNAL.AO.20HFB10AF001XQ11 |  | 20HFB10AF001XQ11 | A coal feeder speed control | AO | 0 | 100 | %
48062 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
48063 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW11CF101 |  | 20HEW11CF101 | A coal feeder seal air flow | AI | 0 | 999999 | m3/h
48064 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE11CF101 |  | 20HFE11CF101 | A inlet coal spreading air flow (lower) | AI | 0 | 9999 | m3/h
48065 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE12CF101 |  | 20HFE12CF101 | A inlet coal spreading air flow (upper) | AI | 0 | 9999 | m3/h
48066 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-10 | KALTIM2.SIGNAL.AI.20HFB10AF001XQ02 |  | 20HFB10AF001XQ02 | A coal feeder flow feedback | AI | 0 | 30 | t/h
49042 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49043 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49044 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49045 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
49046 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 7 | #2 COAL FEEDER A | K0102-04 | KALTIM2.SIGNAL.AI.20HEW10CP101 |  | 20HEW10CP101 | Coal feeder main seal air pipe pressure | AI | 0 | 25 | kPa
48067 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-10 | KALTIM2.SIGNAL.AI.20HFB20AF001XQ01 |  | 20HFB20AF001XQ01 | B coal feeder speed feedback | AI | 0 | 100 | %
48068 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-10 | KALTIM2.SIGNAL.AO.20HFB20AF001XQ11 |  | 20HFB20AF001XQ11 | B coal feeder speed control | AO | 0 | 100 | %
48069 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-04 | KALTIM2.SIGNAL.AI.20HEW12CF101 |  | 20HEW12CF101 | B coal feeder seal air flow | AI | 0 | 999999 | m3/h
48070 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE21CF101 |  | 20HFE21CF101 | B inlet coal spreading air flow (lower) | AI | 0 | 9999 | m3/h
48071 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE22CF101 |  | 20HFE22CF101 | B inlet coal spreading air flow (upper) | AI | 0 | 9999 | m3/h
48072 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 8 | #2 COAL FEEDER B | K0102-10 | KALTIM2.SIGNAL.AI.20HFB20AF001XQ02 |  | 20HFB20AF001XQ02 | B coal feeder flow feedback | AI | 0 | 30 | t/h
48073 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 9 | #2 COAL FEEDER C | K0102-10 | KALTIM2.SIGNAL.AI.20HFB30AF001XQ01 |  | 20HFB30AF001XQ01 | C coal feeder speed feedback | AI | 0 | 100 | %
48074 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 9 | #2 COAL FEEDER C | K0102-10 | KALTIM2.SIGNAL.AI.20HFB30AF001XQ02 |  | 20HFB30AF001XQ02 | C coal feeder flow feedback | AI | 0 | 30 | t/h
48077 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 9 | #2 COAL FEEDER C | K0102-10 | KALTIM2.SIGNAL.AO.20HFB30AF001XQ11 |  | 20HFB30AF001XQ11 | C coal feeder speed control | AO | 0 | 100 | %
48075 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-10 | KALTIM2.SIGNAL.AI.20HFB40AF001XQ01 |  | 20HFB40AF001XQ01 | D coal feeder speed feedback | AI | 0 | 100 | %
48076 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-10 | KALTIM2.SIGNAL.AI.20HFB40AA002XQ12 |  | 20HFB40AA002XQ12 | D Coal Feeder Outlet Valve Feedback | AI | 0 | 100 | %
48078 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-10 | KALTIM2.SIGNAL.AO.20HFB40AF001XQ11 |  | 20HFB40AF001XQ11 | D coal feeder speed control | AO | 0 | 100 | %
48079 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-04 | KALTIM2.SIGNAL.AI.20HEW14CF101 |  | 20HEW14CF101 | D coal feeder seal air flow | AI | 0 | 999999 | m3/h
48080 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-04 | KALTIM2.SIGNAL.AI.20HFE41CF101 |  | 20HFE41CF101 | D inlet coal spreading air flow (lower) | AI | 0 | 10000 | m3/h
48081 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-04 | KALTIM2.SIGNAL.AI.20HFE42CF101 |  | 20HFE42CF101 | D inlet coal spreading air flow (upper) | AI | 0 | 9999 | m3/h
48082 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 10 | #2 COAL FEEDER D | K0102-10 | KALTIM2.SIGNAL.AI.20HFB40AF001XQ02 |  | 20HFB40AF001XQ02 | D coal feeder flow feedback | AI | 0 | 30 | t/h
48083 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-10 | KALTIM2.SIGNAL.AI.20HFB50AF001XQ01 |  | 20HFB50AF001XQ01 | E coal feeder speed feedback | AI | 0 | 100 | %
48084 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-10 | KALTIM2.SIGNAL.AI.20HFB50AA002XQ12 |  | 20HFB50AA002XQ12 | E Coal Feeder outlet valve feedback | AI | 0 | 100 | %
48085 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-10 | KALTIM2.SIGNAL.AO.20HFB50AF001XQ11 |  | 20HFB50AF001XQ11 | E coal feeder speed control | AO | 0 | 100 | %
48086 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-04 | KALTIM2.SIGNAL.AI.20HEW15CF101 |  | 20HEW15CF101 | E coal feeder seal air flow | AI | 0 | 999999 | m3/h
48087 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-04 | KALTIM2.SIGNAL.AI.20HFE51CF101 |  | 20HFE51CF101 | E inlet coal spreading air flow (lower) | AI | 0 | 9999 | m3/h
48088 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-04 | KALTIM2.SIGNAL.AI.20HFE52CF101 |  | 20HFE52CF101 | E inlet coal spreading air flow (upper) | AI | 0 | 40000 | m3/h
48089 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 11 | #2 COAL FEEDER E | K0102-10 | KALTIM2.SIGNAL.AI.20HFB50AF001XQ02 |  | 20HFB50AF001XQ02 | E coal feeder flow feedback | AI | 0 | 30 | t/h
48090 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 12 | #2 COAL FEEDER F | K0102-10 | KALTIM2.SIGNAL.AI.20HFB60AF001XQ01 |  | 20HFB60AF001XQ01 | F coal feeder speed feedback | AI | 0 | 100 | %
48091 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 12 | #2 COAL FEEDER F | K0102-10 | KALTIM2.SIGNAL.AI.20HFB60AA002XQ12 |  | 20HFB60AA002XQ12 | F Coal Feeder outlet valve feedback | AI | 0 | 100 | %
48092 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 12 | #2 COAL FEEDER F | K0102-10 | KALTIM2.SIGNAL.AO.20HFB60AF001XQ11 |  | 20HFB60AF001XQ11 | F coal feeder speed control | AO | 0 | 100 | %
48093 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 12 | #2 COAL FEEDER F | K0102-10 | KALTIM2.SIGNAL.AI.20HFB60AF001XQ02 |  | 20HFB60AF001XQ02 | F coal feeder flow feedback | AI | 0 | 30 | t/h
48094 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE10AA101XQ12 |  | 20HFE10AA101XQ12 | A coal spreading booster fan inlet control damper position feedb | AI | 0 | 100 | %
48095 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AO.20HFE10AA101XQ11 |  | 20HFE10AA101XQ11 | A coal spreading booster fan inlet control damper control comman | AO | 0 | 100 | %
48096 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE10AN001XQ01 |  | 20HFE10AN001XQ01 | A coal spreading booster fan current | AI | 0 | 75 | A
48097 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT102 |  | 20HFE10CT102 | A coal spreading booster fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48098 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT101 |  | 20HFE10CT101 | A coal spreading booster fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48099 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT103 |  | 20HFE10CT103 | A coal spreading booster fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48100 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT104 |  | 20HFE10CT104 | A coal spreading booster fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48101 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT105 |  | 20HFE10CT105 | A coal spreading booster fan motor stator temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
48102 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT106 |  | 20HFE10CT106 | A coal spreading booster fan motor stator temperature 2 | RTD | 0 | 100 | ℃ | [10 empty] | 1
48103 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT107 |  | 20HFE10CT107 | A coal spreading booster fan motor stator temperature 3 | RTD | 0 | 100 | ℃ | [10 empty] | 1
48104 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT108 |  | 20HFE10CT108 | A coal spreading booster fan motor stator temperature 4 | RTD | 0 | 100 | ℃ | [10 empty] | 1
48105 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT109 |  | 20HFE10CT109 | A coal spreading booster fan motor stator temperature 5 | RTD | 0 | 100 | ℃ | [10 empty] | 1
48106 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE10CT110 |  | 20HFE10CT110 | A coal spreading booster fan motor stator temperature 6 | RTD | 0 | 100 | ℃ | [10 empty] | 1
48107 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE10CP101 |  | 20HFE10CP101 | A coal spreading booster fan outlet pressure | AI | 0 | 50 | kPa
48108 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE30CP101 |  | 20HFE30CP101 | Coal spreading air main pipe pressure | AI | 0 | 50 | kPa
48109 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE10CY101 |  | 20HFE10CY101 | A coal spreading booster fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
48110 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE10CY102 |  | 20HFE10CY102 | A coal spreading booster fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
49048 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 13 | #2 CFB FAN A | K0102-04 | KALTIM2.SIGNAL.AI.20HFE30CP101 |  | 20HFE30CP101 | Coal spreading air main pipe pressure | AI | 0 | 50 | kPa
48111 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE20AA101XQ12 |  | 20HFE20AA101XQ12 | B coal spreading booster fan inlet control damper position feedb | AI | 0 | 100 | %
48112 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AO.20HFE20AA101XQ11 |  | 20HFE20AA101XQ11 | B coal spreading booster fan inlet control damper control comman | AO | 0 | 100 | %
48113 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE20AN001XQ01 |  | 20HFE20AN001XQ01 | B coal spreading booster fan current | AI | 0 | 75 | A
48114 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT101 |  | 20HFE20CT101 | B coal spreading booster fan bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48115 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT102 |  | 20HFE20CT102 | B coal spreading booster fan bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48116 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT103 |  | 20HFE20CT103 | B coal spreading booster fan motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48117 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT104 |  | 20HFE20CT104 | B coal spreading booster fan motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48118 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT105 |  | 20HFE20CT105 | B coal spreading booster fan motor stator temperature 1 | RTD | 0 | 200 | ℃ |  |  |  | 120 | 130 |  |  |  |  | 1 | 1
48119 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT106 |  | 20HFE20CT106 | B coal spreading booster fan motor stator temperature 2 | RTD | 0 | 200 | ℃ | [10 empty] | 1
48120 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT107 |  | 20HFE20CT107 | B coal spreading booster fan motor stator temperature 3 | RTD | 0 | 200 | ℃ | [10 empty] | 1
48121 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT108 |  | 20HFE20CT108 | B coal spreading booster fan motor stator temperature 4 | RTD | 0 | 200 | ℃ | [10 empty] | 1
48122 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT109 |  | 20HFE20CT109 | B coal spreading booster fan motor stator temperature 5 | RTD | 0 | 200 | ℃ | [10 empty] | 1
48123 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.RTD.20HFE20CT110 |  | 20HFE20CT110 | B coal spreading booster fan motor stator temperature 6 | RTD | 0 | 200 | ℃ | [10 empty] | 1
48124 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE20CP101 |  | 20HFE20CP101 | B coal spreading booster fan outlet pressure | AI | 0 | 50 | kPa
48125 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE20CY102 |  | 20HFE20CY102 | B coal spreading booster fan rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
48126 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | 14 | #2 CFB FAN B | K0102-04 | KALTIM2.SIGNAL.AI.20HFE20CY101 |  | 20HFE20CY101 | B coal spreading booster fan front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
48866 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER C | K0102-04 | KALTIM2.SIGNAL.AI.20HEW13CF101 |  | 20HEW13CF101 | C coal feeder seal air flow | AI | 0 | 4000 | m3/h
48867 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER F | K0102-04 | KALTIM2.SIGNAL.AI.20HEW16CF101 |  | 20HEW16CF101 | F coal feeder seal air flow | AI | 0 | 4000 | m3/h
48868 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER C | K0102-04 | KALTIM2.SIGNAL.AI.20HFE31CF101 |  | 20HFE31CF101 | C inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
48869 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER C | K0102-04 | KALTIM2.SIGNAL.AI.20HFE32CF101 |  | 20HFE32CF101 | C inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
48870 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER F | K0102-04 | KALTIM2.SIGNAL.AI.20HFE61CF101 |  | 20HFE61CF101 | F inlet coal spreading air flow (lower) | AI | 0 | 6000 | m3/h
48871 | 2 | UJKTT #2 | 3 | #2 COAL FEEDING SYSTEM | #N/A | #2 COAL FEEDER F | K0102-04 | KALTIM2.SIGNAL.AI.20HFE62CF101 |  | 20HFE62CF101 | F inlet coal spreading air flow (upper) | AI | 0 | 4000 | m3/h
48127 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20MK001XQ12 |  | 20LAC20MK001XQ12 | A EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
48128 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB21AA101XQ12 |  | 20LAB21AA101XQ12 | A EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
48129 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AO.20LAB21AA101XQ11 |  | 20LAB21AA101XQ11 | A EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
48130 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AO.20LAC20MK001XQ11 |  | 20LAC20MK001XQ11 | A EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
48131 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAC20AP001XQ01 |  | 20LAC20AP001XQ01 | A EFWP CURRENT | AI | 0 | 300 | A |  |  |  | 174 | [5 empty] | 1 | 1
48132 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB50CT101 |  | 20LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
48133 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT101 |  | 20LAC20CT101 | TEMP OF A EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48134 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT102 |  | 20LAC20CT102 | TEMP OF A EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48135 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT103 |  | 20LAC20CT103 | A EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48136 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT104 |  | 20LAC20CT104 | A EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48137 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT105 |  | 20LAC20CT105 | A EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48138 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT106 |  | 20LAC20CT106 | A EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48139 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT107 |  | 20LAC20CT107 | A EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48140 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT108 |  | 20LAC20CT108 | A EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48141 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT109 |  | 20LAC20CT109 | TEMP 1 OF A EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48142 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT110 |  | 20LAC20CT110 | TEMP 2 OF A EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48143 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT113 |  | 20LAC20CT113 | TEMP OF A EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48144 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT114 |  | 20LAC20CT114 | TEMP OF A EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
48145 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT115 |  | 20LAC20CT115 | TEMP OF A EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48146 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT116 |  | 20LAC20CT116 | OIL TEMP OF A EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
48147 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT117 |  | 20LAC20CT117 | OIL TEMP OF A EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
48148 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT118 |  | 20LAC20CT118 | OIL TEMP OF A EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 62 | [5 empty] | 1 | 1
48149 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.RTD.20LAC20CT119 |  | 20LAC20CT119 | OIL TEMP OF A EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 85 | [5 empty] | 1 | 1
48150 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAC20CP101 |  | 20LAC20CP101 | DIFF P OF A EFWP INLET FLTR | AI | 0 | 50 | kPa | 0.1 | 0.07 | 0.15 | [6 empty] | 2 | 1
48151 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CY105 |  | 20LAC20CY105 | AXIAL DISPLACEMENT OF TURB A EFWP | AI | -2 | 2 | mm |  |  |  | 0.2 | 0.25 |  |  |  |  | 1 | 1
48152 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CY101 |  | 20LAC20CY101 | SHAFT VIBRATION OF A EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
48153 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CY102 |  | 20LAC20CY102 | SHAFT VIBRATION OF A EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
48154 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CY103 |  | 20LAC20CY103 | SHAFT VIBRATION OF A EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
48155 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CY104 |  | 20LAC20CY104 | SHAFT VIBRATION OF A EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  |  | 0.06 | [5 empty] | 1 | 1
48156 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB20CP101 |  | 20LAB20CP101 | P OF A EFWP INLET | AI | 0 | 1 | MPa
48157 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB20CP102 |  | 20LAB20CP102 | P OF A EFWP OUTLET | AI | 0 | 20 | MPa
48158 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB50CP101 |  | 20LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
48159 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CP102 |  | 20LAC20CP102 | A EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa | 0.1 | 0.07 | 0.15 | [6 empty] | 2 | 1
48160 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-28 | KALTIM2.SIGNAL.AI.20LAC20CS101 |  | 20LAC20CS101 | A EFWP SPEED | AI | 0 | 3000 | rpm
49053 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB50CP101 |  | 20LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
49054 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB50CT101 |  | 20LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
49055 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.AI.20LAB50CP101 |  | 20LAB50CP101 | P OF EFWP OUTLET MAIN PIP | AI | 0 | 20 | MPa
49056 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 1 | #2 ELECTRIC FEED WATER PUMP A | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB50CT101 |  | 20LAB50CT101 | TEMP OF EFWP OUTLET MAIN PIP | RTD | 0 | 250 | ℃
48161 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20LAB31AA101XQ12 |  | 20LAB31AA101XQ12 | B EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
48162 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30MK001XQ12 |  | 20LAC30MK001XQ12 | B EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
48163 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AO.20LAB31AA101XQ11 |  | 20LAB31AA101XQ11 | B EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
48164 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AO.20LAC30MK001XQ11 |  | 20LAC30MK001XQ11 | B EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
48165 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20LAC30AP001XQ01 |  | 20LAC30AP001XQ01 | B EFWP CURRENT | AI | 0 | 77 | A
48166 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT101 |  | 20LAC30CT101 | TEMP OF B EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48167 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT102 |  | 20LAC30CT102 | TEMP OF B EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48168 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT103 |  | 20LAC30CT103 | B EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48169 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT104 |  | 20LAC30CT104 | B EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48170 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT105 |  | 20LAC30CT105 | B EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48171 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT106 |  | 20LAC30CT106 | B EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48172 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT107 |  | 20LAC30CT107 | B EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48173 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT108 |  | 20LAC30CT108 | B EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48174 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT109 |  | 20LAC30CT109 | TEMP 1 OF B EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48175 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT110 |  | 20LAC30CT110 | TEMP 2 OF B EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48176 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT113 |  | 20LAC30CT113 | TEMP OF B EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48177 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT114 |  | 20LAC30CT114 | TEMP OF B EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
48178 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT115 |  | 20LAC30CT115 | TEMP OF B EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48179 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT116 |  | 20LAC30CT116 | OIL TEMP OF B EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
48180 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT117 |  | 20LAC30CT117 | OIL TEMP OF B EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
48181 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT118 |  | 20LAC30CT118 | OIL TEMP OF B EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 62 | [5 empty] | 1 | 1
48182 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.RTD.20LAC30CT119 |  | 20LAC30CT119 | OIL TEMP OF B EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 85 | 90 |  |  |  |  | 1 | 1
48183 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20LAC30CP101 |  | 20LAC30CP101 | DIFF P OF B EFWP INLET FLTR | AI | 0 | 100 | kPa | 0.1 | 0.07 | 0.15 | 30 | [5 empty] | 0 | 1
48184 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CY105 |  | 20LAC30CY105 | AXIAL DISPLACEMENT OF TURB B EFWP | AI | -2 | 2 | mm |  |  | 0 | 0.2 | 0.25 |  |  |  |  | 0 | 1
48185 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CY101 |  | 20LAC30CY101 | SHAFT VIBRATION OF B EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48186 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CY102 |  | 20LAC30CY102 | SHAFT VIBRATION OF B EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48187 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CY103 |  | 20LAC30CY103 | SHAFT VIBRATION OF B EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48188 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CY104 |  | 20LAC30CY104 | SHAFT VIBRATION OF B EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48189 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20LAB30CP101 |  | 20LAB30CP101 | P OF B EFWP INLET | AI | 0 | 1 | MPa
48190 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-19 | KALTIM2.SIGNAL.AI.20LAB30CP102 |  | 20LAB30CP102 | P OF B EFWP OUTLET | AI | 0 | 20 | MPa
48191 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CP102 |  | 20LAC30CP102 | B EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa | 0.1 | 0.07 | 0.15 | [6 empty] | 2 | 1
48192 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 2 | #2 ELECTRIC FEED WATER PUMP B | K0102-29 | KALTIM2.SIGNAL.AI.20LAC30CS101 |  | 20LAC30CS101 | B EFWP SPEED | AI | 0 | 4031 | rpm
48193 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AI.20LAB41AA101XQ12 |  | 20LAB41AA101XQ12 | C EFWP RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
48194 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40MK001XQ12 |  | 20LAC40MK001XQ12 | C EFWP coupler motor-driven actuator position | AI | 0 | 100 | %
48195 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AO.20LAB41AA101XQ11 |  | 20LAB41AA101XQ11 | C EFWP RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
48196 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AO.20LAC40MK001XQ11 |  | 20LAC40MK001XQ11 | C EFWP coupler motor-driven actuator control command | AO | 0 | 100 | %
48197 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AI.20LAC40AP001XQ01 |  | 20LAC40AP001XQ01 | C EFWP CURRENT | AI | 0 | 300 | A
48198 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT101 |  | 20LAC40CT101 | TEMP OF C EFWP MTR NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48199 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT102 |  | 20LAC40CT102 | TEMP OF C EFWP MTR DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 70 | 80 |  |  |  |  | 1 | 1
48200 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT103 |  | 20LAC40CT103 | C EFWP MTR STATOR WIDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48201 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT104 |  | 20LAC40CT104 | C EFWP MTR STATOR WIDING TEMP 2 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48202 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT105 |  | 20LAC40CT105 | C EFWP MTR STATOR WIDING TEMP 3 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48203 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT106 |  | 20LAC40CT106 | C EFWP MTR STATOR WIDING TEMP 4 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48204 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT107 |  | 20LAC40CT107 | C EFWP MTR STATOR WIDING TEMP 5 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48205 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT108 |  | 20LAC40CT108 | C EFWP MTR STATOR WIDING TEMP 6 | RTD | 0 | 300 | ℃ |  |  |  | 120 | [5 empty] | 1 | 1
48206 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT109 |  | 20LAC40CT109 | TEMP 1 OF C EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48207 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT110 |  | 20LAC40CT110 | TEMP 2 OF C EFWP HYDRAULIC COUPLING BEARING | RTD | 0 | 300 | ℃ |  |  |  | 90 | 95 |  |  |  |  | 1 | 1
48208 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT113 |  | 20LAC40CT113 | TEMP OF C EFWP NON-DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48209 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT114 |  | 20LAC40CT114 | TEMP OF C EFWP DRIVING END BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
48210 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT115 |  | 20LAC40CT115 | TEMP OF C EFWP THRUST BEARING | RTD | 0 | 300 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48211 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT116 |  | 20LAC40CT116 | OIL TEMP OF C EFWP LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 55 | 60 |  |  |  |  | 1 | 1
48212 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT117 |  | 20LAC40CT117 | OIL TEMP OF C EFWP LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 65 | [5 empty] | 1 | 1
48213 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT118 |  | 20LAC40CT118 | OIL TEMP OF C EFWP WORKING OIL COOLER OUTLET | RTD | 0 | 300 | ℃ |  |  |  | 62 | [5 empty] | 1 | 1
48214 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.RTD.20LAC40CT119 |  | 20LAC40CT119 | OIL TEMP OF C EFWP WORKING OIL COOLER INLET | RTD | 0 | 300 | ℃ |  |  |  | 85 | [5 empty] | 1 | 1
48215 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AI.20LAC40CP101 |  | 20LAC40CP101 | DIFF P OF C EFWP INLET FLTR | AI | 0 | 100 | kPa | 0.1 | 0.07 | 0.15 | 30 | [5 empty] | 0 | 1
48216 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CY105 |  | 20LAC40CY105 | AXIAL DISPLACEMENT OF TURB C EFWP | AI | -2 | 2 | mm |  |  | 0 | 0.2 | 0.25 |  |  |  |  | 0 | 1
48217 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CY103 |  | 20LAC40CY103 | SHAFT VIBRATION OF C EFWP NON-DRIVING END BEARING IN THE X DIREC | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48218 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CY104 |  | 20LAC40CY104 | SHAFT VIBRATION OF C EFWP NON-DRIVING END BEARING IN THE Y DIREC | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48219 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CY101 |  | 20LAC40CY101 | SHAFT VIBRATION OF C EFWP DRIVING END BEARING IN THE X DIRECTION | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48220 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CY102 |  | 20LAC40CY102 | SHAFT VIBRATION OF C EFWP DRIVING END BEARING IN THE Y DIRECTION | AI | 0 | 12 | mm/s |  |  | 0 | 0.06 | [5 empty] | 0 | 1
48221 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AI.20LAB40CP101 |  | 20LAB40CP101 | P OF C EFWP INLET | AI | 0 | 1 | MPa
48222 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-19 | KALTIM2.SIGNAL.AI.20LAB40CP102 |  | 20LAB40CP102 | P OF C EFWP OUTLET | AI | 0 | 20 | MPa
48223 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CP102 |  | 20LAC40CP102 | C EFWP coupler inlet oil pressure | AI | 0 | 0.6 | MPa | 0.1 | 0.07 | 0.15 | [6 empty] | 2 | 1
48224 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 3 | #2 ELECTRIC FEED WATER PUMP C | K0102-30 | KALTIM2.SIGNAL.AI.20LAC40CS101 |  | 20LAC40CS101 | C EFWP SPEED | AI | 0 | 4045 | rpm
48225 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB51CT101 |  | 20LAB51CT101 | TEMP OF NO.2 HP HTR INLET | RTD | 0 | 300 | ℃
48226 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB51CT102 |  | 20LAB51CT102 | TEMP OF NO.2 HP HTR OUTLET | RTD | 0 | 300 | ℃
48227 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCH20CT101 |  | 20LCH20CT101 | NO.2 HP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
48228 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ20CT101 |  | 20LBQ20CT101 | UP WALL TEMP OF 2ND EXTR STM PIP | TC | 0 | 800 | ℃
48229 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ20CT102 |  | 20LBQ20CT102 | BTM WALL TEMP OF 2 EXTR STM PIP | TC | 0 | 800 | ℃
48230 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ20CT103 |  | 20LBQ20CT103 | TEMP OF 2ND EXTR STM PIP | TC | 0 | 800 | ℃
48234 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-18 | KALTIM2.SIGNAL.AI.20LBQ20CP101 |  | 20LBQ20CP101 | P OF 2ND EXTR STM PIP | AI | 0 | 2.5 | MPa
48246 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD20CL101 |  | 20LAD20CL101 | NO.2 HP HTR LEVEL 1 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48247 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD20CL102 |  | 20LAD20CL102 | NO.2 HP HTR LEVEL 2 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48248 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 4 | #2 HIGH PRESSURE HEATER 2 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD20CL103 |  | 20LAD20CL103 | NO.2 HP HTR LEVEL 3 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48231 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD10CL101 |  | 20LAD10CL101 | NO.1 HP HTR LEVEL 1 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48232 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD10CL102 |  | 20LAD10CL102 | NO.1 HP HTR LEVEL 2 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48233 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM2.SIGNAL.AI.20LAD10CL103 |  | 20LAD10CL103 | NO.1 HP HTR LEVEL 3 | AI | 0 | 800 | mm |  |  | -100 | 100 | 250 | 400 |  |  |  | 0 | 1
48235 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AI.20LAB61AA101XQ12 |  | 20LAB61AA101XQ12 | Main feed water control valve position feedback | AI | 0 | 100 | %
48236 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AI.20LAB50AA101XQ12 |  | 20LAB50AA101XQ12 | Main feedwater MOV regulating feedback | AI | 0 | 100 | %
48237 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AO.20LAB50AA101XQ11 |  | 20LAB50AA101XQ11 | Main feedwater MOV regulating command | AO | 0 | 100 | %
48238 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AO.20LAB61AA101XQ11 |  | 20LAB61AA101XQ11 | Main feed water control valve control command | AO | 0 | 100 | %
48239 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB52CT101 |  | 20LAB52CT101 | TEMP OF NO.1 HP HTR INLET | RTD | 0 | 300 | ℃
48240 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-19 | KALTIM2.SIGNAL.RTD.20LAB52CT102 |  | 20LAB52CT102 | TEMP OF NO.1 HP HTR OUTLET | RTD | 0 | 300 | ℃
48241 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCH10CT101 |  | 20LCH10CT101 | NO.1 HP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
48242 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.TC.20LAB50CT102 |  | 20LAB50CT102 | Main boiler feed water temperature | TC | 0 | 400 | ℃
48243 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ10CT101 |  | 20LBQ10CT101 | UP WALL TEMP OF 1ST EXTR STM PIP | TC | 0 | 800 | ℃
48244 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ10CT102 |  | 20LBQ10CT102 | BTM WALL TEMP OF 1 EXTR STM PIP | TC | 0 | 800 | ℃
48245 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM2.SIGNAL.TC.20LBQ10CT103 |  | 20LBQ10CT103 | TEMP OF 1ST EXTR STM PIP | TC | 0 | 800 | ℃
48249 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-18 | KALTIM2.SIGNAL.AI.20LBQ10CP101 |  | 20LBQ10CP101 | P OF 1ST EXTR STM PIP | AI | 0 | 4 | MPa
48250 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AI.20LAB50CF101 |  | 20LAB50CF101 | Main boiler feed water flow 1 | AI | 0 | 500 | t/h |  |  | 0.3 | 0.4 | [5 empty] | 0
48251 | 2 | UJKTT #2 | 4 | #2 FEED WATER SYSTEM | 5 | #2 HIGH PRESSURE HEATER 1 | K0102-02 | KALTIM2.SIGNAL.AI.20LAB50CF102 |  | 20LAB50CF102 | Main boiler feed water flow 2 | AI | 0 | 500 | t/h |  |  | 0.3 | 0.4 | [5 empty] | 0
48253 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNA10AA101XQ12 |  | 20HNA10AA101XQ12 | A iuduced draft fan inlet control damper position feedback | AI | 0 | 100 | %
48254 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AO.20HNA10AA101XQ11 |  | 20HNA10AA101XQ11 | A iuduced draft fan inlet control damper control command | AO | 0 | 100 | %
48255 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNC10AN001XQ01 |  | 20HNC10AN001XQ01 | A iuduced draft fan current | AI | 0 | 300 | A
48256 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA10CT103 |  | 20HNA10CT103 | A IDF outlet air temperature | RTD | 0 | 200 | ℃
48257 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA10CT101 |  | 20HNA10CT101 | Side-A boiler outlet flue gas temperature | RTD | 0 | 200 | ℃
48258 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA10CT102 |  | 20HNA10CT102 | A iuduced draft fan inlet flue gas temperature | RTD | 0 | 200 | ℃
48259 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT101 |  | 20HNC10CT101 | A IDF bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48260 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT102 |  | 20HNC10CT102 | A IDF bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48261 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT103 |  | 20HNC10CT103 | A IDF motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
48262 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT104 |  | 20HNC10CT104 | A IDF motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48263 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT105 |  | 20HNC10CT105 | A IDF motor stator temperature 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48264 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT106 |  | 20HNC10CT106 | A IDF motor stator temperature 2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48265 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT107 |  | 20HNC10CT107 | A IDF motor stator temperature 3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48266 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT108 |  | 20HNC10CT108 | A IDF motor stator temperature 4 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48267 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT109 |  | 20HNC10CT109 | A IDF motor stator temperature 5 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48268 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC10CT110 |  | 20HNC10CT110 | A IDF motor stator temperature 6 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48269 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNA10CP101 |  | 20HNA10CP101 | A iuduced draft fan inlet flue gas pressure | AI | -10 | 0 | kPa | [10 empty] | 1
48270 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNA10CP102 |  | 20HNA10CP102 | A IDF outlet air pressure | AI | -1 | 10 | kPa
48271 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNC10CY101 |  | 20HNC10CY101 | A IDF front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48272 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 1 | #2 ID FAN A | K0102-09 | KALTIM2.SIGNAL.AI.20HNC10CY102 |  | 20HNC10CY102 | A IDF rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48273 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNA20AA101XQ12 |  | 20HNA20AA101XQ12 | B iuduced draft fan inlet control damper position feedback | AI | 0 | 100 | %
48274 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AO.20HNA20AA101XQ11 |  | 20HNA20AA101XQ11 | B iuduced draft fan inlet control damper control command | AO | 0 | 100 | %
48275 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNC20AN001XQ01 |  | 20HNC20AN001XQ01 | B iuduced draft fan current | AI | 0 | 300 | A
48276 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA20CT101 |  | 20HNA20CT101 | Side-B boiler outlet flue gas temperature | RTD | 0 | 200 | ℃
48277 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA20CT102 |  | 20HNA20CT102 | B iuduced draft fan inlet flue gas temperature | RTD | 0 | 200 | ℃
48278 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNA20CT103 |  | 20HNA20CT103 | B IDF outlet air temperature | RTD | 0 | 200 | ℃
48279 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT101 |  | 20HNC20CT101 | B IDF bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48280 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT102 |  | 20HNC20CT102 | B IDF bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48281 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT103 |  | 20HNC20CT103 | B IDF motor bearing temperature 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 90 |  |  |  |  | 1 | 1
48282 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT104 |  | 20HNC20CT104 | B IDF motor bearing temperature 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | [5 empty] | 1 | 1
48283 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT105 |  | 20HNC20CT105 | B IDF motor stator temperature 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48284 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT106 |  | 20HNC20CT106 | B IDF motor stator temperature 2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48285 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT107 |  | 20HNC20CT107 | B IDF motor stator temperature 3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48286 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT108 |  | 20HNC20CT108 | B IDF motor stator temperature 4 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48287 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT109 |  | 20HNC20CT109 | B IDF motor stator temperature 5 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48288 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.RTD.20HNC20CT110 |  | 20HNC20CT110 | B IDF motor stator temperature 6 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48289 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNA20CP102 |  | 20HNA20CP102 | B IDF outlet air pressure | AI | -1 | 10 | kPa
48290 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNA20CP101 |  | 20HNA20CP101 | B iuduced draft fan inlet flue gas pressure | AI | -10 | 0 | kPa | [10 empty] | 1
48291 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNC20CY101 |  | 20HNC20CY101 | B IDF front bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48292 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 2 | #2 ID FAN B | K0102-09 | KALTIM2.SIGNAL.AI.20HNC20CY102 |  | 20HNC20CY102 | B IDF rear bearing vibration | AI | 0 | 12 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48293 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ102 |  | 20HNA30CQ102 | Chimney flue gas humidity | AI | 0 | 20 | %
48294 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ106 |  | 20HNA30CQ106 | Chimney flue gas O2 concentration | AI | 0 | 25 | %
48295 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ102 |  | 20HNA30CQ102 | Flue gas Humadity unit 2 | AI | 0 | 100 | %
48296 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ106 |  | 20HNA30CQ106 | Flue gas O2 unit 2 | AI | 0 | 25 | %
48297 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ107 |  | 20HNA30CQ107 | Flue gas CO2 unit 2 | AI | 0 | 50 | %
48298 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ108 |  | 20HNA30CQ108 | Flue gas Opacity unit 2 | AI | 0 | 30 | %
48299 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CT101 |  | 20HNA30CT101 | Chimney flue gas temperature | AI | 0 | 300 | ℃
48300 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CT101 |  | 20HNA30CT101 | Flue gas Temperature unit 2 | AI | 0 | 200 | ℃
48301 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CP101 |  | 20HNA30CP101 | Chimney flue gas pressure | AI | -5 | 5 | kPa
48302 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CP101 |  | 20HNA30CP101 | Flue gas Pressure unit 2 | AI | 0 | 200 | KPa
48303 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM2.SIGNAL.AI.20HNA30CF101 |  | 20HNA30CF101 | Chimney flue gas flow | AI | 0 | 40 | m/s
48304 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ109 |  | 20HNA30CQ109 | Flue gas Velocity unit 2 | AI | 0 | 100 | m/s
48305 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM2.SIGNAL.AI.20HNA30CQ103XQ01 |  | 20HNA30CQ103XQ01 | Chimney flue gas SO2 concentration 1 | AI | 0 | 500 | mg/Nm3
48306 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM2.SIGNAL.AI.20HNA30CQ103XQ02 |  | 20HNA30CQ103XQ02 | Chimney flue gas SO2 concentration 2 | AI | 0 | 500 | mg/Nm3
48310 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ101 |  | 20HNA30CQ101 | Chimney flue gas dust concentration | AI | 0 | 500 | mg/Nm3
48311 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ104 |  | 20HNA30CQ104 | Chimney flue gas NOx concentration | AI | 0 | 500 | mg/Nm3
48312 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ105 |  | 20HNA30CQ105 | Chimney flue gas CO concentration | AI | 0 | 500 | mg/Nm3
48313 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ101 |  | 20HNA30CQ101 | Flue gas Dust unit 2 | AI | 0 | 500
48314 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ104 |  | 20HNA30CQ104 | Flue gas NOX unit 2 | AI | 0 | 2000
48315 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ105 |  | 20HNA30CQ105 | Flue gas CO unit 2 | AI | 0 | 500
48316 | 2 | UJKTT #2 | 5 | #2 FLUE GAS SYSTEM | 3 | #2 STACK | K0102-09 | KALTIM 0.SIGNAL.AI.20HNA30CQ103 |  | 20HNA30CQ103 | Flue gas SO2 unit 2 | AI | 0 | 1500
48317 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA70AA101XQ12 |  | 20LCA70AA101XQ12 | COND RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
48318 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AO.20LCA70AA101XQ11 |  | 20LCA70AA101XQ11 | COND RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
48319 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCB30AP001XQ01 |  | 20LCB30AP001XQ01 | A CONDENSATE PMP CURRENT | AI | 0 | 75 | A
48320 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA50CT101 |  | 20LCA50CT101 | TEMP OF CONDENSATE PMP OUTLET MAIN PIP | RTD | 0 | 300 | ℃
48321 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT101 |  | 20LCB30CT101 | A CONDENSATE PMP THRUST BEARING TEMP | RTD | 0 | 100 | ℃ | [10 empty] | 1
48322 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT102 |  | 20LCB30CT102 | A CONDENSATE PMP MTR BEARING TEMP 1 | RTD | 0 | 120 | ℃ |  |  |  | 85 | 90 |  |  |  |  | 1 | 1
48323 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT103 |  | 20LCB30CT103 | A CONDENSATE PMP MTR BEARING TEMP 2 | RTD | 0 | 120 | ℃ |  |  |  | 85 | 90 |  |  |  |  | 1 | 1
48324 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT104 |  | 20LCB30CT104 | A CONDENSATE PMP MTR STATOR TEMP 1 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48325 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT105 |  | 20LCB30CT105 | A CONDENSATE PMP MTR STATOR TEMP 2 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48326 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT106 |  | 20LCB30CT106 | A CONDENSATE PMP MTR STATOR TEMP 3 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48327 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT107 |  | 20LCB30CT107 | A CONDENSATE PMP MTR STATOR TEMP 4 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48328 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT108 |  | 20LCB30CT108 | A CONDENSATE PMP MTR STATOR TEMP 5 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48329 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB30CT109 |  | 20LCB30CT109 | A CONDENSATE PMP MTR STATOR TEMP 6 | RTD | 0 | 120 | ℃ |  |  |  | 115 | 120 |  |  |  |  | 1 | 1
48330 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA30CP101 |  | 20LCA30CP101 | DIFF P OF A CONDENSATE PMP INLET FLTR | AI | 0 | 100 | kPa
48331 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCB30CY101 |  | 20LCB30CY101 | A CONDENSATE PMP BEARING VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 4.6 | 7.1 |  |  |  |  | 1 | 1
48332 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCB30CY102 |  | 20LCB30CY102 | A CONDENSATE PMP BEARING VIBRATION Y | AI | 0 | 20 | mm/s | [10 empty] | 1
48333 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LAW10CP101 |  | 20LAW10CP101 | CONDENSATE PMP SEAL WTR P | AI | 0 | 1.2 | MPa |  |  | 0.25 | [6 empty] | 2
48334 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA30CP102 |  | 20LCA30CP102 | A CONDENSATE PMP OUTLET P | AI | 0 | 2.5 | MPa
48335 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA50CP101 |  | 20LCA50CP101 | P OF CONDENSATE PMP OUTLET MAIN PIP | AI | 0 | 2.5 | MPa |  |  | 1.2 | [6 empty] | 2 | 1
48336 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.20GUC10CQ101 |  | 20GUC10CQ101 | Unit 2 Condensate pump outport O2 | AI | 0 | 1000
48337 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.20GUC10CQ102 |  | 20GUC10CQ102 | Unit 2 Condensate pump outport cc | AI | 0 | 20
49064 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA50CP101 |  | 20LCA50CP101 | P OF CONDENSATE PMP OUTLET MAIN PIP | AI | 0 | 2.5 | MPa
49065 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA50CT101 |  | 20LCA50CT101 | TEMP OF CONDENSATE PMP OUTLET MAIN PIP | RTD | 0 | 300 | ℃
49066 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AO.20LCA70AA101XQ11 |  | 20LCA70AA101XQ11 | COND RECYCLE CTRL VLV ADJ CMD | AO | 0 | 100 | %
49067 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LCA70AA101XQ12 |  | 20LCA70AA101XQ12 | COND RECYCLE CTRL VLV POSITION | AI | 0 | 100 | %
49068 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.20GUC10CQ101 |  | 20GUC10CQ101 | Unit 2 Condensate pump outport O2 | AI | 0 | 1000
49069 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A |  | KALTIM 0.SIGNAL.AI.20GUC10CQ102 |  | 20GUC10CQ102 | Unit 2 Condensate pump outport cc | AI | 0 | 20
49070 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 1 | #2 CONDENSATE PUMP A | K0102-20 | KALTIM2.SIGNAL.AI.20LAW10CP101 |  | 20LAW10CP101 | CONDENSATE PMP SEAL WTR P | AI | 0 | 1.2 | MPa
48338 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20LCB40AP001XQ01 |  | 20LCB40AP001XQ01 | B CONDENSATE PMP CURRENT | AI | 0 | 75 | A
48339 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT101 |  | 20LCB40CT101 | B CONDENSATE PMP THRUST BEARING TEMP | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  |  |  |  | 1 | 1
48340 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT102 |  | 20LCB40CT102 | B CONDENSATE PMP MTR BEARING TEMP 1 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48341 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT103 |  | 20LCB40CT103 | B CONDENSATE PMP MTR BEARING TEMP 2 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48342 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT104 |  | 20LCB40CT104 | B CONDENSATE PMP MTR STATOR TEMP 1 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48343 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT105 |  | 20LCB40CT105 | B CONDENSATE PMP MTR STATOR TEMP 2 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48344 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT106 |  | 20LCB40CT106 | B CONDENSATE PMP MTR STATOR TEMP 3 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48345 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT107 |  | 20LCB40CT107 | B CONDENSATE PMP MTR STATOR TEMP 4 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48346 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT108 |  | 20LCB40CT108 | B CONDENSATE PMP MTR STATOR TEMP 5 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48347 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.RTD.20LCB40CT109 |  | 20LCB40CT109 | B CONDENSATE PMP MTR STATOR TEMP 6 | RTD | 0 | 120 | ℃ | [10 empty] | 1
48348 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20LCA40CP101 |  | 20LCA40CP101 | DIFF P OF B CONDENSATE PMP INLET FLTR | AI | 0 | 100 | kPa
48349 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20LCB40CY102 |  | 20LCB40CY102 | B CONDENSATE PMP BEARING VIBRATION Y | AI | 0 | 50 | mm/s | [10 empty] | 1
48350 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20LCB40CY101 |  | 20LCB40CY101 | B CONDENSATE PMP BEARING VIBRATION X | AI | 0 | 50 | mm/s | [10 empty] | 1
48351 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 2 | #2 CONDENSATE PUMP B | K0102-20 | KALTIM2.SIGNAL.AI.20LCA40CP102 |  | 20LCA40CP102 | B CONDENSATE PMP OUTLET P | AI | 0 | 2.5 | MPa
48352 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 3 | #2 GLAND STEAM CONDENSER | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA51CT101 |  | 20LCA51CT101 | CONDENSATE WTR TEMP OF GLD STM COND INLET | RTD | 0 | 300 | ℃
48353 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 3 | #2 GLAND STEAM CONDENSER | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA51CT102 |  | 20LCA51CT102 | CONDENSATE WTR TEMP OF GLD STM COND OUTLET | RTD | 0 | 300 | ℃
48354 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 3 | #2 GLAND STEAM CONDENSER | K0102-31 | KALTIM2.SIGNAL.TC.20MAW10CT101 |  | 20MAW10CT101 | STM TEMP OF GLD STM COND INLET | TC | 0 | 800 | ℃
48355 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 3 | #2 GLAND STEAM CONDENSER | K0102-31 | KALTIM2.SIGNAL.AI.20MAW10CP101 |  | 20MAW10CP101 | STM P OF GLD STM COND INLET | AI | -100 | 0 | kPa
48356 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 3 | #2 GLAND STEAM CONDENSER | K0102-21 | KALTIM2.SIGNAL.AI.20MAW10CL101 |  | 20MAW10CL101 | GLD STM COND LEVEL | AI | 0 | 300 | mm |  |  |  | 250 | [5 empty] | 1 | 1
48357 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ70AA102XQ12 |  | 20LCJ70AA102XQ12 | 7 LP HTR EMG DRN CTRL VLV 2 PSN | AI | 0 | 100 | %
48358 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ70AA101XQ12 |  | 20LCJ70AA101XQ12 | 7 LP HTR EMG DRN CTRL VLV 1 PSN | AI | 0 | 100 | %
48359 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ70AA101XQ11 |  | 20LCJ70AA101XQ11 | 7 LP HTR EMG DRN CTRL VLV 1 ADJ CMD | AO | 0 | 100 | %
48360 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ70AA102XQ11 |  | 20LCJ70AA102XQ11 | 7 LP HTR EMG DRN CTRL VLV 2 ADJ CMD | AO | 0 | 100 | %
48361 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA53CT101 |  | 20LCA53CT101 | TEMP OF NO.7 LP HTR WTR INLET | RTD | 0 | 300 | ℃
48362 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA53CT102 |  | 20LCA53CT102 | TEMP OF NO.7 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
48363 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCJ70CT101 |  | 20LCJ70CT101 | NO.7 LP heater emergency drainage temperature | RTD | 0 | 300 | ℃
48364 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT101 |  | 20LBS70CT101 | B SIDE UP WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48365 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT102 |  | 20LBS70CT102 | B SIDE BTM WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48366 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT103 |  | 20LBS70CT103 | B SIDE TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48367 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT104 |  | 20LBS70CT104 | A SIDE UP WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48368 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT105 |  | 20LBS70CT105 | A SIDE BTM WALL TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48369 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS70CT106 |  | 20LBS70CT106 | A SIDE TEMP OF 7TH EXTR STM PIP | TC | 0 | 800 | ℃
48370 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-21 | KALTIM2.SIGNAL.AI.20LCC70CL102 |  | 20LCC70CL102 | NO.7 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
48371 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.AI.20LBS70CP101 |  | 20LBS70CP101 | B SIDE P OF 7TH EXTR STM PIP | AI | 0 | 0.06 | MPa
48372 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 4 | #2 LOW PRESSURE HEATER 7 | K0102-18 | KALTIM2.SIGNAL.AI.20LBS70CP102 |  | 20LBS70CP102 | A SIDE P OF 7TH EXTR STM PIP | AI | 0 | 0.06 | MPa
48373 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ60AA101XQ12 |  | 20LCJ60AA101XQ12 | PNEUMATIC CTRL VLV OF LP DRAIN PMP OUTLET PSN | AI | 0 | 100 | %
48374 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ60AA102XQ12 |  | 20LCJ60AA102XQ12 | 6 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
48375 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ60AA101XQ11 |  | 20LCJ60AA101XQ11 | PNEUMATIC CTRL VLV OF LP DRAIN PMP OUTLET ADJ CMD | AO | 0 | 100 | %
48376 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ60AA102XQ11 |  | 20LCJ60AA102XQ11 | 6 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
48377 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ60AP001XQ01 |  | 20LCJ60AP001XQ01 | LP drain pump current | AI | 0 | 150 | A
48378 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA54CT101 |  | 20LCA54CT101 | TEMP OF NO.6 LP HTR WTR INLET | RTD | 0 | 300 | ℃
48379 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA54CT102 |  | 20LCA54CT102 | TEMP OF NO.6 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
48380 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCJ60CT101 |  | 20LCJ60CT101 | NO.6 LP heater emergency drainage temperature | RTD | 0 | 300 | ℃
48381 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS60CT101 |  | 20LBS60CT101 | UP WALL TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
48382 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS60CT102 |  | 20LBS60CT102 | BTM WALL TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
48383 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS60CT103 |  | 20LBS60CT103 | TEMP OF 6TH EXTR STM PIP | TC | 0 | 800 | ℃
48384 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-21 | KALTIM2.SIGNAL.AI.20LCC60CL102 |  | 20LCC60CL102 | NO.6 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
48385 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 5 | #2 LOW PRESSURE HEATER 6 | K0102-18 | KALTIM2.SIGNAL.AI.20LBS60CP101 |  | 20LBS60CP101 | P OF 6TH EXTR STM PIP | AI | 0 | 0.2 | MPa
48386 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ50AA101XQ12 |  | 20LCJ50AA101XQ12 | 5 LP HTR NORMAL DRN CTRL VLV PSN | AI | 0 | 100 | %
48387 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ50AA102XQ12 |  | 20LCJ50AA102XQ12 | 5 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
48388 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ50AA101XQ11 |  | 20LCJ50AA101XQ11 | 5 LP HTR NORMAL DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
48389 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ50AA102XQ11 |  | 20LCJ50AA102XQ11 | 5 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
48390 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA55CT101 |  | 20LCA55CT101 | TEMP OF NO.5 LP HTR WTR INLET | RTD | 0 | 300 | ℃
48391 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA55CT102 |  | 20LCA55CT102 | TEMP OF NO.5 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
48392 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCJ50CT101 |  | 20LCJ50CT101 | NO.5 LP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
48393 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS50CT101 |  | 20LBS50CT101 | UP WALL TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
48394 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS50CT102 |  | 20LBS50CT102 | BTM WALL TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
48395 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS50CT103 |  | 20LBS50CT103 | TEMP OF 5TH EXTR STM PIP | TC | 0 | 800 | ℃
48396 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-21 | KALTIM2.SIGNAL.AI.20LCC50CL102 |  | 20LCC50CL102 | NO.5 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
48397 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 6 | #2 LOW PRESSURE HEATER 5 | K0102-18 | KALTIM2.SIGNAL.AI.20LBS50CP101 |  | 20LBS50CP101 | P OF 5TH EXTR STM PIP | AI | 0 | 0.3 | MPa
48398 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ40AA101XQ12 |  | 20LCJ40AA101XQ12 | 4 LP HTR NORMAL DRN CTRL VLV PSN | AI | 0 | 100 | %
48399 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.AI.20LCJ40AA102XQ12 |  | 20LCJ40AA102XQ12 | 4 LP HTR EMG DRN CTRL VLV PSN | AI | 0 | 100 | %
48400 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ40AA101XQ11 |  | 20LCJ40AA101XQ11 | 4 LP HTR NORMAL DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
48401 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.AO.20LCJ40AA102XQ11 |  | 20LCJ40AA102XQ11 | 4 LP HTR EMG DRN CTRL VLV ADJ CMD | AO | 0 | 100 | %
48402 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA56CT101 |  | 20LCA56CT101 | TEMP OF NO.4 LP HTR WTR INLET | RTD | 0 | 300 | ℃
48403 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-20 | KALTIM2.SIGNAL.RTD.20LCA56CT102 |  | 20LCA56CT102 | TEMP OF NO.4 LP HTR WTR OUTLET | RTD | 0 | 300 | ℃
48404 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.RTD.20LCJ40CT101 |  | 20LCJ40CT101 | NO.4 LP HTR DRN WTR TEMP | RTD | 0 | 300 | ℃
48405 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS40CT101 |  | 20LBS40CT101 | UP WALL TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
48406 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS40CT102 |  | 20LBS40CT102 | BTM WALL TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
48407 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM2.SIGNAL.TC.20LBS40CT103 |  | 20LBS40CT103 | TEMP OF 4TH EXTR STM PIP | TC | 0 | 800 | ℃
48408 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-21 | KALTIM2.SIGNAL.AI.20LCC40CL102 |  | 20LCC40CL102 | NO.4 LP HTR LEVEL 2 | AI | 0 | 1000 | mm |  |  |  | 150 | 300 | 450 |  |  |  | 1 | 1
48409 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 7 | #2 LOW PRESSURE HEATER 4 | K0102-18 | KALTIM2.SIGNAL.AI.20LBS40CP101 |  | 20LBS40CP101 | P OF 4TH EXTR STM PIP | AI | 0 | 0.8 | MPa
48410 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.AI.20LBS30AA101XQ12 |  | 20LBS30AA101XQ12 | CTRL VLV OF 3RD EXTR STM TO DEAE POSITION | AI | 0 | 100 | %
48411 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-20 | KALTIM2.SIGNAL.AI.20LCA50AA101XQ12 |  | 20LCA50AA101XQ12 | DEAE LEVEL CTRL VLV POSITION | AI | 0 | 100 | %
48412 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-23 | KALTIM2.SIGNAL.AI.20LBG26AA101XQ12 |  | 20LBG26AA101XQ12 | CTRL VLV ON THE PIP FROM AUX STM TO DEAE PSN | AI | 0 | 100 | %
48413 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.AO.20LBS30AA101XQ11 |  | 20LBS30AA101XQ11 | Control valve of 3rd extraction steam to deaerator adjust comman | AO | 0 | 100 | %
48414 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-20 | KALTIM2.SIGNAL.AO.20LCA50AA101XQ11 |  | 20LCA50AA101XQ11 | DEAE LEVEL CTRL VLV ADJ CMD | AO | 0 | 100 | %
48415 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-23 | KALTIM2.SIGNAL.AO.20LBG26AA101XQ11 |  | 20LBG26AA101XQ11 | CTRL VLV ON THE PIP FROM AUX STM TO DEAE ADJ CMD | AO | 0 | 100 | %
48416 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.RTD.20LAA01CT101 |  | 20LAA01CT101 | TEMP OF DEAE WTR TANK | RTD | 0 | 200 | ℃
48417 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.TC.20LBS30CT101 |  | 20LBS30CT101 | UP WALL TEMP OF 3RD EXTR STM PIP | TC | 0 | 800 | ℃
48418 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.TC.20LBS30CT102 |  | 20LBS30CT102 | BTM WALL TEMP OF 3 EXTR STM PIP | TC | 0 | 800 | ℃
48419 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.TC.20LBS30CT103 |  | 20LBS30CT103 | TEMP OF 3RD EXTR STM PIP | TC | 0 | 800 | ℃
48420 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-23 | KALTIM2.SIGNAL.TC.20LBG26CT101 |  | 20LBG26CT101 | TEMP OF THE STM FROM AUX STM TO DEAE | TC | 0 | 800 | ℃
48421 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-20 | KALTIM2.SIGNAL.AI.20LAA01CL101 |  | 20LAA01CL101 | DEAE WTR TANK LEVEL 1 | AI | 0 | 2400 | mm | -1300 |  | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
48422 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-20 | KALTIM2.SIGNAL.AI.20LAA01CL102 |  | 20LAA01CL102 | DEAE WTR TANK LEVEL 2 | AI | 0 | 2400 | mm | -1300 |  | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
48423 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-20 | KALTIM2.SIGNAL.AI.20LAA01CL103 |  | 20LAA01CL103 | DEAE WTR TANK LEVEL 3 | AI | 0 | 2400 | mm | -1300 |  | -200 | 200 | 300 | 400 |  |  |  | 0 | 1
48424 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.AI.20LAA01CP101 |  | 20LAA01CP101 | P 1 OF DEAE | AI | 0 | 1.2 | MPa
48425 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.AI.20LAA01CP102 |  | 20LAA01CP102 | P 2 OF DEAE | AI | 0 | 1.2 | MPa
48426 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-18 | KALTIM2.SIGNAL.AI.20LBS30CP101 |  | 20LBS30CP101 | P OF 3RD EXTR STM PIP | AI | 0 | 1.5 | MPa
48427 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR | K0102-23 | KALTIM2.SIGNAL.AI.20LBG26CP101 |  | 20LBG26CP101 | P OF THE STM FROM AUX STM TO DEAE | AI | 0 | 1.6 | MPa
48428 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR |  | KALTIM 0.SIGNAL.AI.20GUB10CQ103 |  | 20GUB10CQ103 | Unit 2 Deaerator import CC | AI | 0 | 20
48429 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR |  | KALTIM 0.SIGNAL.AI.20GUB20CQ101 |  | 20GUB20CQ101 | Unit 2 Deaerator outport O2 | AI | 0 | 100
48430 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR |  | KALTIM 0.SIGNAL.AI.20GUB10CQ101 |  | 20GUB10CQ101 | Unit 2 Deaerator import O2 | AI | 0 | 1000
48431 | 2 | UJKTT #2 | 6 | #2 CONDENSATE WATER SYSTEM | 8 | #2 DEARATOR |  | KALTIM 0.SIGNAL.AI.20GUB10CQ102 |  | 20GUB10CQ102 | Unit 2 Deaerator import PH | AI | 0 | 14
48432 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT101 |  | 20MAA01CT101 | TEMP OF STM AFR MAIN STM VLV | TC | 0 | 800 | ℃
48433 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT102 |  | 20MAA01CT102 | EXTERNAL WALL TEMP BFR MAIN STM VLV | TC | 0 | 800 | ℃
48434 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT103 |  | 20MAA01CT103 | EXTERNAL WALL TEMP OF STM CHEST COVER FLANGE OF MAIN STM VLV | TC | 0 | 800 | ℃
48435 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT104 |  | 20MAA01CT104 | MAIN STM VLV BOLT TEMP | TC | 0 | 800 | ℃
48436 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT105 |  | 20MAA01CT105 | EXTERNAL WALL TEMP 1 OF MAIN STM PIP | TC | 0 | 800 | ℃
48437 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT106 |  | 20MAA01CT106 | EXTERNAL WALL TEMP 2 OF MAIN STM PIP | TC | 0 | 800 | ℃
48438 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT107 |  | 20MAA01CT107 | EXTERNAL WALL TEMP 3 OF MAIN STM PIP | TC | 0 | 800 | ℃
48439 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT108 |  | 20MAA01CT108 | EXTERNAL WALL TEMP 4 OF MAIN STM PIP | TC | 0 | 800 | ℃
48440 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP101 |  | 20MAA01CP101 | P OF STM BFR MAIN STM VLV | AI | 0 | 16 | MPa
48441 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 1 | #2 MAIN STEAM VALVE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP102 |  | 20MAA01CP102 | P OF STM AFR MAIN STM VLV | AI | 0 | 16 | MPa
48442 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 2 | #2 GOVERNOR VALVE L1 | K0102-31 | KALTIM2.SIGNAL.AI.20MAW31AA101XQ12 |  | 20MAW31AA101XQ12 | CTRL VLV OF SHAFT SEALING STM POSITION | AI | 0 | 100 | %
48443 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 2 | #2 GOVERNOR VALVE L1 |  | KALTIM2.SIGNAL.AO.20CBA01XQ12 |  | 20CBA01XQ12 | Remote control main steam pressure set value | AO | 0 | 100 | %
48444 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 2 | #2 GOVERNOR VALVE L1 | K0102-31 | KALTIM2.SIGNAL.AO.20MAW31AA101XQ11 |  | 20MAW31AA101XQ11 | CTRL VLV OF SHAFT SEALING STM ADJ CMD | AO | 0 | 100 | %
48445 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 2 | #2 GOVERNOR VALVE L1 | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP103 |  | 20MAA01CP103 | P OF STM AFR NO.1 CTRL VLV | AI | 0 | 16 | MPa
48446 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 3 | #2 GOVERNOR VALVE L2 | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP104 |  | 20MAA01CP104 | P OF STM AFR NO.2 CTRL VLV | AI | 0 | 16 | MPa
48447 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 4 | #2 GOVERNOR VALVE R1 | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP105 |  | 20MAA01CP105 | P OF STM AFR NO.3 CTRL VLV | AI | 0 | 16 | MPa
48448 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 5 | #2 GOVERNOR VALVE R2 | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP106 |  | 20MAA01CP106 | P OF STM AFR NO.4 CTRL VLV | AI | 0 | 16 | MPa
48449 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA11CT151 |  | 20MAA11CT151 | TEMP OF THE NO.1 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48450 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA51CT153 |  | 20MAA51CT153 | Temperature of the NO.1 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48451 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD11CY101 |  | 20MAD11CY101 | SHAFT VIBRATION OF NO.1 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
48452 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD11CY102 |  | 20MAD11CY102 | SHAFT VIBRATION OF NO.1 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
48453 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD11CY103 |  | 20MAD11CY103 | Vibration of NO.1 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
48454 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 6 | #2 TURBINE BEARING NO. 1 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD11CY104 |  | 20MAD11CY104 | Vibration of NO.1 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 125 | 254 |  |  |  |  | 1 | 1
48455 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT109 |  | 20MAA01CT109 | EXTERNAL WALL TEMP OF TOP HALF OF HP CYLINDER REAR | TC | 0 | 800 | ℃
48456 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT118 |  | 20MAA01CT118 | INTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
48457 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-31 | KALTIM2.SIGNAL.TC.20MAW20CT101 |  | 20MAW20CT101 | TEMP OF THE GATE ROD LEAKAGE STM AND HP CYLINDER SHAFT SEALING S | TC | 0 | 800 | ℃
48458 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT110 |  | 20MAA01CT110 | TEMP OF STM BFR GOVERNING STAGE | TC | 0 | 800 | ℃
48459 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT111 |  | 20MAA01CT111 | EXTERNAL WALL TEMP OF TOP HALF OF STM CYLINDER | TC | 0 | 800 | ℃
48460 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT113 |  | 20MAA01CT113 | EXTERNAL WALL TEMP OF BTM HALF OF STM CYLINDER | TC | 0 | 800 | ℃
48461 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT115 |  | 20MAA01CT115 | EXTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
48462 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT116 |  | 20MAA01CT116 | INTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
48463 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT117 |  | 20MAA01CT117 | EXTERNAL BOLT WALL TEMP OF TOP HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
48464 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT119 |  | 20MAA01CT119 | EXTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
48465 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT120 |  | 20MAA01CT120 | INTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER LEFT SIDE | TC | 0 | 800 | ℃
48466 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT121 |  | 20MAA01CT121 | EXTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
48467 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT122 |  | 20MAA01CT122 | INTERNAL BOLT WALL TEMP OF BTM HALF OF CYLINDER RIGHT SIDE | TC | 0 | 800 | ℃
48468 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT123 |  | 20MAA01CT123 | TEMP OF STM AFR NO.5 STAGE | TC | 0 | 800 | ℃
48469 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT124 |  | 20MAA01CT124 | TEMP OF STM AFR NO.8 STAGE | TC | 0 | 800 | ℃
48470 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT125 |  | 20MAA01CT125 | TEMP OF STM AFR NO.11 STAGE | TC | 0 | 800 | ℃
48471 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT126 |  | 20MAA01CT126 | TEMP OF STM AFR NO.14 STAGE | TC | 0 | 800 | ℃
48472 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT127 |  | 20MAA01CT127 | TEMP OF STM AFR NO.16 STAGE | TC | 0 | 800 | ℃
48473 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT128 |  | 20MAA01CT128 | TEMP OF CYLINDER LEFT SIDE BOLT AFR GOVERNING STAGE | TC | 0 | 800 | ℃
48474 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAA01CT129 |  | 20MAA01CT129 | TEMP OF CYLINDER RIGHT SIDE BOLT AFR GOVERNING STAGE | TC | 0 | 800 | ℃
48475 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP113 |  | 20MAA01CP113 | P OF GLD STM BFR ENTERING HP CYLINDER | AI | -100 | 150 | kPa
48476 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP114 |  | 20MAA01CP114 | P OF GLD STM AFR ENTERING HP CYLINDER | AI | -100 | 150 | kPa
48477 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CY103 |  | 20MAD10CY103 | AXIAL DISPLACEMENT 1 OF TURB | AI | -2 | 2 | mm |  |  | -1 | 0.8 | [5 empty] | 0 | 1
48478 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CY104 |  | 20MAD10CY104 | AXIAL DISPLACEMENT 2 OF TURB | AI | -2 | 2 | mm |  |  | -1 | 0.8 | [5 empty] | 0 | 1
48479 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD21CY104 |  | 20MAD21CY104 | THERMAL EXPANSION OF HP CYLINDER | AI | -4 | 6 | mm |  |  | -1 | 2.5 | [5 empty] | 0 | 1
48480 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAD10CY105 |  | 20MAD10CY105 | Thermal expansion 1 of turbine | AI | 0 | 35 | mm
48481 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAD10CY106 |  | 20MAD10CY106 | Thermal expansion 2 of turbine | AI | 0 | 35 | mm
48482 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-31 | KALTIM2.SIGNAL.AI.20MAW20CP101 |  | 20MAW20CP101 | P OF THE GATE ROD LEAKAGE STM AND HP CYLINDER SHAFT SEALING STM | AI | 0 | 1 | MPa
48483 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP107 |  | 20MAA01CP107 | Pressure of steam after governing stage | AI | 0 | 16 | MPa
48484 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP108 |  | 20MAA01CP108 | P OF STM AFR NO.5 STAGE | AI | 0 | 6 | MPa
48485 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP109 |  | 20MAA01CP109 | P OF STM AFR NO.8 STAGE | AI | 0 | 4 | MPa
48486 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP110 |  | 20MAA01CP110 | P OF STM AFR NO.11 STAGE | AI | 0 | 16 | MPa
48487 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP111 |  | 20MAA01CP111 | P OF STM AFR NO.14 STAGE | AI | 0 | 6 | MPa
48488 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CP112 |  | 20MAA01CP112 | P OF STM AFR NO.16 STAGE | AI | -0.1 | 0.25 | MPa
48489 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CS104 |  | 20MAD10CS104 | TURB ZERO SPEED | AI | 0 | 100 | rpm
48490 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CS101 |  | 20MAD10CS101 | TURB SPEED 1 | AI | 0 | 5000 | rpm |  |  |  | 3200 | [5 empty] | 1 | 1
48491 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CS102 |  | 20MAD10CS102 | TURB SPEED 2 | AI | 0 | 5000 | rpm |  |  |  | 3200 | [5 empty] | 1 | 1
48492 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CS103 |  | 20MAD10CS103 | TURB SPEED 3 | AI | 0 | 5000 | rpm |  |  |  | 3200 | [5 empty] | 1 | 1
48493 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD10CY102 |  | 20MAD10CY102 | ECCENTRICITY RATIO OF TURB | AI | 0 | 200 | um |  |  |  | 6 | [5 empty] | 1 | 1
49120 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 7 | #2 HP TURBINE | K0102-36 | 20MAA01CT911 |  | 20MAA01CT911 | DELTA EXTERNAL WALL TEMP OF TOP BTM HALF OF STM CYLINDER | CALC | 0 | 800 | C
48494 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT151 |  | 20MAA12CT151 | TEMP 1 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48495 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT152 |  | 20MAA12CT152 | TEMP 2 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48496 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT153 |  | 20MAA12CT153 | TEMP 3 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48497 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT154 |  | 20MAA12CT154 | TEMP 4 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48498 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT155 |  | 20MAA12CT155 | TEMP 5 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48499 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT156 |  | 20MAA12CT156 | TEMP 6 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48500 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT157 |  | 20MAA12CT157 | TEMP 7 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48501 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT158 |  | 20MAA12CT158 | TEMP 8 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48502 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT159 |  | 20MAA12CT159 | TEMP 9 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48503 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAA12CT160 |  | 20MAA12CT160 | TEMP 10 OF THE THRUST TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48504 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC11CT151 |  | 20MAC11CT151 | TEMP 1 OF THE NO.2 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48505 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC11CT152 |  | 20MAC11CT152 | TEMP 2 OF THE NO.2 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48506 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC52CT151 |  | 20MAC52CT151 | Temperature of the NO.2 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48507 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD21CY101 |  | 20MAD21CY101 | SHAFT VIBRATION OF NO.2 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48508 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD21CY102 |  | 20MAD21CY102 | SHAFT VIBRATION OF NO.2 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48509 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD21CY103 |  | 20MAD21CY103 | Vibration of NO.2 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48510 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 8 | #2 TURBINE BEARING NO. 2 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD21CY105 |  | 20MAD21CY105 | Vibration of NO.2 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48511 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC12CT151 |  | 20MAC12CT151 | TEMP 1 OF THE NO.3 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48512 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC12CT152 |  | 20MAC12CT152 | TEMP 2 OF THE NO.3 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48513 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC52CT152 |  | 20MAC52CT152 | Temperature of the NO.3 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48514 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD31CY101 |  | 20MAD31CY101 | SHAFT VIBRATION OF NO.3 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48515 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD31CY102 |  | 20MAD31CY102 | SHAFT VIBRATION OF NO.3 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48516 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD31CY103 |  | 20MAD31CY103 | Vibration of NO.3 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48517 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 9 | #2 TURBINE BEARING NO. 3 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD31CY104 |  | 20MAD31CY104 | Vibration of NO.3 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48518 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAC01CT101 |  | 20MAC01CT101 | TEMP OF STM AFR NO.17 STAGE | TC | 0 | 800 | ℃
48519 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-36 | KALTIM2.SIGNAL.TC.20MAC01CT102 |  | 20MAC01CT102 | TEMP OF STM AFR NO.19 STAGE | TC | 0 | 800 | ℃
48520 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-20 | KALTIM2.SIGNAL.AI.20LCE11CP101 |  | 20LCE11CP101 | DIFF P OF LP CYLINDER WTR SPR FLTR | AI | 0 | 60 | kPa |  |  |  | 30 | [5 empty] | 1
48521 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-24 | KALTIM2.SIGNAL.AI.20MAD41CY104 |  | 20MAD41CY104 | THERMAL EXPANSION OF LP CYLINDER | AI | -4 | 6 | mm | -2.5 |  | -2 | 3.5 | 4 |  |  |  |  | 0
48522 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAC01CP102 |  | 20MAC01CP102 | P OF STM AFR NO.19 STAGE | AI | -0.1 | 0.1 | MPa
48523 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-20 | KALTIM2.SIGNAL.AI.20LCE11CP102 |  | 20LCE11CP102 | P OF LP CYLINDER WTR SPR | AI | 0 | 2.5 | MPa
48524 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 10 | #2 LP TURBINE | K0102-36 | KALTIM2.SIGNAL.AI.20MAC01CP101 |  | 20MAC01CP101 | P OF STM AFR NO.17 STAGE | AI | -0.1 | 0.15 | MPa
48525 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC13CT151 |  | 20MAC13CT151 | TEMP 1 OF THE NO.4 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48526 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC13CT152 |  | 20MAC13CT152 | TEMP 2 OF THE NO.4 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48527 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC53CT151 |  | 20MAC53CT151 | Temperature of the NO.4 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48528 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD41CY101 |  | 20MAD41CY101 | SHAFT VIBRATION OF NO.4 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48529 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD41CY102 |  | 20MAD41CY102 | SHAFT VIBRATION OF NO.4 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48530 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD41CY103 |  | 20MAD41CY103 | Vibration of NO.4 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48531 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 11 | #2 TURBINE BEARING NO. 4 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD41CY105 |  | 20MAD41CY105 | Vibration of NO.4 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48532 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB30AA001XQ12 |  | 20PAB30AA001XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR INLET POSITION | AI | 0 | 100 | %
48533 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB40AA001XQ12 |  | 20PAB40AA001XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET POSITION | AI | 0 | 100 | %
48534 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB40AA101XQ12 |  | 20PAB40AA101XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET POSITION | AI | 0 | 100 | %
48535 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20LCR20AA101XQ12 |  | 20LCR20AA101XQ12 | COND LEVEL REGULATING VLV POSITION | AI | 0 | 100 | %
48536 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB31AA001XQ12 |  | 20PAB31AA001XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR INLET POSITION | AI | 0 | 100 | %
48537 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB41AA001XQ12 |  | 20PAB41AA001XQ12 | MTR VLV OF COND A SIDE CIRCLE WTR OUTLET POSITION | AI | 0 | 100 | %
48538 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB30AA101XQ12 |  | 20PAB30AA101XQ12 | MTR VLV OF COND B SIDE CIRCLE WTR INLET POSITION | AI | 0 | 100 | %
48539 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AO.20LCR20AA101XQ11 |  | 20LCR20AA101XQ11 | COND LEVEL REGULATING VLV ADJ CMD | AO | 0 | 100 | %
48540 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AO.20PAB30AA101XQ11 |  | 20PAB30AA101XQ11 | MTR VLV OF COND B SIDE CIRCLE WTR INLET CMD | AO | 0 | 100 | %
48541 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AO.20PAB40AA101XQ11 |  | 20PAB40AA101XQ11 | MTR VLV OF COND B SIDE CIRCLE WTR OUTLET CMD | AO | 0 | 100 | %
48542 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAJ30BN001XQ01 |  | 20MAJ30BN001XQ01 | A WTR-RING VACUM PMP CURRENT | AI | 0 | 150 | A
48543 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAJ31BN001XQ01 |  | 20MAJ31BN001XQ01 | B WTR-RING VACUM PMP CURRENT | AI | 0 | 100 | A
48544 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.RTD.20MAG10CT101 |  | 20MAG10CT101 | COND TEMP 1 | RTD | 0 | 300 | ℃
48545 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.RTD.20MAG10CT102 |  | 20MAG10CT102 | COND TEMP 2 | RTD | 0 | 300 | ℃
48546 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.RTD.20PAB30CT101 |  | 20PAB30CT101 | TEMP OF COND B SIDE CIRCLE WTR INLET | RTD | 0 | 300 | ℃
48547 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.RTD.20PAB31CT101 |  | 20PAB31CT101 | TEMP OF COND A SIDE CIRCLE WTR INLET | RTD | 0 | 300 | ℃
48548 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.RTD.20PAB40CT101 |  | 20PAB40CT101 | TEMP OF COND B SIDE CIRCLE WTR OUTLET | RTD | 0 | 300 | ℃
48549 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.RTD.20PAB41CT101 |  | 20PAB41CT101 | TEMP OF COND A SIDE CIRCLE WTR OUTLET | RTD | 0 | 300 | ℃
48550 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-32 | KALTIM2.SIGNAL.TC.20LCN10CT101 |  | 20LCN10CT101 | A DRAINS HEADER TEMP | TC | 0 | 800 | ℃
48551 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-32 | KALTIM2.SIGNAL.TC.20LCN10CT102 |  | 20LCN10CT102 | B DRAINS HEADER TEMP | TC | 0 | 800 | ℃
48552 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-32 | KALTIM2.SIGNAL.TC.20LCN20CT101 |  | 20LCN20CT101 | C DRAINS HEADER TEMP | TC | 0 | 800 | ℃
48553 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-32 | KALTIM2.SIGNAL.TC.20LCN20CT102 |  | 20LCN20CT102 | D DRAINS HEADER TEMP | TC | 0 | 800 | ℃
48554 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAJ30CP101 |  | 20MAJ30CP101 | DIFF P OF A WTR-RING VACUM PMP INLET PNEUMATIC VLV INLET AND OUT | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
48555 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAJ31CP101 |  | 20MAJ31CP101 | DIFF P OF B WTR-RING VACUM PMP INLET PNEUMATIC VLV INLET AND OUT | AI | 0 | 100 | kPa |  |  |  | 30 | [5 empty] | 1
48556 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAG10CP101 |  | 20MAG10CP101 | COND P 1 | AI | -100 | 150 | kPa
48557 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAG10CP102 |  | 20MAG10CP102 | COND P 2 | AI | -100 | 150 | kPa
48558 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB30CP101 |  | 20PAB30CP101 | DIFF P BETWEEN B TWICE FLTR INLET AND OUTLET | AI | 0 | 200 | kPa |  |  |  | 30 | [5 empty] | 1
48559 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB30CP102 |  | 20PAB30CP102 | P OF COND B SIDE CIRCLE WTR INLET | AI | 0 | 400 | KPa
48560 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB31CP101 |  | 20PAB31CP101 | DIFF P BETWEEN A TWICE FLTR INLET AND OUTLET | AI | 0 | 200 | kPa |  |  |  | 30 | [5 empty] | 1
48561 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB31CP102 |  | 20PAB31CP102 | P OF COND A SIDE CIRCLE WTR INLET | AI | 0 | 400 | KPa
48562 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB40CP101 |  | 20PAB40CP101 | P OF COND B SIDE CIRCLE WTR OUTLET | AI | 0 | 400 | KPa
48563 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-35 | KALTIM2.SIGNAL.AI.20PAB41CP101 |  | 20PAB41CP101 | P OF COND A SIDE CIRCLE WTR OUTLET | AI | 0 | 400 | KPa
48564 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAG10CP101A |  | 20MAG10CP101A | COND VACUUM P1 | AI | -100 | 0 | KPa
48565 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-22 | KALTIM2.SIGNAL.AI.20MAG10CP102A |  | 20MAG10CP102A | COND VACUUM P2 | AI | -100 | 0 | KPa
48566 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL101 |  | 20MAG10CL101 | Condenser hot well level 1 | AI | 0 | 1200 | mm
48567 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL102 |  | 20MAG10CL102 | Condenser hot well level 2 | AI | 0 | 1500 | mm
48568 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL103 |  | 20MAG10CL103 | Condenser hot well level 3 | AI | 0 | 1200 | mm
48569 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL104 |  | 20MAG10CL104 | Condenser hot well level 4 | AI | 0 | 1500 | mm
48570 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL105 |  | 20MAG10CL105 | COND BACK WTR CHAMBER LEVEL 1 | AI | 0 | 1500 | mm
48571 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-20 | KALTIM2.SIGNAL.AI.20MAG10CL106 |  | 20MAG10CL106 | COND BACK WTR CHAMBER LEVEL 2 | AI | 0 | 1500 | mm
48572 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR | K0102-32 | KALTIM2.SIGNAL.AI.20LCN20CP101 |  | 20LCN20CP101 | B PROPER FLASH DRAIN TANK P | AI | 0 | 1.2 | MPa
49122 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 12 | #2 CONDENSOR |  | 20MAG10CP901 |  | 20MAG10CP901 | Condenser Vacuum | CALC | -100 | 150 | kPa | [8 empty] | AVG((KALTIM2.SIGNAL.AI.20MAG10CP101);(KALTIM2.SIGNAL.AI.20MAG10CP102)
48573 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.AI.20MAW35AA101XQ12 |  | 20MAW35AA101XQ12 | Main steam to aux steam pre relief valve feedback | AI | 0 | 100 | %
48574 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.AO.20MAW35AA101XQ11 |  | 20MAW35AA101XQ11 | Main steam to aux steam pre relief valve cmd | AO | 0 | 100 | %
48575 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-23 | KALTIM2.SIGNAL.TC.20LBG23CT101 |  | 20LBG23CT101 | TEMP OF THE STM FROM AUX STM TO GLD STM SYSTEM | TC | 0 | 800 | ℃
48576 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.TC.20MAW31CT101 |  | 20MAW31CT101 | TEMP OF SHAFT SEALING STM MAIN PIP | TC | 0 | 800 | ℃
48577 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.TC.20MAW33CT101 |  | 20MAW33CT101 | STM TEMP OF STM MIXER | TC | 0 | 800 | ℃
48578 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.AI.20MAW31CP101 |  | 20MAW31CP101 | P OF SHAFT SEALING STM MAIN PIP | AI | 0 | 250 | kPa
48579 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-31 | KALTIM2.SIGNAL.AI.20MAW33CP101 |  | 20MAW33CP101 | STM P OF STM MIXER | AI | 0 | 0.4 | MPa
48580 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 13 | #2 STEAM SEAL SYSTEM | K0102-23 | KALTIM2.SIGNAL.AI.20LBG23CP101 |  | 20LBG23CP101 | P OF THE STM FROM AUX STM TO GLD STM SYSTEM | AI | 0 | 1.6 | MPa
48581 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AI.20LCE19AA101XQ12 |  | 20LCE19AA101XQ12 | Turbine bypass water spray control valve position | AI | 0 | 100 | %
48582 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AI.20MAN10AA101XQ12 |  | 20MAN10AA101XQ12 | Turbine bypass temperature and pressure reduction valve position | AI | 0 | 100 | %
48583 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM2.SIGNAL.AI.20LCE18AA101XQ12 |  | 20LCE18AA101XQ12 | COND SECONDARY DTR WTR SPR CTRL VLV 1 POSITION | AI | 0 | 100 | %
48584 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM2.SIGNAL.AI.20LCE18AA102XQ12 |  | 20LCE18AA102XQ12 | COND SECONDARY DTR WTR SPR CTRL VLV 2 POSITION | AI | 0 | 100 | %
48585 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AO.20LCE19AA101XQ11 |  | 20LCE19AA101XQ11 | Turbine bypass water spray control valve adjust command | AO | 0 | 100 | %
48586 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AO.20MAN10AA101XQ11 |  | 20MAN10AA101XQ11 | Turbine bypass temperature and pressure reduction valve adjust c | AO | 0 | 100 | %
48587 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM2.SIGNAL.AO.20LCE18AA101XQ11 |  | 20LCE18AA101XQ11 | COND SECONDARY DTR WTR SPR CTRL VLV 1 ADJ CMD | AO | 0 | 100 | %
48588 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-20 | KALTIM2.SIGNAL.AO.20LCE18AA102XQ11 |  | 20LCE18AA102XQ11 | COND SECONDARY DTR WTR SPR CTRL VLV 2 ADJ CMD | AO | 0 | 100 | %
48589 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.RTD.20LCE18CT101 |  | 20LCE18CT101 | SECONDARY DTR OUTLET WTR TEMP 1 | RTD | 0 | 300 | ℃
48590 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.RTD.20LCE18CT102 |  | 20LCE18CT102 | SECONDARY DTR OUTLET WTR TEMP 2 | RTD | 0 | 300 | ℃
48591 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.TC.20MAN10CT101 |  | 20MAN10CT101 | STM TEMP AFR HP BYP VLV | TC | 0 | 800 | ℃
48592 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AI.20LCE19CP101 |  | 20LCE19CP101 | DTR WTR P OF HP BYP VLV | AI | 0 | 3 | MPa
48593 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 14 | #2 TURBINE BYPASS SYSTEM | K0102-17 | KALTIM2.SIGNAL.AI.20MAN10CP101 |  | 20MAN10CP101 | STM P AFR HP BYP VLV | AI | 0 | 1 | MPa
48594 | 2 | UJKTT #2 | 7 | #2 TURBINE SYSTEM | 15 | #2 TURNING GEAR | K0102-36 | KALTIM2.SIGNAL.AI.20MAA01CS101XQ01 |  | 20MAA01CS101XQ01 | Emergency intercepter indicator current output | AI | 0 | 100 | %
48595 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC14CT151 |  | 20MAC14CT151 | TEMP 1 OF THE NO.5 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48596 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC14CT152 |  | 20MAC14CT152 | TEMP 2 OF THE NO.5 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48597 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-25 | KALTIM2.SIGNAL.RTD.20MAC53CT152 |  | 20MAC53CT152 | Temperature of the NO.5 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48598 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD51CY101 |  | 20MAD51CY101 | SHAFT VIBRATION OF NO.5 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48599 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD51CY102 |  | 20MAD51CY102 | SHAFT VIBRATION OF NO.5 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48600 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD51CY103 |  | 20MAD51CY103 | Vibration of NO.5 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48601 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 1 | #2 GENERATOR BEARING NO. 5 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD51CY104 |  | 20MAD51CY104 | Vibration of NO.5 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48602 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE018 |  | 20MKA01CE018 | Gen. Active Power | AI | 0 | 100 | %
48603 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE021 |  | 20MKA01CE021 | Gen. Active Power | AI | 0 | 100 | %
48604 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AO.20CBA01XQ11 |  | 20CBA01XQ11 | Remote control load set value | AO | 0 | 100 | %
48605 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE001 |  | 20MKA01CE001 | #2 Gen. Current (A Phase) | AI | 0 | 8000 | A
48606 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE002 |  | 20MKA01CE002 | #2 Gen. Current (B Phase) | AI | 0 | 8000 | A
48607 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE003 |  | 20MKA01CE003 | #2 Gen. Current (C Phase) | AI | 0 | 8000 | A
48608 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE011 |  | 20MKA01CE011 | #2 Gen. Negative Sequence Current | AI | 0 | 100 | A
48609 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE012 |  | 20MKA01CE012 | #2 Gen. Zero Sequence Current | AI | 0 | 50 | A
48610 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKC01CE002 |  | 20MKC01CE002 | #2 Gen. Field Current | AI | 0 | 2500 | A
48611 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT101 |  | 20MKA10CT101 | GEN STATOR WINDING TEMP 1 | RTD | 0 | 300 | ℃
48612 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT102 |  | 20MKA10CT102 | GEN STATOR WINDING TEMP 2 | RTD | 0 | 300 | ℃
48613 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT103 |  | 20MKA10CT103 | GEN STATOR WINDING TEMP 3 | RTD | 0 | 300 | ℃
48614 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT104 |  | 20MKA10CT104 | GEN STATOR WINDING TEMP 4 | RTD | 0 | 300 | ℃
48615 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT105 |  | 20MKA10CT105 | GEN STATOR WINDING TEMP 5 | RTD | 0 | 300 | ℃
48616 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT106 |  | 20MKA10CT106 | GEN STATOR WINDING TEMP 6 | RTD | 0 | 300 | ℃
48617 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT107 |  | 20MKA10CT107 | GEN STATOR CORE TEMP 1 (TURB END) | RTD | 0 | 300 | ℃
48618 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT108 |  | 20MKA10CT108 | GEN STATOR CORE TEMP 2 (TURB END) | RTD | 0 | 300 | ℃
48619 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT109 |  | 20MKA10CT109 | GEN STATOR CORE TEMP 1 (MIDDLE) | RTD | 0 | 300 | ℃
48620 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT110 |  | 20MKA10CT110 | GEN STATOR CORE TEMP 2 (MIDDLE) | RTD | 0 | 300 | ℃
48621 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT111 |  | 20MKA10CT111 | GEN STATOR CORE TEMP 1 (EXCITER END) | RTD | 0 | 300 | ℃
48622 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA10CT112 |  | 20MKA10CT112 | GEN STATOR CORE TEMP 2 (EXCITER END) | RTD | 0 | 300 | ℃
48623 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA20CT101 |  | 20MKA20CT101 | TEMP OF GEN STATOR AIR INLET (TURB END) | RTD | 0 | 300 | ℃
48624 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA20CT102 |  | 20MKA20CT102 | TEMP OF GEN STATOR AIR INLET (EXCITER END) | RTD | 0 | 300 | ℃
48625 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA20CT103 |  | 20MKA20CT103 | TEMP OF GEN STATOR AIR OUTLET (TURB END) | RTD | 0 | 300 | ℃
48626 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR | K0102-36 | KALTIM2.SIGNAL.RTD.20MKA20CT104 |  | 20MKA20CT104 | TEMP OF GEN STATOR AIR OUTLET (EXCITER END) | RTD | 0 | 300 | ℃
48627 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20CBA01XQ03 |  | 20CBA01XQ03 | Frequency correction | AI | 0 | 100 | Hz
48628 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE009 |  | 20MKA01CE009 | #2 Gen. Frequency | AI | 48 | 52 | HZ
48629 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE006 |  | 20MKA01CE006 | #2 Gen. Stator Voltage(A-B) | AI | 0 | 17.94 | kV
48630 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE007 |  | 20MKA01CE007 | #2 Gen. Stator Voltage(B-C) | AI | 0 | 17.94 | kV
48631 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE008 |  | 20MKA01CE008 | #2 Gen. Stator Voltage(A-C) | AI | 0 | 17.94 | kV
48632 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE005 |  | 20MKA01CE005 | #2 Gen. Reactive Power | AI | -132 | 132 | MVAR
48633 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20CBA01XQ01 |  | 20CBA01XQ01 | Load reference | AI | 0 | 100 | MW
48634 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE004 |  | 20MKA01CE004 | #2 Gen. Active Power | AI | 0 | 132 | MW
48635 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE013 |  | 20MKA01CE013 | #2 Gen. Zero Sequence Voltage | AI | 0 | 100 | V
48636 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKC01CE001 |  | 20MKC01CE001 | #2 Gen. Field Voltage | AI | 0 | 350 | V
48637 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20AGC3026 |  | 20AGC3026 | CURRENT GROSS | AI | 0 | 100
48638 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20MKA01CE010 |  | 20MKA01CE010 | #2 Gen. Power Factor | AI | 0.5 | 1.5
48639 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20AGC3027 |  | 20AGC3027 | GEN VAR HIGH LIMIT | AI | 0 | 100
48640 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20AGC3028 |  | 20AGC3028 | GEN VAR LOW LIMIT | AI | 0 | 100
48641 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20AGC3029 |  | 20AGC3029 | GEN POWER FACTOR | AI | 0 | 100
48642 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.20AGC5001 |  | 20AGC5001 | AGC DEMAND POWER | AI | 0 | 65535
48881 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.U2AMDMDMW |  | U2AMDMDMW | LOAD DEMAND | AI | 0 | 150 | MW
48882 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 2 | #2 GENERATOR |  | KALTIM2.SIGNAL.AI.U2AM12MCS0004 |  | U2AM12MCS0004 | UNIT LODA CMD SET | AI | 0 | 150 | MW
48643 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-25 | KALTIM2.SIGNAL.RTD.20MKD11CT151 |  | 20MKD11CT151 | TEMP OF THE NO.6 BEARING TILE | RTD | 0 | 300 | ℃ |  |  |  | 105 | 110 |  |  |  |  | 1 | 1
48644 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-25 | KALTIM2.SIGNAL.RTD.20MKD12CT151 |  | 20MKD12CT151 | Temperature of the NO.6 bearing tile return oil | RTD | 0 | 300 | ℃ |  |  |  |  | 75
48645 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD61CY101 |  | 20MAD61CY101 | SHAFT VIBRATION OF NO.6 BEARING IN THE X DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48646 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD61CY102 |  | 20MAD61CY102 | SHAFT VIBRATION OF NO.6 BEARING IN THE Y DIRECTION | AI | 0 | 400 | um |  |  |  | 150 | [5 empty] | 1 | 1
48647 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD61CY103 |  | 20MAD61CY103 | Vibration of NO.6 bearing in the X direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48648 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 3 | #2 GENERATOR BEARING NO. 6 | K0102-24 | KALTIM2.SIGNAL.AI.20MAD61CY104 |  | 20MAD61CY104 | Vibration of NO.6 bearing in the Y direction | AI | 0 | 200 | um |  |  |  | 120 | [5 empty] | 1 | 1
48649 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 4 | #2 GENERATOR AIR COOLER SET | K0102-34 | KALTIM2.SIGNAL.AI.20PGB75AA101XQ12 |  | 20PGB75AA101XQ12 | CTRL VLV OF GEN AIR COOLER COOLING WTR OUTLET PSN | AI | 0 | 100 | %
48650 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 4 | #2 GENERATOR AIR COOLER SET | K0102-34 | KALTIM2.SIGNAL.AO.20PGB75AA101XQ11 |  | 20PGB75AA101XQ11 | CTRL VLV OF GEN AIR COOLER COOLING WTR OUTLET ADJ CMD | AO | 0 | 100 | %
48651 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 4 | #2 GENERATOR AIR COOLER SET | K0102-34 | KALTIM2.SIGNAL.RTD.20PGB75CT101 |  | 20PGB75CT101 | WTR TEMP OF GEN AIR COOLER COOLING WTR OUTLET | RTD | 0 | 300 | ℃
48652 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE001 |  | 20BAT01CE001 | #2 Gen. Tran. HV Side Current (A Phase) | AI | 0 | 800 | A
48653 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE002 |  | 20BAT01CE002 | #2 Gen. Tran. HV Side Current (B Phase) | AI | 0 | 800 | A
48654 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE003 |  | 20BAT01CE003 | #2 Gen. Tran. HV Side Current (C Phase) | AI | 0 | 800 | A
48655 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE011 |  | 20BAT01CE011 | #2 Gen. Tran. Oil Temperature 1 | AI | 0 | 150 | ℃
48656 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE012 |  | 20BAT01CE012 | #2 Gen. Tran. Oil Temperature 2 | AI | 0 | 150 | ℃
48657 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE013 |  | 20BAT01CE013 | #2 Gen. Tran. Winding Temperature | AI | 0 | 150 | ℃
48658 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE009 |  | 20BAT01CE009 | #2 Gen. Tran. HV Side Frequency | AI | 48 | 52 | HZ
48659 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE004 |  | 20BAT01CE004 | #2 Gen. Tran. HV Side Voltage(A-B) | AI | 0 | 195 | kV
48660 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE005 |  | 20BAT01CE005 | #2 Gen. Tran. HV Side Voltage(B-C) | AI | 0 | 195 | kV
48661 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE006 |  | 20BAT01CE006 | #2 Gen. Tran. HV Side Voltage(A-C) | AI | 0 | 195 | kV
48662 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE008 |  | 20BAT01CE008 | #2 Gen. Tran. HV Side Reactive Power | AI | -156 | 156 | MVAR
48663 | 2 | UJKTT #2 | 8 | #2 GENERATOR SYSTEM | 5 | #2 GENERATOR TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BAT01CE007 |  | 20BAT01CE007 | #2 Gen. Tran. HV Side Active Power | AI | -156 | 156 | MW
48664 | 2 | UJKTT #2 | 9 | #2 EXCITATION SYSTEM | 1 | #2 TRANSFORMER EXCITATION |  | KALTIM2.SIGNAL.AI.20MKT01CE001 |  | 20MKT01CE001 | #2 Excit. Tran. HV Side Current (B Phase) | AI | 0 | 100 | A
48665 | 2 | UJKTT #2 | 9 | #2 EXCITATION SYSTEM | 1 | #2 TRANSFORMER EXCITATION |  | KALTIM2.SIGNAL.AI.20MKT01CE002 |  | 20MKT01CE002 | #2 Excit. Tran. HV Side Active Power | AI | 0 | 1320 | kW
48666 | 2 | UJKTT #2 | 9 | #2 EXCITATION SYSTEM | 1 | #2 TRANSFORMER EXCITATION |  | KALTIM2.SIGNAL.AI.20MKT01CE003 |  | 20MKT01CE003 | #2 Excit. Tran. HV Side Reactive Power | AI | 0 | 1320 | KWAR
48667 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 1 | #2 TRASH RACK | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB11LT101 |  | 20PAB11LT101 | Level of water before Trash rack C | AI | -7 | 5.3 | m
48668 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 1 | #2 TRASH RACK | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB12LT101 |  | 20PAB12LT101 | Level of water before Trash rack D | AI | -7 | 5.3 | m
48669 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 2 | #2 TRAVELING SCREEN C | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB21LT101 |  | 20PAB21LT101 | Level of water before Traveling screen C | AI | 0 | 12 | m | 5 |  |  |  | 8.4
48670 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 2 | #2 TRAVELING SCREEN C | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB21LT102 |  | 20PAB21LT102 | Level of water after Traveling screen C | AI | 0 | 12 | m | 5 |  |  |  | 8.4
48671 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 3 | #2 TRAVELING SCREEN D | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB22LT101 |  | 20PAB22LT101 | Level of water before Traveling screen D | AI | 0 | 12 | m | 5 |  |  |  | 8.4
48672 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 3 | #2 TRAVELING SCREEN D | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB22LT102 |  | 20PAB22LT102 | Level of water after Traveling screen D | AI | 0 | 12 | m | 5 |  |  |  | 8.4
48673 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41AP001XQ01 |  | 20PAB41AP001XQ01 | #2 Unit cwp A motor current | AI | 0 | 150 | A
48674 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT116 |  | 20PAB41CT116 | #2 Unit cwp A motor widing temp. 6 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48675 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT111 |  | 20PAB41CT111 | #2 Unit cwp A motor widing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48676 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT112 |  | 20PAB41CT112 | #2 Unit cwp A motor widing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48677 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT113 |  | 20PAB41CT113 | #2 Unit cwp A motor widing temp. 3 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48678 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT114 |  | 20PAB41CT114 | #2 Unit cwp A motor widing temp. 4 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48679 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT115 |  | 20PAB41CT115 | #2 Unit cwp A motor widing temp. 5 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48680 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT117 |  | 20PAB41CT117 | #2 Unit cwp A thrust bearing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48681 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CT118 |  | 20PAB41CT118 | #2 Unit cwp A thrust bearing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48682 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CF101 |  | 20PAB41CF101 | #2 Unit cwp A outlet flow | AI | 0 | 4 | m3/h
48683 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CY101X |  | 20PAB41CY101X | #2 Unit cwp A bearing vibration (x direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48684 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CY101Y |  | 20PAB41CY101Y | #2 Unit cwp A bearing vibration (y direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48685 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CP102 |  | 20PAB41CP102 | Pressure Hidraulic CWP #2 A | AI | 0 | 20 | MPa
48686 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 4 | #2 CIRCULATING WATER PUMP 1A | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB41CP111 |  | 20PAB41CP111 | #2 Unit cwp A Cwp outlet press | AI | 0 | 0.3 | MPa
48687 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42AP001XQ01 |  | 20PAB42AP001XQ01 | #2 Unit cwp B motor current | AI | 0 | 150 | A
48688 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT116 |  | 20PAB42CT116 | #2 Unit cwp B motor widing temp. 6 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48689 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT111 |  | 20PAB42CT111 | #2 Unit cwp B motor widing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48690 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT112 |  | 20PAB42CT112 | #2 Unit cwp B motor widing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48691 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT113 |  | 20PAB42CT113 | #2 Unit cwp B motor widing temp. 3 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48692 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT114 |  | 20PAB42CT114 | #2 Unit cwp B motor widing temp. 4 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48693 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT115 |  | 20PAB42CT115 | #2 Unit cwp B motor widing temp. 5 | AI | 0 | 300 | ℃ |  |  |  | 110 | 120 |  |  |  |  | 1 | 1
48694 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT117 |  | 20PAB42CT117 | #2 Unit cwp B thrust bearing temp. 1 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48695 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CT118 |  | 20PAB42CT118 | #2 Unit cwp B thrust bearing temp. 2 | AI | 0 | 300 | ℃ |  |  |  | 80 | 90 |  |  |  |  | 1 | 1
48696 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CF101 |  | 20PAB42CF101 | #2 Unit Cwp A outlet flow | AI | 0 | 4 | m3/h
48697 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CY101X |  | 20PAB42CY101X | #2 Unit cwp B bearing vibration (x direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48698 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CY101Y |  | 20PAB42CY101Y | #2 Unit cwp B bearing vibration (y direction) | AI | 0 | 20 | mm/s |  |  |  | 6.3 | 7.1 |  |  |  |  | 1 | 1
48699 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CP102 |  | 20PAB42CP102 | Pressure Hidraulic CWP #2 B | AI | 0 | 20 | MPa
48700 | 2 | UJKTT #2 | 10 | #2 CIRCULATING WATER SYSTEM | 5 | #2 CIRCULATING WATER PUMP 1B | K0603-02 | KALTIM 0.SIGNAL.AI.20PAB42CP111 |  | 20PAB42CP111 | #2 Unit cwp B outlet press | AI | 0 | 0.3 | MPa
48701 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 1 | #2 220V DC SYSTEM 1 |  | KALTIM2.SIGNAL.AI.20BUD02CE002 |  | 20BUD02CE002 | #2 Unit 220V DC System No.1 Charge panel charger current | AI | 0 | 100 | A
48702 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 1 | #2 220V DC SYSTEM 1 |  | KALTIM2.SIGNAL.AI.20BUD03CE002 |  | 20BUD03CE002 | #2 Unit 220V DC System No.1 connect panel battery current | AI | 0 | 100 | A
48703 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 1 | #2 220V DC SYSTEM 1 |  | KALTIM2.SIGNAL.AI.20BUD02CE001 |  | 20BUD02CE001 | #2 Unit 220V DC System No.1 Charge panel charger voltage | AI | 0 | 100 | V
48704 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 1 | #2 220V DC SYSTEM 1 |  | KALTIM2.SIGNAL.AI.20BUD03CE001 |  | 20BUD03CE001 | #2 Unit 220V DC System No.1 connect panel battery voltage | AI | 0 | 100 | V
48705 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 1 | #2 220V DC SYSTEM 1 |  | KALTIM2.SIGNAL.AI.20BUD03CE003 |  | 20BUD03CE003 | #2 Unit 220V DC System No.1 connect panel bus I voltage | AI | 0 | 100 | V
48706 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 2 | #2 220V DC SYSTEM 2 |  | KALTIM2.SIGNAL.AI.20BUD04CE002 |  | 20BUD04CE002 | #2 Unit 220V DC System No.2 connect panel battery current | AI | 0 | 100 | A
48707 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 2 | #2 220V DC SYSTEM 2 |  | KALTIM2.SIGNAL.AI.20BUD05CE002 |  | 20BUD05CE002 | #2 Unit 220V DC System No.2 Charge panel charger current | AI | 0 | 100 | A
48708 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 2 | #2 220V DC SYSTEM 2 |  | KALTIM2.SIGNAL.AI.20BUD04CE001 |  | 20BUD04CE001 | #2 Unit 220V DC System No.2 connect panel battery voltage | AI | 0 | 100 | V
48709 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 2 | #2 220V DC SYSTEM 2 |  | KALTIM2.SIGNAL.AI.20BUD04CE003 |  | 20BUD04CE003 | #2 Unit 220V DC System No.2 connect panel bus II voltage | AI | 0 | 100 | V
48710 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 2 | #2 220V DC SYSTEM 2 |  | KALTIM2.SIGNAL.AI.20BUD05CE001 |  | 20BUD05CE001 | #2 Unit 220V DC System No.2 Charge panel charger voltage | AI | 0 | 100 | V
48711 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 3 | #2 UPS |  | KALTIM2.SIGNAL.AI.20BRA03CE002 |  | 20BRA03CE002 | #2 Unit UPS Output AC Current | AI | 0 | 100 | A
48712 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 3 | #2 UPS |  | KALTIM2.SIGNAL.AI.20BRA03CE003 |  | 20BRA03CE003 | #2 Unit UPS Output Frequency | AI | 48 | 52 | HZ
48713 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 3 | #2 UPS |  | KALTIM2.SIGNAL.AI.20BRA03CE001 |  | 20BRA03CE001 | #2 Unit UPS Output AC Voltage | AI | 0 | 600 | V
48714 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 4 | #2 LV AUXILIARY POWER TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BBA11CE001 |  | 20BBA11CE001 | #2 LV Auxiliary Power TR. A current at 6kV side | AI | 0 | 300 | A
48715 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 4 | #2 LV AUXILIARY POWER TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BBA12CE001 |  | 20BBA12CE001 | #2 LV Auxiliary Power TR. B current at 6kV side | AI | 0 | 300 | A
48716 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA02CE001 |  | 20BBA02CE001 | 6kV unit board bus-tie CB current | AI | 0 | 2000 | A
48717 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA04CE001 |  | 20BBA04CE001 | 6kV unit board II to 6kV comm board No.1 power feeder CB current | AI | 0 | 1000 | A
48718 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA01CE001 |  | 20BBA01CE001 | 6kV unit board II incoming PT voltage for AC phase | AI | 0 | 9.45 | kV
48719 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA15CE001 |  | 20BBA15CE001 | 6kV Unit Board II phase AB voltage | AI | 0 | 10.47 | kV
48720 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA15CE002 |  | 20BBA15CE002 | 6kV Unit Board II phase BC voltage | AI | 0 | 10.47 | kV
48721 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 5 | #2 MV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BBA15CE003 |  | 20BBA15CE003 | 6kV Unit Board II phase CA voltage | AI | 0 | 10.47 | kV
48722 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 6 | #2 CW AUXILIARY POWER TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BBA13CE001 |  | 20BBA13CE001 | #2 Circulating Water TR. current at 6kV side | AI | 0 | 100 | A
48723 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 7 | #2 ESP AUXILIARY POWER TRANSFORMER |  | KALTIM2.SIGNAL.AI.20BBA14CE001 |  | 20BBA14CE001 | #2 ESP TR. current at 6kV side | AI | 0 | 200 | A
48724 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE001 |  | 20BBT01CE001 | #2 Unit Aux. Tran. phase B current | AI | 0 | 1500 | A
48725 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE011 |  | 20BBT01CE011 | #2 Unit Aux. Tran. winding temperature | AI | 0 | 150 | ℃
48726 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE012 |  | 20BBT01CE012 | #2 Unit Aux. Tran. oil temperature 1 | AI | 0 | 150 | ℃
48727 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE013 |  | 20BBT01CE013 | #2 Unit Aux. Tran. oil temperature 2 | AI | 0 | 150 | ℃
48728 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE003 |  | 20BBT01CE003 | #2 Unit Aux. Tran. reactive power | AI | 0 | 34.8 | MVAR
48729 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 8 | #2 UNIT AUXILIARY TRANFORMER |  | KALTIM2.SIGNAL.AI.20BBT01CE002 |  | 20BBT01CE002 | #2 Unit Aux. Tran. active power | AI | 0 | 34.8 | MW
48730 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA02ACE001 |  | 20BFA02ACE001 | #2 Unit service PDC bus-tie CB current | AI | 0 | 800 | A
48731 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA03BCE001 |  | 20BFA03BCE001 | Unit service MCC II B board No.1 power feeder current | AI | 0 | 800 | A
48732 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA04ACE001 |  | 20BFA04ACE001 | Common service MCC A board No.2 power feeder current | AI | 0 | 100 | A
48733 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA05BCE001 |  | 20BFA05BCE001 | #2 emergency power supply IIB board power 1 CB current | AI | 0 | 500 | A
48734 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB02ACE001 |  | 20BFB02ACE001 | Coal bunkey belt conveyor MCC board No.2 power feeder current | AI | 0 | 100 | A
48735 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB03ACE001 |  | 20BFB03ACE001 | Unit service MCC II A board No.2 power feeder current | AI | 0 | 800 | A
48736 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB03BCE001 |  | 20BFB03BCE001 | Unit service MCC II B board No.2 power feeder current | AI | 0 | 800 | A
48737 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB04ACE001 |  | 20BFB04ACE001 | Common service MCC B board No.2 power feeder current | AI | 0 | 100 | A
48738 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB04BCE001 |  | 20BFB04BCE001 | #2 emergency power supply IIA board power 2 CB current | AI | 0 | 500 | A
48739 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMA01BCE001 |  | 20BMA01BCE001 | Incoming CB II of 400/230V emergency power supply IIA board (K26 | AI | 0 | 100 | A
48740 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMA02ACE001 |  | 20BMA02ACE001 | Incoming CB III of 400/230V emergency power supply IIA board K23 | AI | 0 | 100 | A
48741 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMB02ACE001 |  | 20BMB02ACE001 | Incoming CB III of 400/230V emergency power supply IIB board K24 | AI | 0 | 100 | A
48742 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA03ACE001 |  | 20BFA03ACE001 | Unit service MCC II A board No.1 power feeder current | AI | 0 | 800 | A
48743 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA04BCE001 |  | 20BFA04BCE001 | #2 emergency power supply IIA board power 1 CB current | AI | 0 | 500 | A
48744 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB05BCE001 |  | 20BFB05BCE001 | #2 emergency power supply IIB board power 2 CB current | AI | 0 | 500 | A
48745 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMA01ACE001 |  | 20BMA01ACE001 | Incoming CB I of 400/230V emergency power supply IIA board (K25) | AI | 0 | 100 | A
48746 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMB01ACE001 |  | 20BMB01ACE001 | Incoming CB I of 400/230V emergency power supply IIB board (K27) | AI | 0 | 100 | A
48747 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMB01BCE001 |  | 20BMB01BCE001 | Incoming CB II of 400/230V emergency power supply IIB board (K28 | AI | 0 | 100 | A
48748 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFA01BCE002 |  | 20BFA01BCE002 | #2 Power house PDC A board incoming PT voltage for AC phase | AI | 0 | 400 | V
48749 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BFB01ACE002 |  | 20BFB01ACE002 | #2 Power house PDC B board incoming PT voltage for AC phase | AI | 0 | 400 | V
48750 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BHA01BCE002 |  | 20BHA01BCE002 | #2 ESP. PDC A board incoming PT voltage for AC phase | AI | 0 | 400 | V
48751 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMA02BCE001 |  | 20BMA02BCE001 | Emergency power supply IIA board PT phase AC voltage | AI | 0 | 400 | V
48752 | 2 | UJKTT #2 | 11 | #2 POWER TRANSFORMER SYSTEM | 9 | #2 LV AUXILIARY POWER DISTRIBUTION |  | KALTIM2.SIGNAL.AI.20BMB02BCE001 |  | 20BMB02BCE001 | Emergency power supply IIB board PT phase AC voltage | AI | 0 | 400 | V
48753 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 1 | #2 MAIN OIL TANK | K0102-25 | KALTIM2.SIGNAL.AI.20MAU12CL101 |  | 20MAU12CL101 | LUBE OIL TANK LEVEL 1 | AI | 0 | 600 | mm |  |  | -100 | 100 | [5 empty] | 0 | 1
48754 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 1 | #2 MAIN OIL TANK | K0102-25 | KALTIM2.SIGNAL.AI.20MAU12CL102 |  | 20MAU12CL102 | LUBE OIL TANK LEVEL 2 | AI | 0 | 600 | mm |  |  | -100 | 100 | [5 empty] | 0 | 1
48755 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 2 | #2 DC OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30AP004XQ01 |  | 20MAU30AP004XQ01 | DC LUBE OIL PMP CURRENT | AI | 0 | 100 | %
48756 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 2 | #2 DC OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30CP103 |  | 20MAU30CP103 | OIL P 6 OF DC LUBE OIL PMP OUTLET | AI | 0 | 0.6 | MPa
48757 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 3 | #2 AC OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30AP003XQ01 |  | 20MAU30AP003XQ01 | AC LUBE OIL PMP CURRENT | AI | 0 | 100 | A
48758 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 3 | #2 AC OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30CP102 |  | 20MAU30CP102 | OIL P 6 OF AC LUBE OIL PMP OUTLET | AI | 0 | 0.6 | MPa
48759 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 4 | #2 HP OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30AP002XQ01 |  | 20MAU30AP002XQ01 | HP START-UP OIL PMP CURRENT | AI | 0 | 300 | A
48760 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 4 | #2 HP OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU30CP101 |  | 20MAU30CP101 | OIL P 6 OF HP START-UP OIL PMP OUTLET | AI | 0 | 2.5 | MPa
48761 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 5 | #2 MAIN OIL PUMP | K0102-36 | KALTIM2.SIGNAL.AI.20MAU20CP105 |  | 20MAU20CP105 | RESET OIL P | AI | 0 | 4 | MPa
48762 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 5 | #2 MAIN OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU20CP101 |  | 20MAU20CP101 | OIL P OF MAIN LUBE OIL PMP INLET | AI | 0 | 0.4 | MPa
48763 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 5 | #2 MAIN OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU20CP102 |  | 20MAU20CP102 | OIL P BFR CHK OF MAIN LUBE OIL PMP OUTLET | AI | 0 | 4 | MPa
48764 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 5 | #2 MAIN OIL PUMP | K0102-25 | KALTIM2.SIGNAL.AI.20MAU20CP103 |  | 20MAU20CP103 | OIL P AFR CHK OF MAIN LUBE OIL PMP OUTLET | AI | 0 | 4 | MPa
48765 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB50AA101XQ12 |  | 20PGB50AA101XQ12 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER PSN | AI | 0 | 100 | %
48766 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.AO.20PGB50AA101XQ11 |  | 20PGB50AA101XQ11 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER ADJ CMD | AO | 0 | 100 | %
48767 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-25 | KALTIM2.SIGNAL.RTD.20MAV12CT101 |  | 20MAV12CT101 | OIL TEMP OF A LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃
48768 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-25 | KALTIM2.SIGNAL.RTD.20MAV12CT102 |  | 20MAV12CT102 | OIL TEMP OF A LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
48769 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB50CT101 |  | 20PGB50CT101 | WTR TEMP OF TURB LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
49108 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.AO.20PGB50AA101XQ11 |  | 20PGB50AA101XQ11 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER ADJ CMD | AO | 0 | 100 | %
49109 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB50AA101XQ12 |  | 20PGB50AA101XQ12 | WTR INLET CTRL VLV OF TURB LUBE OIL COOLER PSN | AI | 0 | 100 | %
49110 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 6 | #2 LUBE OIL COOLER A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB50CT101 |  | 20PGB50CT101 | WTR TEMP OF TURB LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
48770 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 7 | #2 LUBE OIL COOLER B | K0102-25 | KALTIM2.SIGNAL.RTD.20MAV13CT101 |  | 20MAV13CT101 | OIL TEMP OF B LUBE OIL COOLER INLET | RTD | 0 | 300 | ℃
48771 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 7 | #2 LUBE OIL COOLER B | K0102-25 | KALTIM2.SIGNAL.RTD.20MAV13CT102 |  | 20MAV13CT102 | OIL TEMP OF B LUBE OIL COOLER OUTLET | RTD | 0 | 300 | ℃
48772 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 8 | #2 JACKING OIL PUMP A | K0102-25 | KALTIM2.SIGNAL.AI.20MAU40AP001XQ01 |  | 20MAU40AP001XQ01 | A JACKING OIL PMP CURRENT | AI | 0 | 100 | A |  |  |  |  | 58
48773 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 8 | #2 JACKING OIL PUMP A | K0102-25 | KALTIM2.SIGNAL.AI.20MAU40CP101 |  | 20MAU40CP101 | OIL P OF JACKING OIL MAIN PIP | AI | 0 | 25 | MPa |  |  | 8 | [6 empty] | 2 | 1
49112 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 8 | #2 JACKING OIL PUMP A | K0102-25 | KALTIM2.SIGNAL.AI.20MAU40CP101 |  | 20MAU40CP101 | OIL P OF JACKING OIL MAIN PIP | AI | 0 | 25 | MPa
48774 | 2 | UJKTT #2 | 12 | #2 LUBRICANT OIL SYSTEM | 9 | #2 JACKING OIL PUMP B | K0102-25 | KALTIM2.SIGNAL.AI.20MAU40AP002XQ01 |  | 20MAU40AP002XQ01 | B JACKING OIL PMP CURRENT | AI | 0 | 100 | A
48775 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 1 | #2 EXPANSION TANK | K0102-33 | KALTIM2.SIGNAL.AI.20PGB20AA101XQ12 |  | 20PGB20AA101XQ12 | LEVEL CTRL VLV OF EXPANSION TANK PSN | AI | 0 | 100 | %
48776 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 1 | #2 EXPANSION TANK | K0102-33 | KALTIM2.SIGNAL.AO.20PGB20AA101XQ11 |  | 20PGB20AA101XQ11 | LEVEL CTRL VLV OF EXPANSION TANK ADJ CMD | AO | 0 | 100 | %
48777 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 1 | #2 EXPANSION TANK | K0102-33 | KALTIM2.SIGNAL.AI.20PGB20CL101 |  | 20PGB20CL101 | LEVEL OF EXPANSION TANK | AI | 0 | 1200 | mm |  |  | 300 | 1100 | [5 empty] | 0 | 1
48778 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB30AP001XQ01 |  | 20PGB30AP001XQ01 | A CLSDCOOLING WTR PMP CURRENT | AI | 0 | 50 | A |  |  |  | 21.98 | [5 empty] | 1 | 1
48779 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB30CT101 |  | 20PGB30CT101 | A CLSDCOOLING WTR PMP DRIVEN END TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
48780 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB30CT102 |  | 20PGB30CT102 | A CLSDCOOLING WTR PMP NON-DRIVEN TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
48781 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB30CT103 |  | 20PGB30CT103 | A CLSDCOOLING WTR PMP WINDING TEMP 1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48782 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB30CT104 |  | 20PGB30CT104 | A CLSDCOOLING WTR PMP WINDING TEMP2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48783 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB30CT105 |  | 20PGB30CT105 | A CLSDCOOLING WTR PMP WINDING TEMP3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48784 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB30CP101 |  | 20PGB30CP101 | DIFF P OF A CLSDCOOLING WTR PMP INLET FLTR | AI | 0 | 100 | kPa |  |  |  | 40 | [5 empty] | 1
48785 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB32CP101 |  | 20PGB32CP101 | P OF THE MAIN PIP OF CLSDCOOLING WTR PMPS | AI | 0 | 1 | MPa |  |  | 0.4 | [6 empty] | 2 | 1
48786 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.20GUP10CQ101 |  | 20GUP10CQ101 | Unit 2 Common header of Closed cooling water PH | AI | 0 | 14
48787 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.20GUP10CQ102 |  | 20GUP10CQ102 | Unit 2 Common header of Closed cooling water CC | AI | 0 | 20
49074 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.20GUP10CQ101 |  | 20GUP10CQ101 | Unit 2 Common header of Closed cooling water PH | AI | 0 | 14
49075 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A |  | KALTIM 0.SIGNAL.AI.20GUP10CQ102 |  | 20GUP10CQ102 | Unit 2 Common header of Closed cooling water CC | AI | 0 | 20
49076 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 2 | #2 CCCW PUMP A | K0102-33 | KALTIM2.SIGNAL.AI.20PGB32CP101 |  | 20PGB32CP101 | P OF THE MAIN PIP OF CLSDCOOLING WTR PMPS | AI | 0 | 1 | MPa
48788 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.AI.20PGB31AP001XQ01 |  | 20PGB31AP001XQ01 | B CLSDCOOLING WTR PMP CURRENT | AI | 0 | 50 | A |  |  |  | 21.98 | [5 empty] | 1 | 1
48789 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB31CT101 |  | 20PGB31CT101 | B CLSDCOOLING WTR PMP DRIVEN END TEMP | RTD | 0 | 300 | ℃ |  |  |  | 80 | [5 empty] | 1 | 1
48790 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB31CT102 |  | 20PGB31CT102 | B CLSDCOOLING WTR PMP NON-DRIVEN TEMP | RTD | 0 | 300 | ℃ |  |  |  | 70 | [5 empty] | 1 | 1
48791 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB31CT103 |  | 20PGB31CT103 | B CLSDCOOLING WTR PMP WINDING TEMP1 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48792 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB31CT104 |  | 20PGB31CT104 | B CLSDCOOLING WTR PMP WINDING TEMP2 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48793 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB31CT105 |  | 20PGB31CT105 | B CLSDCOOLING WTR PMP WINDING TEMP3 | RTD | 0 | 300 | ℃ |  |  |  | 110 | [5 empty] | 1 | 1
48794 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 3 | #2 CCCW PUMP B | K0102-33 | KALTIM2.SIGNAL.AI.20PGB31CP101 |  | 20PGB31CP101 | DIFF P OF B CLSDCOOLING WTR PMP INLET FLTR | AI | 0 | 60 | KPa |  |  |  | 40 | [5 empty] | 1
48795 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB33CT101 |  | 20PGB33CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS INLET | RTD | 0 | 300 | ℃
48796 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB40CT101 |  | 20PGB40CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS OUTLET | RTD | 0 | 300 | ℃
48797 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB10CT101 |  | 20PCB10CT101 | TEMP OF THE MAIN PIP OF STRAINER CIRCLE WTR | RTD | 0 | 300 | ℃
48798 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB20CT101 |  | 20PCB20CT101 | WTR TEMP OF A CLSDWTR HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
48799 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-35 | KALTIM2.SIGNAL.AI.20PCB10CP101 |  | 20PCB10CP101 | P OF THE MAIN PIP OF STRAINER CIRCLE WTR | AI | 0 | 0.4 | MPa |  |  | 0.35 | [6 empty] | 2
49081 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-35 | KALTIM2.SIGNAL.AI.20PCB10CP101 |  | 20PCB10CP101 | P OF THE MAIN PIP OF STRAINER CIRCLE WTR | AI | 0 | 0.4 | MPa |  |  | 0.35 | [6 empty] | 2
49082 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB10CT101 |  | 20PCB10CT101 | TEMP OF THE MAIN PIP OF STRAINER CIRCLE WTR | RTD | 0 | 300 | ℃
49083 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB33CT101 |  | 20PGB33CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS INLET | RTD | 0 | 300 | ℃
49084 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 4 | #2 HE CCCW A | K0102-33 | KALTIM2.SIGNAL.RTD.20PGB40CT101 |  | 20PGB40CT101 | TEMP OF THE COOLING WTR OF CLSDWTR HEAT EXCHANGERS OUTLET | RTD | 0 | 300 | ℃
48800 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 5 | #2 HE CCCW B | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB20CT102 |  | 20PCB20CT102 | WTR TEMP OF B CLSDWTR HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
48801 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 6 | #2 HE VACUM PUMP A | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB40CT101 |  | 20PCB40CT101 | WTR TEMP OF A WTR-RING VACUM PMP HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
48802 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 6 | #2 HE VACUM PUMP A | K0102-35 | KALTIM2.SIGNAL.AI.20PCB30CP101 |  | 20PCB30CP101 | DIFF P OF A WTR-RING VACUM PMP HEAT EXCHANGER INLET FLTR | AI | 0 | 100 | KPa |  |  |  | 30 | [5 empty] | 1
48803 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 7 | #2 HE VACUM PUMP B | K0102-35 | KALTIM2.SIGNAL.RTD.20PCB40CT102 |  | 20PCB40CT102 | WTR TEMP OF B WTR-RING VACUM PMP HEAT EXCHANGER OUTLET | RTD | 0 | 300 | ℃
48804 | 2 | UJKTT #2 | 13 | #2 CCCW SYSTEM | 7 | #2 HE VACUM PUMP B | K0102-35 | KALTIM2.SIGNAL.AI.20PCB30CP102 |  | 20PCB30CP102 | DIFF P OF B WTR-RING VACUM PMP HEAT EXCHANGER INLET FLTR | AI | 0 | 1000 | kPa |  |  |  | 30 | [5 empty] | 1
48805 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB20CP101 |  | 20QFB20CP101 | Pressure of boiler instrument air main pipe 1 | AI | 0 | 1 | MPa |  |  | 0.5 | [6 empty] | 2
48806 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB21CP101 |  | 20QFB21CP101 | Boiler #1 corner instrument air main pipe pressure | AI | 0 | 1 | MPa |  |  | 0.5 | [6 empty] | 2
48807 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB22CP101 |  | 20QFB22CP101 | Boiler #2 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
48808 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB23CP101 |  | 20QFB23CP101 | Boiler #3 corner instrument air main pipe pressure | AI | 0 | 1 | MPa
48809 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB24CP101 |  | 20QFB24CP101 | Boiler #4 corner instrument air main pipe pressure | AI | 0 | 1 | MPa |  |  | 0.5 | [6 empty] | 2
48810 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-03 | KALTIM2.SIGNAL.AI.20QFB30CP101 |  | 20QFB30CP101 | Pressure of boiler instrument air main pipe 2 | AI | 0 | 1 | MPa |  |  | 0.5 | [6 empty] | 2
48811 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-06 | KALTIM2.SIGNAL.AI.20QFB40CP101 |  | 20QFB40CP101 | Pressure of turbine instrument air main pipe 1 | AI | 0 | 1 | MPa
48812 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-06 | KALTIM2.SIGNAL.AI.20QFB50CP101 |  | 20QFB50CP101 | Pressure of turbine instrument air main pipe 2 | AI | 0 | 1 | MPa
48813 | 2 | UJKTT #2 | 14 | #2 INSTRUMENT AIR SYSTEM | 1 | #2 INSTRUMENT AIR DISTRIBUTION | K0108-07 | KALTIM2.SIGNAL.AI.20QFB51CP101 |  | 20QFB51CP101 | Pressure of extraction steam check valve instrument air main pip | AI | 0 | 1 | MPa
48814 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 1 | #2 EH MAIN OIL TANK | K0102-27 | KALTIM2.SIGNAL.RTD.20MAX01CT101 |  | 20MAX01CT101 | OIL TEMP OF EH OIL TANK | RTD | 0 | 300 | ℃ |  |  | 20 | [6 empty] | 2
48815 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 1 | #2 EH MAIN OIL TANK | K0102-27 | KALTIM2.SIGNAL.AI.20MAX01CL101 |  | 20MAX01CL101 | EH OIL TANK LEVEL | AI | 0 | 700 | mm | 280 |  | 410 | 580 | [5 empty] | 0 | 1
48816 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 2 | #2 EH MAIN OIL PUMP A | K0102-27 | KALTIM2.SIGNAL.AI.20MAX11AP001XQ01 |  | 20MAX11AP001XQ01 | A MAIN EH PMP CURRENT | AI | 0 | 100 | A
48817 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 2 | #2 EH MAIN OIL PUMP A | K0102-27 | KALTIM2.SIGNAL.AI.20MAX20CP101 |  | 20MAX20CP101 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 21 | MPa
48818 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 2 | #2 EH MAIN OIL PUMP A | K0102-27 | KALTIM2.SIGNAL.AI.20MAX20CP102 |  | 20MAX20CP102 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 25 | MPa
49115 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 2 | #2 EH MAIN OIL PUMP A | K0102-27 | KALTIM2.SIGNAL.AI.20MAX20CP101 |  | 20MAX20CP101 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 21 | MPa
49116 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 2 | #2 EH MAIN OIL PUMP A | K0102-27 | KALTIM2.SIGNAL.AI.20MAX20CP102 |  | 20MAX20CP102 | OIL P OF EH PMPS OUTLET MAIN PIP | AI | 0 | 25 | MPa
48819 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 3 | #2 EH MAIN OIL PUMP B | K0102-27 | KALTIM2.SIGNAL.AI.20MAX12AP001XQ01 |  | 20MAX12AP001XQ01 | B MAIN EH PMP CURRENT | AI | 0 | 100 | A
48820 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 4 | #2 EH COOLER A | K0102-27 | KALTIM2.SIGNAL.RTD.20MAX14CT101 |  | 20MAX14CT101 | OIL TEMP OF A EH OIL COOLER OUTLET | RTD | 0 | 300 | ℃
48821 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 5 | #2 EH COOLER B | K0102-27 | KALTIM2.SIGNAL.RTD.20MAX60CT101 |  | 20MAX60CT101 | OIL TEMP OF B EH OIL COOLER INLET | RTD | 0 | 300 | ℃
48822 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 5 | #2 EH COOLER B | K0102-27 | KALTIM2.SIGNAL.RTD.20MAX60CT102 |  | 20MAX60CT102 | OIL TEMP OF B EH OIL COOLER OUTLET | RTD | 0 | 300 | ℃
49118 | 2 | UJKTT #2 | 15 | #2 ELECTRO HYDROLIC SYSTEM | 5 | #2 EH COOLER B | K0102-27 | KALTIM2.SIGNAL.RTD.20MAX60CT101 |  | 20MAX60CT101 | OIL TEMP OF A EH OIL COOLER INLET | RTD | 0 | 300 | ℃
48823 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.TC.20LBG20CT101 |  | 20LBG20CT101 | TEMP OF THE STM OF AUX STM MAIN PIP | TC | 0 | 800 | ℃
48824 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.TC.20LBG22CT101 |  | 20LBG22CT101 | TEMP OF THE STM FROM NO.3 EXTR STM TO AUX STM | TC | 0 | 800 | ℃
48825 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.TC.20LBG24CT101 |  | 20LBG24CT101 | TEMP OF THE STM FROM AUX STM TO BOILER BTM HEATING | TC | 0 | 800 | ℃
48826 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.TC.20LBG25CT101 |  | 20LBG25CT101 | TEMP OF THE STM FROM AUX STM TO OIL GUN ATOMIZATION | TC | 0 | 800 | ℃
48827 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.AI.20LBG25CP101 |  | 20LBG25CP101 | P OF THE STM FROM AUX STM TO OIL GUN ATOMIZATION | AI | 0 | 1.6 | MPa
48828 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.AI.20LBG20CP101 |  | 20LBG20CP101 | P OF THE STM OF AUX STM MAIN PIP | AI | 0 | 1.6 | MPa
48829 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.AI.20LBG22CP101 |  | 20LBG22CP101 | P OF THE STM FROM NO.3 EXTR STM TO AUX STM | AI | 0 | 1.6 | MPa
48830 | 2 | UJKTT #2 | 16 | #2 AUXILIARY STEAM SYSTEM | 1 | #2 AUXILIARY STEAM SYSTEM | K0102-23 | KALTIM2.SIGNAL.AI.20LBG24CP101 |  | 20LBG24CP101 | P OF THE STM FROM AUX STM TO BOILER BTM HEATING | AI | 0 | 1.6 | MPa
48831 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20HDA10AN001XQ12 |  | 20HDA10AN001XQ12 | A slag cooler speed feedback | AI | 0 | 100 | %
48832 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36AA101XQ12 |  | 20LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
48833 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AO.20HDA10AN001XQ11 |  | 20HDA10AN001XQ11 | A slag cooler control command | AO | 0 | 100 | %
48834 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AO.20LCE36AA101XQ11 |  | 20LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
48835 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.RTD.20LCE36CT101 |  | 20LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
48836 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-08 | KALTIM2.SIGNAL.TC.20HDA10CT101 |  | 20HDA10CT101 | Furnace to A slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
48837 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE30CP101 |  | 20LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa |  |  | 0.4 | [6 empty] | 2
48838 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36CP101 |  | 20LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49095 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE30CP101 |  | 20LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa
49096 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AO.20LCE36AA101XQ11 |  | 20LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
49097 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36AA101XQ12 |  | 20LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
49098 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36CP101 |  | 20LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49099 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.RTD.20LCE36CT101 |  | 20LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
49100 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE30CP101 |  | 20LCE30CP101 | Slag cooler cooling water inlet main pipe pressure | AI | 0 | 3 | MPa
49101 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AO.20LCE36AA101XQ11 |  | 20LCE36AA101XQ11 | Slag cooler cooling water outlet control valve control command | AO | 0 | 100 | %
49102 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36AA101XQ12 |  | 20LCE36AA101XQ12 | Slag cooler cooling water outlet control valve position feedback | AI | 0 | 100 | %
49103 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.AI.20LCE36CP101 |  | 20LCE36CP101 | Slag cooler pump outlet main pipe pressure | AI | 0 | 3 | MPa
49104 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 1 | #2 SLAG COOLER A | K0102-16 | KALTIM2.SIGNAL.RTD.20LCE36CT101 |  | 20LCE36CT101 | Slag cooler pump outlet main pipe temperature | RTD | 0 | 150 | ℃
48839 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 2 | #2 SLAG COOLER B | K0102-16 | KALTIM2.SIGNAL.AI.20HDA20AN001XQ12 |  | 20HDA20AN001XQ12 | B slag cooler speed feedback | AI | 0 | 100 | %
48840 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 2 | #2 SLAG COOLER B | K0102-16 | KALTIM2.SIGNAL.AO.20HDA20AN001XQ11 |  | 20HDA20AN001XQ11 | B slag cooler control command | AO | 0 | 100 | %
48841 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 2 | #2 SLAG COOLER B | K0102-08 | KALTIM2.SIGNAL.TC.20HDA20CT101 |  | 20HDA20CT101 | Furnace to B slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
48842 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 3 | #2 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AI.20HDA30AN001XQ12 |  | 20HDA30AN001XQ12 | C slag cooler speed feedback | AI | 0 | 100 | %
48843 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 3 | #2 SLAG COOLER C | K0102-16 | KALTIM2.SIGNAL.AO.20HDA30AN001XQ11 |  | 20HDA30AN001XQ11 | C slag cooler control command | AO | 0 | 100 | %
48844 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 3 | #2 SLAG COOLER C | K0102-08 | KALTIM2.SIGNAL.TC.20HDA30CT101 |  | 20HDA30CT101 | Furnace to C slag cooler slag temperature | TC | 0 | 1000 | ℃ |  |  | 200 | [6 empty] | 2 | 1
48845 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 4 | #2 SLAG SILO | K0612-02 | KALTIM2.SIGNAL.AI.20EEA10CP101 |  | 20EEA10CP101 | 2# boiler convey-bed material sys. transport gas pres. | AI | 0 | 1000 | kPa |  |  | 0.3 | [6 empty] | 2
48846 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 4 | #2 SLAG SILO | K0613-01 | KALTIM2.SIGNAL.AI.20ETE10CL101 |  | 20ETE10CL101 | #2 boiler ash silo Level | AI | 0 | 8.5 | m |  |  |  | 7.64 | [5 empty] | 1 | 1
48847 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 4 | #2 SLAG SILO | K0613-01 | KALTIM2.SIGNAL.AI.20ETE30CL101 |  | 20ETE30CL101 | #2 boiler ash silo Level | AI | 0 | 1.7 | m |  |  | 0.9 | [6 empty] | 2 | 1
48848 | 2 | UJKTT #2 | 17 | #2 ASH HANDLING SYSTEM | 4 | #2 SLAG SILO | K0612-02 | KALTIM2.SIGNAL.AI.20EEA10CP102 |  | 20EEA10CP102 | 2# boiler convey-bed material sys. transport material pres | AI | 0 | 1 | MPa |  |  | 0.3 | [6 empty] | 2
48849 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.RTD.20ERB10CT101 |  | 20ERB10CT101 | Fuel oil main pipe temperature | RTD | 0 | 300 | ℃
48850 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.AI.20ERB10CP101 |  | 20ERB10CP101 | Fuel oil inlet pressure | AI | 0 | 3 | MPa |  |  | 1.2 | [6 empty] | 2
48851 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.AI.20ERB10CP102 |  | 20ERB10CP102 | Fuel oil main pipe pressure | AI | 0 | 3 | MPa |  |  | 0.6 | [6 empty] | 2
48852 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.AI.20ERB20CP101 |  | 20ERB20CP101 | Return fuel oil main pipe pressure | AI | 0 | 3 | MPa
48853 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.AI.20ERB10CF101 |  | 20ERB10CF101 | Fuel oil inlet main pipe flow | AI | 0 | 25 | t/h
48854 | 2 | UJKTT #2 | 18 | #2 FUEL OIL SYSTEM | 1 | #2 FUEL OIL SYSTEM | K0102-11 | KALTIM2.SIGNAL.AI.20ERB20CF101 |  | 20ERB20CF101 | Return fuel oil main pipe flow | AI | 0 | 25 | t/h
48857 | 2 | UJKTT #2 | 19 | #2 LIMESTONE INJECTION SYSTEM | 1 | #2 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM2.SIGNAL.AI.20EQH10CL101 |  | 20EQH10CL101 | #2 Boiler Limestone storage level | AI | 0 | 100 | %
48858 | 2 | UJKTT #2 | 19 | #2 LIMESTONE INJECTION SYSTEM | 1 | #2 LIMESTONE INJECTION SYSTEM |  | KALTIM 0.SIGNAL.AI.20BFA07ACE001 |  | 20BFA07ACE001 | C limestone transport aerification fan current | AI | 0 | 100 | A
48859 | 2 | UJKTT #2 | 19 | #2 LIMESTONE INJECTION SYSTEM | 1 | #2 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM2.SIGNAL.AI.20EQH10CP101 |  | 20EQH10CP101 | A Limestone duct pressure 1 | AI | 0 | 100 | kPa
48860 | 2 | UJKTT #2 | 19 | #2 LIMESTONE INJECTION SYSTEM | 1 | #2 LIMESTONE INJECTION SYSTEM | K0611-04 | KALTIM2.SIGNAL.AI.20EQH10CP102 |  | 20EQH10CP102 | A Limestone duct pressure 2 | AI | 0 | 100 | kPa
48861 | 2 | UJKTT #2 | 19 | #2 LIMESTONE INJECTION SYSTEM | 1 | #2 LIMESTONE INJECTION SYSTEM |  | KALTIM 0.SIGNAL.AI.20EDD10CP101 |  | 20EDD10CP101 | Pressure of conveying pipe for conveying-limestone 2# | AI | 0 | 100 | MPa
48862 | 2 | UJKTT #2 | 20 | #2 FLY ASH SYSTEM | 1 | #2 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.20ETG10CP101 |  | 20ETG10CP101 | pressure conveying-ash 2# boiler | AI | 0 | 100
48863 | 2 | UJKTT #2 | 20 | #2 FLY ASH SYSTEM | 1 | #2 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.20ETG11CP101 |  | 20ETG11CP101 | pressure value of convying-ash main pipe in 2# boiler 1st ESP fi | AI | 0 | 100
48864 | 2 | UJKTT #2 | 20 | #2 FLY ASH SYSTEM | 1 | #2 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.20ETG41CP101 |  | 20ETG41CP101 | pressure value of conveying-ash main pipe in 2# boiler air prehe | AI | 0 | 100
48865 | 2 | UJKTT #2 | 20 | #2 FLY ASH SYSTEM | 1 | #2 FLY ASH SYSTEM |  | KALTIM 0.SIGNAL.AI.20ETG21CP101 |  | 20ETG21CP101 | pressure value of conveying-ash main pipe in 2# boiler 2nd&3rd E | AI | 0 | 100
47274
48252
48307
48308
48309
48855
48856