## UNIT#1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | DPU_1_A:714 | DPU_1_A:714 |  | #1 SECONDARY AIR FLOW OF #1 BOILER | AI | 0 | 60000 | m3/h | [6 empty] | TOTAL
2 | Manipulated Variable | Secondary Air Flow | DPU_1_A:717 | DPU_1_A:717 |  | #2 SECONDARY AIR FLOW OF #1 BOILER | AI | 0 | 60000 | m3/h
3 | Disturbance Variable | Coal Flow | DPU_1_A:246 | DPU_1_A:246 |  | #1 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [6 empty] | TOTAL
4 | Disturbance Variable | Coal Flow | DPU_1_A:282 | DPU_1_A:282 |  | #1 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
5 | Disturbance Variable | Coal Flow | DPU_1_A:291 | DPU_1_A:291 |  | #1 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
6 | Disturbance Variable | Load | DPU_3_A:522 | DPU_3_A:522 |  | #1 GENERATOR ACTIVE POWER | AI | 0 | 20 | MW
7 | Disturbance Variable | Primary Air Flow | DPU_1_A:708 | DPU_1_A:708 |  | #1 PRIMARY AIR FLOW OF #1 BOILER | AI | 0 | 40000 | m3/h | [6 empty] | TOTAL
8 | Disturbance Variable | Primary Air Flow | DPU_1_A:711 | DPU_1_A:711 |  | #2 PRIMARY AIR FLOW OF #1 BOILER | AI | 0 | 40000 | m3/h
9 | Constrain Variable | Oxygen Sensor | DPU_1_A:222 | DPU_1_A:222 |  | GAS FLUE INLET O2% OF #1 BOILER | AI | 0 | 100 | %
10 | Constrain Variable | Furnace Pressure | DPU_1_A:9 | DPU_1_A:9 |  | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa | [6 empty] | AVERAGE
11 | Constrain Variable | Furnace Pressure | DPU_1_A:63 | DPU_1_A:63 |  | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa
12 | Constrain Variable | Furnace Pressure | DPU_1_A:33 | DPU_1_A:33 |  | #1 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 | 0 | -150 | 10 | 0 | 50 | AVERAGE
13 | Constrain Variable | Furnace Pressure | DPU_1_A:75 | DPU_1_A:75 |  | #1 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 | 0 | -150 | 10 | 0 | 50
14 | Constrain Variable | Furnace Differential Pressure | DPU_1_A:99 | DPU_1_A:99 |  | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa | [6 empty] | AVERAGE
15 | Constrain Variable | Furnace Differential Pressure | DPU_1_A:141 | DPU_1_A:141 |  | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa
16 | Constrain Variable | Bed Differential Pressure | DPU_1_A:102 | DPU_1_A:102 |  | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | -20 | 20 | KPa | [6 empty] | AVERAGE
17 | Constrain Variable | Bed Differential Pressure | DPU_1_A:144 | DPU_1_A:144 |  | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | -20 | 20 | KPa
18 | Constrain Variable | Bed Temperature | DPU_1_A:393 | DPU_1_A:393 |  | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100 | AVERAGE
19 | Constrain Variable | Bed Temperature | DPU_1_A:453 | DPU_1_A:453 |  | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
20 | Constrain Variable | Bed Temperature | DPU_1_A:396 | DPU_1_A:396 |  | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
21 | Constrain Variable | Bed Temperature | DPU_1_A:450 | DPU_1_A:450 |  | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
22 | Constrain Variable | Bed Temperature | DPU_1_A:420 | DPU_1_A:420 |  | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | AI | 0 | 1200 | °C | [6 empty] | AVERAGE
23 | Constrain Variable | Bed Temperature | DPU_1_A:408 | DPU_1_A:408 |  | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | AI | 0 | 1200 | °C
24 | Constrain Variable | Furnace Temperature | DPU_1_A:399 | DPU_1_A:399 |  | #1 BOILER FURNACE OUTLET TEMPERATURE | AI | 0 | 1200 | °C | [6 empty] | AVERAGE
25 | Constrain Variable | Furnace Temperature | DPU_1_A:426 | DPU_1_A:426 |  | #1 BOILER FURNACE OUTLET TEMPERATURE | AI | 0 | 1200 | °C
26 | Constrain Variable | Stack NOx |  |  |  | N/A
27 | Constrain Variable | Stack CO |  |  |  | N/A
28 | Efficiency Variable | Coal Flow | DPU_1_A:246 | DPU_1_A:246 |  | #1 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [6 empty] | TOTAL
29 | Efficiency Variable | Coal Flow | DPU_1_A:282 | DPU_1_A:282 |  | #1 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
30 | Efficiency Variable | Coal Flow | DPU_1_A:291 | DPU_1_A:291 |  | #1 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
31 | Efficiency Variable | Main Steam Pressure | DPU_3_A:525 | DPU_3_A:525 |  | #1 TURBINE MAIN STEAM PRE. BEF ELEC MSV | AI | 0 | 10 | MPa |  |  |  | 5.098
32 | Efficiency Variable | Main Steam Pressure | DPU_1_A:15 | DPU_1_A:15 |  | #1 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa |  |  | 4.61 | 5.1
33 | Efficiency Variable | Feed Water Pressure | DPU_1_A:0 | DPU_1_A:0 |  | #1 BOILER UPSTREAM-CONTROL VALVE PRESSURE | AI | 0 | 16 | MPa
34 | Efficiency Variable | Feed Water Pressure | DPU_2_A:15 | DPU_2_A:15 |  | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 |  |  | AVERAGE
35 | Efficiency Variable | Feed Water Pressure | DPU_2_A:18 | DPU_2_A:18 |  | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
36 | Efficiency Variable | Feed Water Pressure | DPU_2_A:483 | DPU_2_A:483 |  | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
37 | Efficiency Variable | SH Spray Water Pressure | DPU_2_A:15 | DPU_2_A:15 |  | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 |  |  | AVERAGE
38 | Efficiency Variable | SH Spray Water Pressure | DPU_2_A:18 | DPU_2_A:18 |  | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
39 | Efficiency Variable | SH Spray Water Pressure | DPU_2_A:483 | DPU_2_A:483 |  | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
40 | Efficiency Variable | Main Steam Temperature | DPU_1_A:369 | DPU_1_A:369 |  | #1 BOILER MAIN STEAM TEMPERATURE | AI | 0 | 600 | °C |  |  | 465 | 490 |  | 491
41 | Efficiency Variable | Main Steam Temperature | DPU_3_A:336 | DPU_3_A:336 |  | #1 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | AI | 0 | 600 | °C |  |  | 455 | 488
42 | Efficiency Variable | Feed Water Temperature | DPU_3_A:276 | DPU_3_A:276 |  | #1 TURBINE HP HEATER OUTLET WATER TEMP | AI | 0 | 200 | °C
43 | Efficiency Variable | Feed Water Temperature | DPU_1_A:786 | DPU_1_A:786 |  | #1 BOILER FEEDWATER TEMPERATURE | AI | 0 | 200 | °C
44 | Efficiency Variable | SH Spray Temperature | DPU_3_A:276 | DPU_3_A:276 |  | #1 TURBINE HP HEATER OUTLET WATER TEMP | AI | 0 | 200 | °C
45 | Efficiency Variable | Main Steam Flow | DPU_1_A:750 | DPU_1_A:750 |  | #1 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h
46 | Efficiency Variable | Feed Water Flow | DPU_1_A:744 | DPU_1_A:744 |  | #1 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h
47 | Efficiency Variable | SH Spray Water Flow | DPU_1_A:756 | DPU_1_A:756 |  | #1 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h | [6 empty] | TOTAL
48 | Efficiency Variable | SH Spray Water Flow | DPU_1_A:759 | DPU_1_A:759 |  | #1 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h
49 | Control Variable | FD Fan Air Flow | DPU_1_A:780 | DPU_1_A:780 |  | CONTROL SIGNAL OF #1 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %
50 | Control Variable | FD Fan Air Flow | DPU_1_A:483 | DPU_1_A:483 |  | CONTROL SIGNAL OF #1 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %

## UNIT#2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | DPU_4_A:729 | DPU_4_A:729 |  | #1 SECONDARY AIR FLOW OF #2 BOILER | AI | 0 | 60000 | m3/h | [6 empty] | TOTAL
2 | Manipulated Variable | Secondary Air Flow | DPU_4_A:732 | DPU_4_A:732 |  | #2 SECONDARY AIR FLOW OF #2 BOILER | AI | 0 | 60000 | m3/h
3 | Disturbance Variable | Coal Flow | DPU_4_A:936 | DPU_4_A:936 |  | #2 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [6 empty] | TOTAL
4 | Disturbance Variable | Coal Flow | DPU_4_A:282 | DPU_4_A:282 |  | #2 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
5 | Disturbance Variable | Coal Flow | DPU_4_A:291 | DPU_4_A:291 |  | #2 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
6 | Disturbance Variable | Load | DPU_6_A:438 | DPU_6_A:438 |  | #2 GENERATOR ACTIVE POWER | AI | 0 | 20 | MW
7 | Disturbance Variable | Primary Air Flow | DPU_4_A:723 | DPU_4_A:723 |  | #1 PRIMARY AIR FLOW OF #2 BOILER | AI | 0 | 40000 | m3/h | [6 empty] | TOTAL
8 | Disturbance Variable | Primary Air Flow | DPU_4_A:726 | DPU_4_A:726 |  | #2 PRIMARY AIR FLOW OF #2 BOILER | AI | 0 | 40000 | m3/h
9 | Constrain Variable | Oxygen Sensor | DPU_4_A:222 | DPU_4_A:222 |  | GAS FLUE INLET O2% OF #2 BOILER | AI | 0 | 100 | %
10 | Constrain Variable | Furnace Pressure | DPU_4_A:9 | DPU_4_A:9 |  | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa | [6 empty] | AVERAGE
11 | Constrain Variable | Furnace Pressure | DPU_4_A:63 | DPU_4_A:63 |  | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa
12 | Constrain Variable | Furnace Pressure | DPU_4_A:876 | DPU_4_A:876 |  | #2 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 | 0 | -150 | 10 | 0 | 50 | AVERAGE
13 | Constrain Variable | Furnace Pressure | DPU_4_A:879 | DPU_4_A:879 |  | #2 BOILER FURNACE OUTLET PRESSURE | AI | -1000 | 1000 | Pa | -500 | 0 | -150 | 10 | 0 | 50
14 | Constrain Variable | Furnace Differential Pressure | DPU_4_A:930 | DPU_4_A:930 |  | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa | [6 empty] | AVERAGE
15 | Constrain Variable | Furnace Differential Pressure | DPU_4_A:141 | DPU_4_A:141 |  | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa
16 | Constrain Variable | Bed Differential Pressure | DPU_4_A:102 | DPU_4_A:102 |  | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | -20 | 20 | KPa | [6 empty] | AVERAGE
17 | Constrain Variable | Bed Differential Pressure | DPU_4_A:144 | DPU_4_A:144 |  | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | -20 | 20 | KPa
18 | Constrain Variable | Bed Temperature | DPU_4_A:393 | DPU_4_A:393 |  | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100 | AVERAGE
19 | Constrain Variable | Bed Temperature | DPU_4_A:396 | DPU_4_A:396 |  | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
20 | Constrain Variable | Bed Temperature | DPU_4_A:450 | DPU_4_A:450 |  | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
21 | Constrain Variable | Bed Temperature | DPU_4_A:453 | DPU_4_A:453 |  | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | 0 | 1200 | °C | 0 | 0 | 400 | 1000 | 0 | 1100
22 | Constrain Variable | Bed Temperature | DPU_4_A:408 | DPU_4_A:408 |  | #2 BOILER UPPER TEMPERATURE OF BOILING BED | AI | 0 | 1200 | °C | [6 empty] | AVERAGE
23 | Constrain Variable | Bed Temperature | DPU_4_A:420 | DPU_4_A:420 |  | #2 BOILER UPPER TEMPERATURE OF BOILING BED | AI | 0 | 1200 | °C
24 | Constrain Variable | Furnace Temperature | DPU_4_A:399 | DPU_4_A:399 |  | #2 BOILER FURNACE OUTLET TEMPERATURE | AI | 0 | 1200 | °C | [6 empty] | AVERAGE
25 | Constrain Variable | Furnace Temperature | DPU_4_A:426 | DPU_4_A:426 |  | #2 BOILER FURNACE OUTLET TEMPERATURE | AI | 0 | 1200 | °C
26 | Constrain Variable | Stack NOx |  |  |  | N/A
27 | Constrain Variable | Stack CO |  |  |  | N/A
28 | Efficiency Variable | Coal Flow | DPU_4_A:936 | DPU_4_A:936 |  | #2 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 20 | t/h | [6 empty] | TOTAL
29 | Efficiency Variable | Coal Flow | DPU_4_A:282 | DPU_4_A:282 |  | #2 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
30 | Efficiency Variable | Coal Flow | DPU_4_A:291 | DPU_4_A:291 |  | #2 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | 0 | 100 | t/h
31 | Efficiency Variable | Main Steam Pressure | DPU_6_A:480 | DPU_6_A:480 |  | #2 TURBINE MAIN STEAM PRE.BEF ELEC MSV | AI | 0 | 10 | MPa |  |  |  | 5.098
32 | Efficiency Variable | Main Steam Pressure | DPU_4_A:15 | DPU_4_A:15 |  | #2 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa |  |  | 4.61 | 5.1
33 | Efficiency Variable | Feed Water Pressure | DPU_4_A:0 | DPU_4_A:0 |  | #2 BOILER UPSTREAN-CONTROL VALVE PRESSURE | AI | 0 | 16 | MPa
34 | Efficiency Variable | Feed Water Pressure | DPU_5_A:15 | DPU_5_A:15 |  | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 |  |  | AVERAGE
35 | Efficiency Variable | Feed Water Pressure | DPU_5_A:18 | DPU_5_A:18 |  | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
36 | Efficiency Variable | Feed Water Pressure | DPU_5_A:21 | DPU_5_A:21 |  | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
37 | Efficiency Variable | SH Spray Water Pressure | DPU_5_A:15 | DPU_5_A:15 |  | #1 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8 |  |  | AVERAGE
38 | Efficiency Variable | SH Spray Water Pressure | DPU_5_A:18 | DPU_5_A:18 |  | #2 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
39 | Efficiency Variable | SH Spray Water Pressure | DPU_5_A:21 | DPU_5_A:21 |  | #3 FEED WATER PUMP OUTLET PRESSURE | AI | 0 | 16 | MPa |  |  |  | 7.8
40 | Efficiency Variable | Main Steam Temperature | DPU_4_A:369 | DPU_4_A:369 |  | #2 BOILER MAIN STEAM TEMPERATURE | AI | 0 | 600 | °C |  |  | 465 | 490 |  | 491
41 | Efficiency Variable | Main Steam Temperature | DPU_6_A:336 | DPU_6_A:336 |  | #2 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | AI | 0 | 600 | °C |  |  | 455 | 488
42 | Efficiency Variable | Feed Water Temperature | DPU_6_A:276 | DPU_6_A:276 |  | #2 TURBINE HP HEATER OUTLET WATER TEMP | AI | 0 | 200 | °C
43 | Efficiency Variable | Feed Water Temperature | DPU_4_A:924 | DPU_4_A:924 |  | #2 BOILER FEEDWATER TEMPERATURE | AI | 0 | 200 | °C
44 | Efficiency Variable | SH Spray Temperature | DPU_6_A:276 | DPU_6_A:276 |  | #2 TURBINE HP HEATER OUTLET WATER TEMP | AI | 0 | 200 | °C
45 | Efficiency Variable | Main Steam Flow | DPU_4_A:714 | DPU_4_A:714 |  | #2 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h
46 | Efficiency Variable | Feed Water Flow | DPU_4_A:708 | DPU_4_A:708 |  | #2 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h
47 | Efficiency Variable | SH Spray Water Flow | DPU_4_A:717 | DPU_4_A:717 |  | #2 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h | [6 empty] | TOTAL
48 | Efficiency Variable | SH Spray Water Flow | DPU_4_A:720 | DPU_4_A:720 |  | #2 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h
49 | Control Variable | FD Fan Air Flow | DPU_4_A:462 | DPU_4_A:462 |  | CONTROL SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %
50 | Control Variable | FD Fan Air Flow | DPU_4_A:483 | DPU_4_A:483 |  | CONTROL SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %

## 2022-09-14 10 19 MariaDB_soketd
NO | UNIT | SYSTEM | EQUIPMENT | f_equipment_id | Tag Name | Description | Tag Type | Tag Unit | Range Lo | Range Hi | L3 | L2 | L1 | H1 | H2 | H3
1 | PLTU Belitung 1 |  | BATTERY SYSTEM UNIT 1 | 3329
2 | PLTU Belitung 1 |  | WATER TANK #1 | 3362
3 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL BUNKER SYSTEM A #1 | 3200 | DPU_1_A:171 | #1 BOILER #1 COAL BUNKER LEVEL | AI | mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL BUNKER SYSTEM B #1 | 3201 | DPU_1_A:174 | #1 BOILER #2 COAL BUNKER LEVEL | AI | mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER A #1 | 3202 | DPU_1_A:246 | #1 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
6 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER A #1 | 3202 | DPU_1_A:249 | #1 BOILER #1 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
7 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER A #1 | 3202 | DPU_1_A:735 | #1 BOILER #1 COAL FEEDER ACCUMULATIVE TOTAL VOLUME PULSE INPUT | AI | t | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0
8 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER A #1 | 3202 | DPU_1_A:474 | #1 BOILER #1 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
9 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER B #1 | 3203 | DPU_1_A:282 | #1 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
10 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER B #1 | 3203 | DPU_1_A:285 | #1 BOILER #2 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
11 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER B #1 | 3203 | DPU_1_A:738 | #1 BOILER #2 COAL FEEDER ACCUMULATIVE TOTAL VOLUNE PULSE INPUT | AI | t | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER B #1 | 3203 | DPU_1_A:477 | #1 BOILER #2 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
13 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER C #1 | 3204 | DPU_1_A:291 | #1 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
14 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER C #1 | 3204 | DPU_1_A:294 | #1 BOILER #3 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
15 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER C #1 | 3204 | DPU_1_A:741 | #1 BOILER #3 COAL FEEDER ACCUMULATIVE TOTAL VOLUME PULSE INPUT | AI | t | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | PLTU Belitung 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER C #1 | 3204 | DPU_1_A:495 | #1 BOILER #3 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
17 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:225 | #1 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
18 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:513 | #1 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
19 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:237 | #1 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
20 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:501 | #1 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
21 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:243 | #1 TURBINE CONDENSATION WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
22 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:27 | #1 TURBINE CONDENSER LEVEL | AI | mm | 0 | 1025 | 150 | 0 | 0 | 600 | 0 | 1000
23 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:30 | #1 TURBINE CONDENSER VACUUM | AI | Kpa | -100 | 0 | 0 | 0 | 0 | -87 | 0 | -61
24 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | CONDENSER #1 | 3207 | DPU_3_A:81 | #1 TURBINE CONDENSER VACUUM | AI | Kpa | -100 | 0 | 0 | 0 | 0 | -87 | 0 | -61
25 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | GSH #1 | 3208 | DPU_3_A:36 | #1 TURBINE EXTRACTION STM PRE.OF GLAND STM HEATER | AI | MPa | -0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0
26 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | GSH #1 | 3208 | DPU_3_A:495 | #1 TURBINE AVERAGE PRE.TANK PRE. | AI | MPa | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
27 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | GSH #1 | 3208 | DPU_3_A:354 | CONTROL SIGNAL OF #1 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
28 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | GSH #1 | 3208 | DPU_3_A:99 | FEEDBACK SIGNAL OF #1 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
29 | PLTU Belitung 1 | CONDENSATE SYSSTEM #1 | VACCUM PUMP A #1 VACCUM PUMP B #1 | 3209 | DPU_3_A:75 | #1 TURBINE VACUUM PUMP INLET PRE. | AI | Kpa | -160 | 0 | 0 | 0 | -95 | -88 | 0 | 0
30 | PLTU Belitung 1 | CONDENSATE SYSTEM | GLAND STEAM HEATER SYSTEM #1 | 3364
31 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP SYSTEM A#1 | 3205 | DPU_3_A:21 | #1 TURBINE #1 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
32 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP SYSTEM A#1 | 3205 | DPU_3_A:120 | #1 TURBINE #1 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
33 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP SYSTEM B#1 | 3206 | DPU_3_A:63 | #1 TURBINE #2 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
34 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP SYSTEM B#1 | 3206 | DPU_3_A:462 | #1 TURBINE CONDENSATION WATER FLOW | AI | t/h | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0
35 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP SYSTEM B#1 | 3206 | DPU_3_A:156 | #1 TURBINE #1 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
36 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | LPH #1 | 3342 | DPU_3_A:282 | #1 TURBINE LP HEATER INLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
37 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | LPH #1 | 3342 | DPU_3_A:285 | #1 TURBINE LP HEATER OUTLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
38 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | VACUUM PUMP A #1 | 3358 | DPU_3_A:162 | #1 TURBINE VACUUM PUMP SK-6 CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
39 | PLTU Belitung 1 | Condensate System #1 | VACUUM PUMP B #1 | 3359
40 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | WATER EJECTOR SYSTEM #1 | 3360 | DPU_3_A:351 | CONTROL SIGNAL OF #1 TURBINE CONDENSER LEVEL CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
41 | PLTU Belitung 1 | CONDENSATE SYSTEM #1 | WATER EJECTOR SYSTEM #1 | 3360 | DPU_3_A:96 | FEEDBACK SIGNAL OF #1 TURBINE CONDENSER LEVEL CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
42 | PLTU Belitung 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 3210 | DPU_3_A:72 | #1 TURBINE BALL CIRCULATING PUMP OUTLET PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
43 | PLTU Belitung 1 | COOLING SYSTEM #1 | CLOSED CYCLE COOLING WATER PUMP #1A | 3211 | DPU_2_A:0 | #1 TURBINE #1 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
44 | PLTU Belitung 1 | COOLING SYSTEM #1 | CLOSED CYCLE COOLING WATER PUMP #1B | 3212 | DPU_2_A:57 | #1 TURBINE #2 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
45 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:36 | #1 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
46 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:39 | #1.2 CIRCULATING WATER PUMP OUTLET MAIN PIPE PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
47 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:186 | FRONT BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
48 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:189 | BACK BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
49 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:192 | MOTOR STATOR TEMP 1 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
50 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:477 | MOTOR STATOR TEMP 2 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
51 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:198 | MOTOR STATOR TEMP 3 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
52 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:42 | #1.2 CIRCULATING WATER PUMP OUTLET MAIN PIPE FLOW | AI | t/h | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0
53 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP A #1 | 3213 | DPU_2_A:69 | #1 TURBINE #1 CIRCULATING WATER PUMP CURRENT INDICATOR | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
54 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:54 | #2 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
55 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:201 | FRONT BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
56 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:204 | BACK BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
57 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:474 | MOTOR STATOR TEMP 1 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
58 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:210 | MOTOR STATOR TEMP 2 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
59 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:213 | MOTOR STATOR TEMP 3 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
60 | PLTU Belitung 1 | COOLING SYSTEM #1 | CWP PUMP B #1 | 3216 | DPU_2_A:72 | #1 TURBINE #2 CIRCULATING WATER PUMP CURRENT INDICATOR | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
61 | PLTU Belitung 1 | COOLING SYSTEM #1 | RECIRCULATING PUMP A #1 | 3218 | DPU_2_A:6 | #1 TURBINE #1 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
62 | PLTU Belitung 1 | COOLING SYSTEM #1 | RECIRCULATING PUMP B #1 | 3219 | DPU_2_A:60 | #1 TURBINEI2 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
63 | PLTU Belitung 1 | Electrical System #1 | RECTIFIER BATTERY EMERGENCY SWITCHGEAR 20 KV | 3350
64 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:12 | LP FEED WATER PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
65 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:15 | #1 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
66 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:141 | FRONT BEARING TEMP OF #1 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
67 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:144 | BACK BEARING TEMP OF #1 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
68 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:147 | MOTOR STATOR TEMP 1 OF #1 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
69 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:150 | MOTOR STATOR TEMP 2 OF #1 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
70 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:153 | MOTOR STATOR TEMP 3 OF #1 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
71 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-A #1 | 3220 | DPU_2_A:3 | #1 TURBINE #1 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
72 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:18 | #2 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
73 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:156 | FRONT BEARING TEMP OF #2 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
74 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:159 | BACK BEARING TEMP OF #2 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
75 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:162 | MOTOR STATOR TEMP 1 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
76 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:165 | MOTOR STATOR TEMP 2 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
77 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:168 | MOTOR STATOR TEMP 3 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
78 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-B #1 | 3221 | DPU_2_A:63 | #1 TURBINE #2 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
79 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:483 | #3 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
80 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:171 | FRONT BEARING TEMP OF #3 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
81 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:174 | BACK BEARING TEMP OF #3 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
82 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:177 | MOTOR STATOR TEMP 1 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
83 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:180 | MOTOR STATOR TEMP 2 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
84 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:183 | MOTOR STATOR TEMP 3 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
85 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | BFP-C #1 | 3222 | DPU_2_A:66 | #1 TURBINE #3 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
86 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:9 | DEAERATOR PRESSURE | AI | MPa | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
87 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:135 | DEAERATOR TEMPERATURE | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
88 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:138 | DEAERATOR STEAM PIPELINE TEMPERATURE | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
89 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:33 | DEAERATOR LEVEL | AI | mm | 0 | 2200 | 800 | 0 | 1000 | 0 | 0 | 0
90 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:48 | DEAERATOR LEVEL | AI | mm | 0 | 2200 | 800 | 0 | 1000 | 0 | 0 | 0
91 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:216 | CONTROL SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
92 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:45 | FEEDBACK SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
93 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:219 | CONTROL SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
94 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | DEAERATOR #1 | 3223 | DPU_2_A:51 | FEEDBACK SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
95 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:0 | #1 BOILER UPSTREAM CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
96 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:3 | #1 BOILER DOWNSTREAM-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
97 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:744 | #1 BOILER FEEDWATER FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
98 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:471 | CONTROL SIGNAL OF #1 BOILER MAIN FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
99 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:243 | FEEDBACK SIGNAL OF #1 BOILER MAIN FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
100 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:489 | CONTROL SIGNAL OF #1 BOILER SUBSIDIARY FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
101 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | FEED WATER PIPING #1 | 3224 | DPU_1_A:270 | FEEDBACK SIGNAL OF #1 BOILER SUBSIDIARY FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
102 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | HPH #1 | 3225 | DPU_3_A:270 | #1 TURBINE HP HEATER INLET WATER TEMP | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
103 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | HPH #1 | 3225 | DPU_3_A:273 | #1 TURBINE HP HEATER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
104 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | HPH #1 | 3225 | DPU_3_A:276 | #1 TURBINE HP HEATER OUTLET WATER TEMP | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
105 | PLTU Belitung 1 | FEED WATER SYSTEM #1 | HPH #1 | 3225 | DPU_3_A:84 | #1 TURBINE HP HEATER LEVEL | AI | mm | 0 | 900 | 0 | 0 | 300 | 800 | 0 | 0
106 | PLTU Belitung 1 | FEED WATER SYSTEM #2 | FEED WATER PIPING #1 | 3226
107 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | ELECTROSTATIC PRECIPITATOR (ESP) #1 SYSTEM | 3227 | DPU_1_A:732 | #1 BOILER INDUCED AIR FLOW | AI | m3/h | 0 | 200000 | 0 | 0 | 0 | 0 | 0 | 0
108 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:39 | #1 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:81 | #1 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:42 | #1 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:84 | #1 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:87 | #1 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:111 | #1 BOILER GAS PRESSURE BEFORE ECONONIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:93 | #1 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:147 | #1 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:96 | #1 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:150 | #1 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:108 | BOILER OUTLET GAS PRESSURE OF #1 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:153 | BOILER OUTLET GAS PRESSURE OF #1 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:375 | #1 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
121 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:435 | #1 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
122 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:378 | #1 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
123 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:438 | #1 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
124 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:390 | #1 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | AI | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
125 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:444 | #1 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | AI | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
126 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:309 | #1 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
127 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:333 | #1 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
128 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:312 | #1 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | AI | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
129 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:336 | #1 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | AI | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
130 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:315 | BOILER OUTLET GAS TEMPERATURE OF #1 BOILER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
131 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | FLUE GAS DUCTING SYSTEM #1 | 3228 | DPU_1_A:318 | BOILER OUTLET GAS TEMPERATURE OF #1 BOILER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
132 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | GAS ANALYZER #1 | 3336 | DPU_1_A:219 | BOILER OUTLET GAS O2% OF #1 BOILER | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
133 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | GAS ANALYZER #1 | 3336 | DPU_1_A:222 | GAS FLUE INLET O2% OF #1 BOILER | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
134 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:135 | #1 BOILER #1 INDUCED BRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:351 | FRONT BEARING TEMP OF #1 BOILER #1 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
136 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:705 | BACK BEARING TEMP OF #1 BOILER #1 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
137 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:465 | CONTROL SIGNAL OF #1 BOILER #1 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
138 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:237 | FEEDBACK SIGNAL OF #1 BOILER #1 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
139 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM A #1 | 3229 | DPU_1_A:255 | #1 BOILER #1 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
140 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:114 | #1 BOILER #2 INDUCED BRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:363 | FRONT BEARING TEMP OF #1 BOILER #2 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
142 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:366 | BACK BEARING TEMP OF #1 BOILER #2 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
143 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:486 | CONTROL SIGNAL OF #1 BOILER #2 IB FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
144 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:240 | FEEDBACK SIGNAL OF #1 BOILER #2 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
145 | PLTU Belitung 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN SYSTEM B #1 | 3230 | DPU_1_A:258 | #1 BOILER #2 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
146 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:372 | #1 BOILER FRONT ATTEMPERATOR TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
147 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:417 | #1 BOILER BACK ATTEMPERATOR TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
148 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:756 | #1 BOILER FRONT BESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
149 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:759 | #1 BOILER BACK BESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
150 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:468 | CONTROL SIGNAL OF #1 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
151 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:273 | FEEDBACK SIGNAL OF #1 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
152 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:492 | CONTROL SIGNAL OF #1 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
153 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ATTEMPERATOR HEATER #1 | 3231 | DPU_1_A:276 | FB FEEDBACK SIGNAL OF #1 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
154 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | DAILY OIL TANK | 3232 | DPU_2_A:96 | 1# 5M3 DAILY OIL TANK LEVEL | AI | mm | 0 | 2150 | 0 | 0 | 430 | 0 | 0 | 0
155 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | DAILY OIL TANK | 3232 | DPU_2_A:99 | 2# 5M3 DAILY OIL TANK LEVEL | AI | mm | 0 | 2150 | 0 | 0 | 430 | 0 | 0 | 0
156 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | DAILY OIL TANK | 3232 | DPU_2_A:102 | 3# 5M3 DAILY OIL TANK LEVEL | AI | mm | 0 | 2150 | 0 | 0 | 430 | 0 | 0 | 0
157 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | DAILY OIL TANK | 3232 | DPU_2_A:105 | 5M3 DAILY OIL TANK LEVEL | AI | mm | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
158 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | ECONOMIZER SYSTEM #1 | 3233 | DPU_1_A:786 | #1 BOILER FEEDWATER TEMPERATURE | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
159 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FEED BACK AIR FAN A SYSTEM #1 | 3234 | DPU_2_A:81 | #1 BOILER #1 RETURN FAN CURRENT INDICATE | AI | A | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0
160 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FEED BACK AIR FAN B SYSTEM #1 | 3235 | DPU_1_A:45 | #1 BOILER REFEED AIR FAN OUTLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
161 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FEED BACK AIR FAN B SYSTEM #1 | 3235 | DPU_2_A:84 | #1 BOILER #2 RETURN FAN CURRENT INDICATE | AI | A | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0
162 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:30 | #1 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
163 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:72 | #1 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
164 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:9 | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
165 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:63 | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
166 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:24 | #1 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0
167 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:66 | #1 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0
168 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:33 | #1 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -1000 | 1000 | -500 | 0 | -150 | 10 | 0 | 50
169 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:75 | #1 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -1000 | 1000 | -500 | 0 | -150 | 10 | 0 | 50
170 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:99 | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
171 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:141 | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
172 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:306 | #1 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
173 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:330 | #1 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
174 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:393 | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
175 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:453 | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
176 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:396 | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
177 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:450 | #1 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
178 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:420 | #1 BOILER UPPER TEMPERATURE OF BOILING BED | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
179 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:408 | #1 BOILER UPPER TEMPERATURE OF BOILING BED | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
180 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:402 | #1 BOILER MIDDLE FURNACE TEMPERATURE | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
181 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:423 | #1 BOILER MIDDLE FURNACE TEMPERATURE | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
182 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:399 | #1 BOILER FURNACE OUTLET TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
183 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:426 | #1 BOILER FURNACE OUTLET TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
184 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:411 | #1 BOILER SEPARATOR INLET GAS TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 950 | 0 | 1050
185 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE #1 | 3236 | DPU_1_A:456 | #1 BOILER SEPARATOR INLET GAS TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 950 | 0 | 1050
186 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE ASH & SLAG REMOVAL #1 | 3337 | DPU_1_A:177 | #1 BOILER SLAG BIN LEVEL | AI | mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE ASH & SLAG REMOVAL #1 | 3337 | DPU_2_A:75 | #1 BOILER #1 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
188 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE ASH & SLAG REMOVAL #1 | 3337 | DPU_2_A:222 | #1 BOILER #1 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
189 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE ASH & SLAG REMOVAL #1 | 3337 | DPU_2_A:486 | #1 BOILER #2 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
190 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | FURNACE ASH & SLAG REMOVAL #1 | 3337 | DPU_2_A:225 | #1 BOILER #2 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
191 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | HIGH TEMPERATURE HEATER #1 | 3237 | DPU_1_A:12 | #1 BOILER SUPERHEATER OUTLET HEADER PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
192 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | HIGH TEMPERATURE HEATER #1 | 3237 | DPU_1_A:432 | #1 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
193 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | HIGH TEMPERATURE HEATER #1 | 3237 | DPU_1_A:381 | #1 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
194 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | HIGH TEMPERATURE HEATER #1 | 3237 | DPU_1_A:384 | #1 BOILER SUPERHEATER INTERNEDIATE HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
195 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | HIGH TEMPERATURE HEATER #1 | 3237 | DPU_1_A:441 | #1 BOILER SUPERHEATER OUTLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
196 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNITION GUN A #1 | 3239 | DPU_1_A:21 | #1 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
197 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNITION GUN A #1 | 3239 | DPU_1_A:303 | #1 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
198 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNITION GUN B #1 | 3240 | DPU_1_A:69 | #1 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
199 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNITION GUN B #1 | 3240 | DPU_1_A:327 | #1 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
200 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNTION #1 | 3238 | DPU_2_A:87 | #1 BOILER FEEDING OIL PRESSURE | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
201 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNTION #1 | 3238 | DPU_2_A:90 | #1 BOILER FEEDING OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
202 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNTION #1 | 3238 | DPU_2_A:93 | #1 BOILER RETURN OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
203 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNTION #1 | 3238 | DPU_2_A:228 | CONTROL SIGNAL OF #1 BOILER RETURN OIL FLOW REGULATOR VALVE | AO | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
204 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | IGNTION #1 | 3238 | DPU_2_A:114 | FEEDBACK SIGNAL OF #1 BOILER RETURN OIL FLOW REGULATOR VALVE | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
205 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:117 | THE LOWER PRESSURE OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
206 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:120 | THE FEEDING BACK PRESSURE OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
207 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:123 | THE MIDDLE PRESSURE OF HI BOILER LEFT CYCLONE SEPARATOR | AI | Pa | -400 | 200 | 0 | 0 | 0 | 0 | 0 | 0
208 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:90 | #1 BOILER LEFT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -200 | 200 | 0 | 500
209 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:156 | THE FEEDING BACK BP OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0
210 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:159 | THE LOOSE DP OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0
211 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:405 | #1 BOILER LEFT CYCLONE REVERT TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 455 | 488 | 0 | 0
212 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LEFT CYCLONE SEPARATOR SYSTEM #1 | 3241 | DPU_1_A:726 | #1 BOILER AIR FLOW OF LEFT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
213 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | LOW TEMPERATURE HEATER #1 | 3242 | DPU_1_A:414 | #1 BOILER SWING PIPE INLET HEADER TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
214 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:18 | #1 BOILER PRIMARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
215 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:321 | FRONT BEARING TEMP OF #1 BOILER #1 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
216 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:324 | BACK BEARING TEMP OF #1 BOILER #1 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
217 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:708 | #1 PRIMARY AIR FLOW OF #1 BOILER | AI | Pa | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
218 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:459 | CONTROL SIGNAL OF #1 BOILER #1 PA FAN INLET DANGER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
219 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:228 | FEEDBACK SIGNAL OF #1 BOILER #1 PA FAN INLET DANGER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
220 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM A #1 | 3243 | DPU_1_A:225 | #1 BOILER #1 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
221 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:339 | FRONT BEARING TEMP OF #1 BOILER #2 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
222 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:342 | BACK BEARING TEMP OF #1 BOILER #2 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
223 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:711 | #2 PRIMARY AIR FLOW OF #1 BOILER | AI | Pa | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
224 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:480 | CONTROL SIGNAL OF #1 BOILER #2 PA FAN INLET DANGER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
225 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:261 | FEEDBACK SIGNAL OF #1 BOILER #2 PA FAN INLET DANGER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
226 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | PRIMARY AIR FAN SYSTEM B #1 | 3244 | DPU_1_A:264 | #1 BOILER #2 PA FAN CURRENT INDICATE | AI | A | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0
227 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:126 | THE LOWER PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
228 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:129 | THE FEEDING BACK PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | -400 | 200 | 0 | 0 | 0 | 0 | 0 | 0
229 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:132 | THE MIDDLE PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | -400 | 200 | 0 | 0 | 0 | 0 | 0 | 0
230 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:138 | #1 BOILER RIGHT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -200 | 200 | 0 | 500
231 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:162 | THE FEEDING BACK DP OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0
232 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:165 | THE LOOSE DP OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | -4 | 4 | 0 | 0 | 0 | 0 | 0 | 0
233 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:429 | #1 BOILER RIGHT CYCLONE REVERT TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 465 | 490 | 0 | 491
234 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3245 | DPU_1_A:729 | #1 BOILER AIR FLOW OF RIGHT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
235 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:345 | FRONT BEARING TEMP OF #1 BOILER #1 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
236 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:348 | BACK BEARING TEMP OF BOILERL #1 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
237 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:714 | #1 SECONDARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
238 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:780 | CONTROL SIGNAL OF #1 BOILER #1 SA FAN INLET DANGER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
239 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:234 | FEEDBACK SIGNAL OF #1 BOILER #1 SA FAN INLET DANGER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
240 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 | 3246 | DPU_1_A:231 | #1 BOILER #1 SA FAN CURRENT INDICATE | AI | A | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0
241 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM A #1 SECONDARY AIR FAN SYSTEM B #1 | 3247 | DPU_1_A:633 | #1 BOILER SECONDARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 5098 | 0 | 0
242 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:357 | FRONT BEARING TEMP OF #1 BOILER #2 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
243 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:360 | BACK BEARING TEMP OF #1 BOILER #2 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
244 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:717 | #2 SECONDARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
245 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:483 | CONTROL SIGNAL OF #1 BOILER #2 SA FAN INLET DANGER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
246 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:267 | FEEDBACK SIGNAL OF #1 BOILER #2 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
247 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | SECONDARY AIR FAN SYSTEM B #1 | 3248 | DPU_1_A:279 | #1 BOILER #2 SA FAN CURRENT INDICATE | AI | A | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0
248 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEAM DRUM #1 | 3249 | DPU_1_A:6 | #1 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
249 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEAM DRUM #1 | 3249 | DPU_1_A:60 | #1 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
250 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEAM DRUM #1 | 3249 | DPU_1_A:105 | #1 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
251 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEAM DRUM #1 | 3249 | DPU_1_A:168 | #1 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
252 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEEL OIL TANK | 3355 | DPU_2_A:108 | 1# 100M3 STEEL OIL TANK LEVEL | AI | mm | 0 | 5800 | 0 | 0 | 0 | 0 | 0 | 0
253 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | STEEL OIL TANK | 3355 | DPU_2_A:111 | 2# 100M3 STEEL OIL TANK LEVEL | AI | mm | 0 | 5800 | 0 | 0 | 0 | 0 | 0 | 0
254 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:36 | #1 BOILER LEFT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
255 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:78 | #1 BOILER RIGHT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
256 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:48 | #1 BOILER LEFT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
257 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:51 | #1 BOILER LEFT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
258 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:54 | #1 BOILER RIGHT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
259 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:57 | #1 BOILER RIGHT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
260 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:102 | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | -20 | 20 | 0 | 0 | 0 | 0 | 0 | 0
261 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:144 | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | -20 | 20 | 0 | 0 | 0 | 0 | 0 | 0
262 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:387 | #1 BOILER LEFT WIND BOX TEMPERATURE | AI | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
263 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:447 | #1 BOILER RIGHT WIND BOX TEMPERATURE | AI | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
264 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:720 | #1 BOILER AIR FLOW OF LEFT WIND BOX | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 5098 | 0 | 0
265 | PLTU Belitung 1 | FURNACE & CYCLONE SYSTEM #1 | WINDBOX #1 | 3250 | DPU_1_A:723 | #1 BOILER AIR FLOW OF RIGHT WIND BOX | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 5098 | 0 | 0
266 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | COOLER SYSTEM #1 | 3251 | DPU_3_A:288 | #1 TURBINE GENERATOR OUTLET WIND TEMP 1 | AI | C | 0 | 50 | 0 | 0 | 0 | 40 | 0 | 0
267 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | COOLER SYSTEM #1 | 3251 | DPU_3_A:291 | #1 TURBINE GENERATOR OUTLET WIND TEMP 2 | AI | C | 0 | 100 | 0 | 0 | 0 | 40 | 0 | 0
268 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | COOLER SYSTEM #1 | 3251 | DPU_3_A:294 | #1 TURBINE GENERATOR INLET WIND TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
269 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | COOLER SYSTEM #1 | 3251 | DPU_3_A:297 | #1 TURBINE AIR COOLER OUTLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
270 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:333 | #1 TURBINE GENERATOR STATOR CORE TEMP 6 | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
271 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:117 | #1 TURBINE GENERATOR FRONT SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
272 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:153 | #1 TURBINE GENERATOR BACK SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
273 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:522 | #1 GENERATOR ACTIVE POWER | AI |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:519 | #1 GENERATOR FREQUENCY | AI |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 3252 | DPU_3_A:456 | #1 GENERATOR POWER FACTOR | AI |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | PLTU Belitung 1 | Generator System #1 | GENERATOR BEARING 3 #1 | 3386
277 | PLTU Belitung 1 | Generator System #1 | GENERATOR BEARING 4 #1 | 3384
278 | PLTU Belitung 1 | Generator System #1 | GENERATOR COOLER SYSTEM #1 | 3388
279 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:300 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 1 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
280 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:303 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 2 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
281 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:306 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 3 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
282 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:309 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 4 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
283 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:312 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 5 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
284 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:315 | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 6 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
285 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:318 | #1 TURBINE GENERATOR STATOR CORE TEMP 1 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
286 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:321 | #1 TURBINE GENERATOR STATOR CORE TEMP 2 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
287 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:324 | #1 TURBINE GENERATOR STATOR CORE TEMP 3 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
288 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:327 | #1 TURBINE GENERATOR STATOR CORE TEMP 4 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
289 | PLTU Belitung 1 | GENERATOR SYSTEM #1 | GENERATOR EXCITER SET #1 | 3253 | DPU_3_A:330 | #1 TURBINE GENERATOR STATOR CORE TEMP 5 | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
290 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | AC OIL PUMP #1 | 3254 | DPU_3_A:24 | #1 TURBINE AC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
291 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | DC OIL PUMP #1 | 3255 | DPU_3_A:498 | #1 TURBINE DC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
292 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | HP OIL PUMP #1 | 3256 | DPU_3_A:159 | #1 TURBINE HP STARTING OIL PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
293 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | LUBRICANT SUPPLY PIPING SYSTEM #1 | 3257 | DPU_3_A:33 | #1 TURBINE LUBE OIL PRE. | AI | MPa | 0 | 0.25 | 0.015 | 0.045 | 0.7 | 0.15 | 2 | 0
294 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | MAIN OIL TANK #1 | 3258 | DPU_3_A:87 | #1 TURBINE OIL TANK LEVEL | AI | mm | -200 | 200 | -200 | 0 | -150 | 150 | 0 | 200
295 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 A | 3346 | DPU_3_A:246 | #1 TURBINE OIL COOLER INLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
296 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 A | 3346 | DPU_3_A:252 | #1 TURBINE OIL COOLER OUTLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
297 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 A | 3346 | DPU_3_A:258 | #1 TURBINE OIL COOLER INLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
298 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 A | 3346 | DPU_3_A:264 | #1 TURBINE OIL COOLER OUTLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
299 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 B | 3347 | DPU_3_A:249 | #1 TURBINE OIL COOLER INLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
300 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 B | 3347 | DPU_3_A:255 | #1 TURBINE OIL COOLER OUTLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
301 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 B | 3347 | DPU_3_A:261 | #1 TURBINE OIL COOLER INLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
302 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | OIL COOLER SYSTEM #1 B | 3347 | DPU_3_A:267 | #1 TURBINE OIL COOLER OUTLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
303 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | STEAM TURBINE MAIN OIL PUMP #1 | 3259 | DPU_3_A:12 | #1 TURBINE MAIN OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0.8 | 0 | 0 | 0
304 | PLTU Belitung 1 | LUBRICATION SUPPLY SYSTEM #1 | STEAM TURBINE MAIN OIL PUMP #1 | 3259 | DPU_3_A:60 | #1 TURBINE MAIN OIL PUMP INTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0.8 | 0 | 0 | 0
305 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3262 | DPU_1_A:15 | #1 BOILER MAIN STEAM PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
306 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3262 | DPU_3_A:336 | #1 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | AI | C | 0 | 600 | 0 | 0 | 455 | 488 | 0 | 0
307 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3262 | DPU_1_A:369 | #1 BOILER MAIN STEAM TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 465 | 490 | 0 | 491
308 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3262 | DPU_1_A:750 | #1 BOILER MAIN STEAM FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
309 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3262 | DPU_3_A:525 | #1 TURBINE MAIN STEAM PRE.BEF ELEC MSV | AI | MPa | 0 | 10 | 0 | 0 | 0 | 5.098 | 0 | 0
310 | PLTU Belitung 1 | Main Steam System #1 | MAIN STEAM PIPING SYSTEM #1 (ELECTRIC MSV SYSTEM) | 3344
311 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:54 | #1 TURBINE AST OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
312 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:57 | #1 TURBINE DPC OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
313 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:165 | #1 TURBINE #1 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
314 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:168 | #1 TURBINE #2 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
315 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:171 | #1 TURBINE #3 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
316 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:174 | #1 TURBINE #4 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
317 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:177 | #1 TURBINE #5 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
318 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:180 | #1 TURBINE #6 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
319 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:183 | #1 TURBINE #7 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
320 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:186 | #1 TURBINE #8 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
321 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:189 | #1 TURBINE #9 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
322 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:192 | #1 TURBINE #10 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
323 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:195 | #1 TURBINE #1 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
324 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:198 | #1 TURBINE #2 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
325 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:201 | #1 TURBINE #3 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
326 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:204 | #1 TURBINE #4 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
327 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:207 | #1 TURBINE #1 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
328 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:210 | #1 TURBINE #2 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
329 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:213 | #1 TURBINE #3 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
330 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:216 | #1 TURBINE #4 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
331 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:219 | #1 TURBINE #1 POSITIVE THRUST BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
332 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:222 | #1 TURBINE #1 NEGATIVE THRUST BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
333 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:342 | #1 TURBINE CYLINDER WALL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
334 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:345 | #1 TURBINE CYLINDER WALL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
335 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:348 | #1 TURBINE EXTRACTION 1 STEAM PRE. | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
336 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:102 | #1 TURBINE AXIAL POSITION 1 | AI | mm | -2 | 2 | -0.7 | 0 | -0.6 | 1 | 0 | 1.3
337 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:126 | #1 TURBINE AXIAL POSITION 2 | AI | mm | -2 | 2 | -0.7 | 0 | -0.6 | 1 | 0 | 1.3
338 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:465 | #1 TURBINE STEAM TURBINE SPEED 1 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
339 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:129 | #1 TURBINE STEAM TURBINE SPEED 2 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
340 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:132 | #1 TURBINE STEAM TURBINE SPEED 3 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
341 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:114 | #1 TURBINE STEAM TURBINE FRONT SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
342 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:150 | #1 TURBINE STEAM TURBINE BACK SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
343 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:504 | #1 TURBINE STARTING OIL PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
344 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:6 | #1 TURBINE SAFETY OIL PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
345 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:9 | #1 TURBINE EXHAUST STEAM PRE | AI | MPa | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
346 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 3263 | DPU_3_A:15 | #1 TURBINE VELOCITY STAGE PRE. | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
347 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 TO SEALING STEAM SYSTEM | 3264 | DPU_3_A:339 | #1 TURBINE MAIN STEAM TEMP. BEF MSV | AI | C | 0 | 600 | 0 | 0 | 455 | 488 | 0 | 0
348 | PLTU Belitung 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 TO SEALING STEAM SYSTEM | 3264 | DPU_3_A:45 | #1 TURBINE MAIN STEAM PRE.BEF MSV | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
349 | PLTU Belitung 1 | Sealing Steam System #1 | DRAUGHT FAN GLAND STEAM CONDENSER A #1 | 3334
350 | PLTU Belitung 1 | Sealing Steam System #2 | DRAUGHT FAN GLAND STEAM CONDENSER A #2 | 3335
351 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING FOR HP FEED WATER #1 | 3351 | DPU_3_A:42 | #1 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
352 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING FOR HP FEED WATER #1 | 3351 | DPU_3_A:48 | #1 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
353 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING FOR HP FEED WATER #1 | 3351 | DPU_3_A:459 | #1 TURBINE EXTRACTION 1 STEAM FLOW | AI | t/h | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0
354 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING FOR HP FEED WATER #1 | 3351 | DPU_3_A:18 | #1 TURBINE EXTRACTION STEAM PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
355 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING LP CONDENSATE #1 | 3353 | DPU_3_A:51 | #1 TURBINE LP HEATER INLET STEAM PRE. | AI | MPa | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
356 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM PIPING LP CONDENSATE #1 | 3353 | DPU_3_A:279 | #1 TURBINE LP HEATER INLET STEAM TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
357 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #1 | 3265 | DPU_2_A:27 | DEAERATOR STEAM PIPELINE PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
358 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #1 | 3265 | DPU_3_A:231 | #1 TURBINE CONDENSER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 60 | 80 | 0 | 0
359 | PLTU Belitung 1 | TURBINE EXTRACTION SYSTEM #1 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #1 | 3265 | DPU_3_A:234 | #1 TURBINE CONDENSER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 60 | 80 | 0 | 0
360 | PLTU Belitung 1 | Turbine System #1 | EXTRACTION STEAM PIPING FOR HP FEED WATER PIPING #1 | 3390
361 | PLTU Belitung 1 | Turbine System #1 | EXTRACTION STEAM PIPING LP CONDENSATE WATER PIPING #1 | 3392
362 | PLTU Belitung 1 | Turbine System #1 | HP TURBINE #1 | 3368
363 | PLTU Belitung 1 | Turbine System #1 | TURBINE BEARING 1 #1 | 3372
364 | PLTU Belitung 1 | Turbine System #1 | TURBINE BEARING 2 #1 | 3370
365 | PLTU Belitung 1 | Turbine System #1 | TURBINE BEARING THRUST #1 | 3374
366 | PLTU Belitung 2 |  | WATER TANK #2 | 3363
367 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING FOR HP FEED WATER PIPING #2 | 3352 | DPU_6_A:18 | #2 TURBINE EXTRACTION STEAM PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
368 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING FOR HP FEED WATER PIPING #2 | 3352 | DPU_6_A:42 | #2 TURBINE CONTROL WATER PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
369 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING FOR HP FEED WATER PIPING #2 | 3352 | DPU_6_A:48 | #2 TURBINE CONTROL WATER PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
370 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING FOR HP FEED WATER PIPING #2 | 3352 | DPU_6_A:525 | #2 TURBINE EXTRACTION 1 STEAM FLOW | AI | t/h | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0
371 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING LP CONDENSATE #2 | 3354 | DPU_6_A:51 | #2 TURBINE LP HEATER INLET STEAM PRE | AI | MPa | -0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
372 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM PIPING LP CONDENSATE #2 | 3354 | DPU_6_A:279 | #2 TURBINE LP HEATER INLET STEAM TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
373 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL BUNKER SYSTEM A #2 | 3266 | DPU_4_A:171 | #2 BOILER #1 COAL BUNKER LEVEL | AI | mm | 0 | 0 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
374 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL BUNKER SYSTEM B #2 | 3267 | DPU_4_A:174 | #2 BOILER #2 COAL BUNKER LEVEL | AI | mm | 0 | 0 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
375 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER A #2 | 3268 | DPU_4_A:936 | #2 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
376 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER A #2 | 3268 | DPU_4_A:249 | #2 BOILER #1 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
377 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER A #2 | 3268 | DPU_4_A:474 | #2 BOILER #1 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
378 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER B #2 | 3269 | DPU_4_A:282 | #2 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
379 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER B #2 | 3269 | DPU_4_A:285 | #2 BOILER #2 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
380 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER B #2 | 3269 | DPU_4_A:477 | #2 BOILER #2 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
381 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER C #2 | 3270 | DPU_4_A:291 | #2 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
382 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER C #2 | 3270 | DPU_4_A:294 | #2 BOILER #3 COAL FEEDER ROTATIONAL SPEED INPUT | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
383 | PLTU Belitung 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER C #2 | 3270 | DPU_4_A:495 | #2 BOILER #3 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
384 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:507 | #2 TURBINE CONDENSER VACUUM | AI | Kpa | -100 | 0 | 0 | 0 | 0 | -87 | 0 | -61
385 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:510 | #2 TURBINE CONDENSER VACUUM | AI | Kpa | -100 | 0 | 0 | 0 | 0 | -87 | 0 | -61
386 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:225 | #2 TURBINE CONDENSER CIRCULATING VATER OUTLET TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
387 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:228 | #2 TURBINE CONDENSER CIRCULATING VATER OUTLET TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
388 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:237 | #2 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
389 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:240 | #2 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
390 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:243 | #2 TURBINE CONDENSATION WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
391 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | CONDENSER #2 | 3273 | DPU_6_A:540 | #2 TURBINE CONDENSER LEVEL | AI | mm | 0 | 1025 | 0 | 0 | 0 | 600 | 0 | 1000
392 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | GSH #2 | 3274 | DPU_6_A:36 | #2 TURBINE EXTRACTION STM PRE.DF GLAND STM HEATER | AI | MPa | -0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0
393 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | GSH #2 | 3274 | DPU_6_A:39 | #2 TURBINE AVERAGE PRE.TANK PRE | AI | MPa | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
394 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | GSH #2 | 3274 | DPU_6_A:354 | CONTROL SIGNAL OF #2 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
395 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | GSH #2 | 3274 | DPU_5_A:402 | FEEDBACK SIGNAL OF #2 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
396 | PLTU Belitung 2 | CONDENSATE SYSSTEM #2 | VACCUM PUMP A #2 VACCUM PUMP B #2 | 3275 | DPU_6_A:513 | #2 TURBINE VACUUM PUMP INLET PRE | AI | Kpa | -160 | 0 | 0 | 0 | -95 | -88 | 0 | 0
397 | PLTU Belitung 2 | CONDENSATE SYSTEM | GLAND STEAM HEATER SYSTEM #2 | 3365
398 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP SYSTEM A#2 | 3271 | DPU_6_A:21 | #2 TURBINE #1 CONDENSATE PUMP OUTLET PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
399 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP SYSTEM A#2 | 3271 | DPU_6_A:120 | #2 TURBINE #1 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
400 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP SYSTEM B#2 | 3272 | DPU_6_A:63 | #2 TURBINE #2 CONDENSATE PUMP OUTLET PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
401 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP SYSTEM B#2 | 3272 | DPU_6_A:519 | #2 TURBINE CONDENSATION WATER FLOW | AI | t/h | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0
402 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP SYSTEM B#2 | 3272 | DPU_6_A:156 | #2 TURBINE #2 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
403 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | LPH #2 | 3343 | DPU_6_A:282 | #2 TURBINE LP HEATER INLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
404 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | LPH #2 | 3343 | DPU_6_A:285 | #2 TURBINE LP HEATER OUTLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
405 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | VACCUM PUMP A #2 | 3356 | DPU_6_A:162 | #2 TURBINE VACUUM PUMP SK-6 CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
406 | PLTU Belitung 2 | Condensate System #2 | VACCUM PUMP B #2 | 3357
407 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | WATER EJECTOR SYSTEM #2 | 3361 | DPU_6_A:351 | CONTROL SIGNAL OF #2 TURBINE CONDENSER LEVEL CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
408 | PLTU Belitung 2 | CONDENSATE SYSTEM #2 | WATER EJECTOR SYSTEM #2 | 3361 | DPU_6_A:534 | FEEDBACK SIGNAL OF #2 TURBINE CONDENSER LEVEL CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
409 | PLTU Belitung 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 3276 | DPU_6_A:72 | #2 TURBINE BALL CIRCULATING PUMP OUTLET PRE | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
410 | PLTU Belitung 2 | COOLING SYSTEM #2 | CLOSED CYCLE COOLING WATER PUMP #2A | 3278 | DPU_5_A:0 | #2 TURBINE #1 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
411 | PLTU Belitung 2 | COOLING SYSTEM #2 | CLOSED CYCLE COOLING WATER PUMP #2B | 3277 | DPU_5_A:57 | #2 TURBINE #2 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
412 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:36 | #1 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
413 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:39 | #1.2 CIRCULATING WATER PUMP OUTLET MAIN PIPE PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
414 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:150 | FRONT BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
415 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:153 | BACK BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
416 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:156 | MOTOR STATOR TEMP 1 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
417 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:159 | MOTOR STATOR TEMP 2 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
418 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:162 | MOTOR STATOR TEMP 3 OF #1 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
419 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:405 | #1.2 CIRCULATING WATER PUMP OUTLET MAIN PIPE FLOW | AI | t/h | 0 | 6000 | 0 | 0 | 0 | 0 | 0 | 0
420 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP A #2 | 3279 | DPU_5_A:69 | #2 TURBINE #1 CIRCULATING WATER PUMP CURRENT INDICATOR | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
421 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:54 | #2 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0.05 | 0 | 0 | 0
422 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:165 | FRONT BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
423 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:168 | BACK BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
424 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:171 | MOTOR STATOR TEMP 1 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
425 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:174 | MOTOR STATOR TEMP 2 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
426 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:177 | MOTOR STATOR TEMP 3 OF #2 CIRCULATING WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
427 | PLTU Belitung 2 | COOLING SYSTEM #2 | CWP PUMP B #2 | 3281 | DPU_5_A:72 | #2 TURBINE #2 CIRCULATING WATER PUMP CURRENT INDICATOR | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
428 | PLTU Belitung 2 | COOLING SYSTEM #2 | RECIRCULATING PUMP A #2 | 3282 | DPU_5_A:6 | #2 TURBINE #1 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
429 | PLTU Belitung 2 | COOLING SYSTEM #2 | RECIRCULATING PUMP B #2 | 3283 | DPU_5_A:60 | #2 TURBINE #2 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
430 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:12 | LP FEED WATER PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
431 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:15 | #1 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
432 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:105 | FRONT BEARING TEMP OF #1 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
433 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:108 | BACK BEARING TEMP OF #1 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
434 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:111 | MOTOR STATOR TEMP 1 OF #1 FEED WATER PUMP | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
435 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:114 | MOTOR STATOR TEMP 2 OF #1 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
436 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:117 | MOTOR STATOR TEMP 3 OF #1 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
437 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-A #2 | 3284 | DPU_5_A:3 | #2 TURBINE #1 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
438 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:18 | #2 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
439 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:120 | FRONT BEARING TEMP OF #2 FEED WATER PUMP MOTOR | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
440 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:123 | BACK BEARING TEMP OF #2 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
441 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:126 | MOTOR STATOR TEMP 1 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
442 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:129 | MOTOR STATOR TEMP 2 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
443 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:132 | MOTOR STATOR TEMP 3 OF #2 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
444 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-B #2 | 3285 | DPU_5_A:63 | #2 TURBINE #2 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
445 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:21 | #3 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 7.8 | 0 | 0
446 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:135 | FRONT BEARING TEMP OF #3 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
447 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:138 | BACK BEARING TEMP OF #3 FEED WATER PUMP MOTOR | AI | C | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 80
448 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:141 | MOTOR STATOR TEMP 1 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
449 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:144 | MOTOR STATOR TEMP 2 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
450 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:147 | MOTOR STATOR TEMP 3 OF #3 FEED WATER PUMP | AI | C | 0 | 300 | 0 | 0 | 0 | 110 | 0 | 120
451 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | BFP-C #2 | 3286 | DPU_5_A:66 | #2 TURBINE #3 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
452 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:9 | DEAERATOR PRESSURE | AI | MPa | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
453 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:99 | DEAERATOR TEMPERATURE | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
454 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:102 | DEAERATOR STEAM PIPELINE TEMPERATURE | AI | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
455 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:33 | DEAERATOR LEVEL | AI | mm | 0 | 2200 | 800 | 0 | 1000 | 0 | 0 | 0
456 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:48 | DEAERATOR LEVEL | AI | mm | 0 | 2200 | 800 | 0 | 1000 | 0 | 0 | 0
457 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:180 | CONTROL SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
458 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:45 | FEEDBACK SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
459 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:183 | CONTROL SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
460 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | DEAERATOR #2 | 3287 | DPU_5_A:51 | FEEDBACK SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
461 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:0 | #2 BOILER UPSTREAN-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
462 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:3 | #2 BOILER DOWNSTREAN-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
463 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:708 | #2 BOILER FEEDWATER FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
464 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:471 | CONTROL SIGNAL OF #2 BOILER MAIN FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
465 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:243 | FEEDBACK SIGNAL OF #2 BOILER MAIN FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
466 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:489 | CONTROL SIGNAL DFI2 BOILER SUBSIDIARY FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
467 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | FEED WATER PIPING #2 | 3288 | DPU_4_A:270 | FEEDBACK SIGNAL OF #2 BOILER SUBSIDIARY FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
468 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | HPH #2 | 3289 | DPU_6_A:270 | #2 TURBINE HP HEATER INLET WATER TEMP | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
469 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | HPH #2 | 3289 | DPU_6_A:273 | #2 TURBINE HP HEATER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
470 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | HPH #2 | 3289 | DPU_6_A:276 | #2 TURBINE HP HEATER OUTLET WATER TEMP | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
471 | PLTU Belitung 2 | FEED WATER SYSTEM #2 | HPH #2 | 3289 | DPU_6_A:84 | #2 TURBINE HP HEATER LEVEL | AI | mm | 0 | 0 | 0 | 0 | 300 | 800 | 0 | 0
472 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | ELECTROSTATIC PRECIPITATOR (ESP) #2 SYSTEM | 3290 | DPU_4_A:735 | #2 BOILER INDUCED AIR FLOW | AI | m3/h | 0 | 200000 | 0 | 0 | 0 | 0 | 0 | 0
473 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:840 | #2 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
474 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:843 | #2 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:846 | #2 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
476 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:849 | #2 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
477 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:852 | #2 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
478 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:855 | #2 BOILER GAS PRESSURE BEFORE ECONONIZER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
479 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:858 | #2 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
480 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:861 | #2 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | C | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:864 | #2 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:867 | #2 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:870 | BOILER OUTLET GAS PRESSURE OF #2 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:873 | BOILER OUTLET GAS PRESSURE OF #2 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:375 | #2 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
486 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:435 | #2 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
487 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:378 | #2 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
488 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:438 | #2 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | AI | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
489 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:390 | #2 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | AI | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
490 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:444 | #2 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | AI | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
491 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:909 | #2 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
492 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:912 | #2 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
493 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:312 | #2 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | AI | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
494 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:915 | #2 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | AI | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
495 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:897 | BOILER OUTLET GAS TEMPERATURE OF #2 BOILER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
496 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | FLUE GAS DUCTING SYSTEM #2 | 3291 | DPU_4_A:903 | BOILER OUTLET GAS TEMPERATURE OF #2 BOILER | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
497 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | GAS ANALYZER #2 | 3341 | DPU_4_A:891 | BOILER OUTLET GAS O2% OF #2 BOILER | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
498 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | GAS ANALYZER #2 | 3341 | DPU_4_A:222 | GAS FLUE INLET O2% OF #2 BOILER | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
499 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:828 | #2 BOILER #1 INDUCED BRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:351 | FRONT BEARING TEMP OF #2 BOILER #1 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
501 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:354 | BACK BEARING TEMP OF #2 BOILER #1 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
502 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:465 | CONTROL SIGNAL OF #2 BOILER #1 IB FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
503 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:237 | FEEDBACK SIGNAL OF #2 BOILER #1 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
504 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM A #2 | 3292 | DPU_4_A:255 | #2 BOILER #1 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
505 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:831 | #2 BOILER #2 INDUCED BRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:363 | FRONT BEARING TEMP OF #2 BOILER #2 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 75
507 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:366 | BACK BEARING TEMP OF #2 BOILER #2 INDUCED DRAFT FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
508 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:486 | CONTROL SIGNAL OF #2 BOILER #2 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
509 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:240 | FEEDBACK SIGNAL OF #2 BOILER #2 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
510 | PLTU Belitung 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN SYSTEM B #2 | 3293 | DPU_4_A:258 | #2 BOILER #2 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
511 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:372 | #2 BOILER FRONT ATTEMPERATOR TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
512 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:417 | #2 BOILER BACK ATTEMPERATOR TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
513 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:717 | #2 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
514 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:720 | #2 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
515 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:468 | CONTROL SIGNAL OF #2 BOILER FRONT ATTENPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
516 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:273 | FEEDBACK SIGNAL OF #2 BOILER FRONT ATTENPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
517 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:492 | CONTROL SIGNAL OF #2 BOILER BACK ATTENPERATING VOTER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
518 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ATTEMPERATOR HEATER #2 | 3294 | DPU_4_A:276 | FEEDBACK SIGNAL OF #2 BOILER BACK ATTENPERATING VOTER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
519 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | ECONOMIZER SYSTEM #2 | 3295 | DPU_4_A:924 | #2 BOILER FEEDWATER TEMPERATURE | AI | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
520 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FEED BACK AIR FAN A SYSTEM #2 | 3296 | DPU_5_A:81 | #2 BOILER #1 RETURN FAN CURRENT INDICATE | AI | A | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0
521 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FEED BACK AIR FAN B SYSTEM #2 | 3297 | DPU_4_A:45 | #2 BOILER REFEED AIR FAN OUTLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
522 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FEED BACK AIR FAN B SYSTEM #2 | 3297 | DPU_5_A:84 | #2 BOILER #2 RETURN FAN CURRENT INDICATE | AI | A | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0
523 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:30 | #2 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
524 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:72 | #2 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
525 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:9 | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
526 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:63 | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
527 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:885 | #2 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0
528 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:882 | #2 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1600 | 0 | 0 | 0 | 0 | 0 | 0
529 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:876 | #2 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -1000 | 1000 | -500 | 0 | -150 | 10 | 0 | 50
530 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:879 | #2 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -1000 | 1000 | -500 | 0 | -150 | 10 | 0 | 50
531 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:930 | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
532 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:141 | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 455 | 488 | 0 | 0
533 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:306 | #2 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
534 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:330 | #2 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
535 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:393 | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
536 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:396 | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
537 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:450 | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
538 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:453 | #2 BOILER BED OF MATERIAL TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 400 | 1000 | 0 | 1100
539 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:408 | #2 BOILER UPPER TEMPERATURE OF BOILING BED | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
540 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:420 | #2 BOILER UPPER TEMPERATURE OF BOILING BED | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
541 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:402 | #2 BOILER MIDDLE FURNACE TEMPERATURE | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
542 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:423 | #2 BOILER MIDDLE FURNACE TEMPERATURE | AI | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
543 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:399 | #2 BOILER FURNACE OUTLET TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
544 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:426 | #2 BOILER FURNACE OUTLET TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
545 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:411 | #2 BOILER SEPARATOR INLET GAS TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
546 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE #2 | 3298 | DPU_4_A:456 | #2 BOILER SEPARATOR INLET GAS TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
547 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE ASH & SLAG REMOVAL #2 | 3338 | DPU_4_A:177 | #2 BOILER SLAG BIN LEVEL | AI | mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
548 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE ASH & SLAG REMOVAL #2 | 3338 | DPU_5_A:75 | #2 BOILER #1 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
549 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE ASH & SLAG REMOVAL #2 | 3338 | DPU_5_A:186 | #2 BOILER #1 COLD SLAG REMOTE SPEED CONTROL | AO | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
550 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE ASH & SLAG REMOVAL #2 | 3338 | DPU_5_A:78 | #2 BOILER #2 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
551 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | FURNACE ASH & SLAG REMOVAL #2 | 3338 | DPU_5_A:189 | #2 BOILER #2 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
552 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #1 | 3299
553 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #2 | 3300 | DPU_4_A:12 | #2 BOILER SUPERHEATER OUTLET HEADER PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
554 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #2 | 3300 | DPU_4_A:381 | #2 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
555 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #2 | 3300 | DPU_4_A:432 | #2 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
556 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #2 | 3300 | DPU_4_A:384 | #2 BOILER SUPERHEATER INTERNEDIATE HEADER TEMF | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
557 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | HIGH TEMPERATURE HEATER #2 | 3300 | DPU_4_A:441 | #2 BOILER SUPERHEATER OUTLET HEADER TEMP | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
558 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION #2 | 3301 | DPU_5_A:87 | #2 BOILER FEEDING OIL PRESSURE | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
559 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION #2 | 3301 | DPU_5_A:90 | #2 BOILER FEEDING OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
560 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION #2 | 3301 | DPU_5_A:93 | #2 BOILER RETURN OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
561 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION #2 | 3301 | DPU_5_A:192 | CONTROL SIGNAL OF #2 BOILER RETURN OIL FLOW REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
562 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION #2 | 3301 | DPU_5_A:96 | FEEDBACK SIGNAL OF #2 BOILER RETURN OIL FLOW REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
563 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION GUN A #2 | 3302 | DPU_4_A:21 | #2 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
564 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION GUN A #2 | 3302 | DPU_4_A:303 | #2 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
565 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION GUN B #2 | 3303 | DPU_4_A:69 | #2 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
566 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | IGNITION GUN B #2 | 3303 | DPU_4_A:327 | #2 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | AI | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
567 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:117 | THE LOWER PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
568 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:120 | THE FEEDING BACK PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
569 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:123 | THE MIDDLE PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
570 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:834 | #2 BOILER LEFT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -200 | 200 | 0 | 500
571 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:156 | THE FEEDING BACK BP OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
572 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:159 | THE LOOSE DP OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
573 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:405 | #2 BOILER LEFT CYCLONE REVERT TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
574 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LEFT CYCLONE SEPARATOR SYSTEM #2 | 3304 | DPU_4_A:744 | #2 BOILER AIR FLOW OF LEFT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
575 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | LOW TEMPERATURE HEATER #2 | 3305 | DPU_4_A:414 | #2 BOILER SWING PIPE INLET HEADER TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
576 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:18 | #2 BOILER PRIMARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
577 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:321 | FRONT BEARING TEMP OF #2 BOILER #1 PRIMARY AIR | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
578 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:324 | BACK BEARING TEMP OF #2 BOILER #1 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
579 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:723 | #1 PRIMARY AIR FLOW OF #2 BOILER | AI | Pa | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
580 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:459 | CONTROL SIGNAL OF #2 BOILER #1 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
581 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:231 | FEEDBACK SIGNAL OF #2 BOILER #1 PA FAN INLET DANGER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
582 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM A #2 | 3306 | DPU_4_A:225 | #2 BOILER #1 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
583 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:339 | FRONT BEARING TEMP OF #2 BOILER #2 PRIMARY AIR | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
584 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:342 | BACK BEARING TEMP OF #2 BOILER #2 PRIMARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
585 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:726 | #2 PRIMARY AIR FLOW OF #2 BOILER | AI | Pa | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
586 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:480 | CONTROL SIGNAL OF #2 BOILER #2 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
587 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:261 | FEEDBACK SIGNAL OF #2 BOILER #2 PA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
588 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | PRIMARY AIR FAN SYSTEM B #2 | 3307 | DPU_4_A:264 | #2 BOILER #2 PA FAN CURRENT INDICATE | AI | A | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0
589 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #1 | 3308
590 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:126 | THE LOWER PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
591 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:129 | THE FEEDING BACK PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
592 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:132 | THE MIDDLE PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
593 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:837 | #1 BOILER RIGHT CYCLONE SEPARATOR INLET PRESSUREI | AI | Pa | -500 | 500 | -500 | 0 | -200 | 200 | 0 | 500
594 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:162 | THE FEEDING BACK DP OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
595 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:165 | THE LOOSE DP OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
596 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:429 | #2 BOILER RIGHT CYCLONE REVERT TEMPERATURE | AI | C | 0 | 1200 | 0 | 0 | 465 | 490 | 0 | 491
597 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | RIGHT CYCLONE SEPARATOR SYSTEM #2 | 3309 | DPU_4_A:747 | #2 BOILER AIR FLOW OF RIGHT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
598 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:345 | FRONT BEARING TEMP OF #2 BOILER #1 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
599 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:348 | BACK BEARING TEMP OF #2 BOILER #1 SECONDARY AIR | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
600 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:729 | #1 SECONDARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
601 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:462 | CONTROL SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
602 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:234 | -FB FEEDBACK SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
603 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 | 3311 | DPU_4_A:228 | #2 BOILER #1 SA FAN CURRENT INDICATE | AI | A | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0
604 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM A #2 SECONDARY AIR FAN SYSTEM B #2 | 3312 | DPU_4_A:27 | #2 BOILER SECONDARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 5098 | 0 | 0
605 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:357 | FRONT BEARING TEMP OF #2 BOILER #2 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
606 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:360 | BACK BEARING TEMP OF #2 BOILER #2 SECONDARY AIR FAN | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
607 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:732 | #2 SECONDARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
608 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:483 | CONTROL SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
609 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:267 | FEEDBACK SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
610 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | SECONDARY AIR FAN SYSTEM B #2 | 3313 | DPU_4_A:279 | #2 BOILER #2 SA FAN CURRENT INDICATE | AI | A | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0
611 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | STEAM DRUM #2 | 3314 | DPU_4_A:6 | #2 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
612 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | STEAM DRUM #2 | 3314 | DPU_4_A:60 | #2 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
613 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | STEAM DRUM #2 | 3314 | DPU_4_A:105 | #2 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
614 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | STEAM DRUM #2 | 3314 | DPU_4_A:168 | #2 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
615 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:36 | #2 BOILER LEFT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
616 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:78 | #2 BOILER RIGHT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
617 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:48 | #2 BOILER LEFT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
618 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:51 | #2 BOILER LEFT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
619 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:54 | #2 BOILER RIGHT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
620 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:57 | #2 BOILER RIGHT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
621 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:102 | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 465 | 490 | 0 | 491
622 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:144 | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
623 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:387 | #2 BOILER LEFT WIND BOX TEMPERATURE | AI | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
624 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:447 | #2 BOILER RIGHT WIND BOX TEMPERATURE | AI | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
625 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:954 | #2 BOILER AIR FLOW OF LEFT WIND BOX | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
626 | PLTU Belitung 2 | FURNACE & CYCLONE SYSTEM #2 | WINDBOX #2 | 3315 | DPU_4_A:918 | #2 BOILER AIR FLOW OF RIGHT WIND BOX | AI | m3/h | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0
627 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | COOLER SYSTEM #2 | 3316 | DPU_6_A:288 | #2 TURBINE GENERATOR OUTLET WIND TEMP 1 | AI | C | 0 | 50 | 0 | 0 | 0 | 40 | 0 | 0
628 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | COOLER SYSTEM #2 | 3316 | DPU_6_A:291 | #2 TURBINE GENERATOR OUTLET WIND TEMP 2 | AI | C | 0 | 100 | 0 | 0 | 0 | 40 | 0 | 0
629 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | COOLER SYSTEM #2 | 3316 | DPU_6_A:294 | #2 TURBINE GENERATOR INLET WIND TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
630 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | COOLER SYSTEM #2 | 3316 | DPU_6_A:297 | #2 TURBINE AIR COOLER OUTLET WATER TEMP | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
631 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:333 | #2 TURBINE GENERATOR STATOR CORE TEMP 6 | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
632 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:117 | #2 TURBINE GENERATOR FRONT SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
633 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:153 | #2 TURBINE GENERATOR BACK SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
634 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:438 | #2 GENERATOR ACTIVE POWER | AI | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
635 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:486 | #2 GENERATOR FREQUENCY | AI | Hz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
636 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 3317 | DPU_6_A:444 | #2 GENERATOR POWER FACTOR | AI | pF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
637 | PLTU Belitung 2 | Generator System #2 | GENERATOR BEARING 3 #2 | 3387
638 | PLTU Belitung 2 | Generator System #2 | GENERATOR BEARING 4 #2 | 3385
639 | PLTU Belitung 2 | Generator System #2 | GENERATOR COOLER SYSTEM #2 | 3389
640 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:300 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 1 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
641 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:303 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 2 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
642 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:306 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 3 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
643 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:309 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 4 | AI | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
644 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:312 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 5 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
645 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:315 | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 6 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
646 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:318 | #2 TURBINE GENERATOR STATOR CORE TEMP 1 | AI | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
647 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:321 | #2 TURBINE GENERATOR STATOR CORE TEMP 2 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
648 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:324 | #2 TURBINE GENERATOR STATOR CORE TEMP 3 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
649 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:327 | #2 TURBINE GENERATOR STATOR CORE TEMP 4 | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 120
650 | PLTU Belitung 2 | GENERATOR SYSTEM #2 | GENERATOR EXCITER SET #2 | 3318 | DPU_6_A:330 | #2 TURBINE GENERATOR STATOR CORE TEMP 5 | AI | C | 0 | 400 | 0 | 0 | 0 | 70 | 0 | 80
651 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | AC OIL PUMP #2 | 3319 | DPU_6_A:24 | #2 TURBINE AC LUBE OIL PUMP OUTLET PRE | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
652 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | DC OIL PUMP #2 | 3320 | DPU_6_A:69 | #2 TURBINE DC LUBE OIL PUMP OUTLET PRE | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
653 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | HP OIL PUMP #2 | 3322 | DPU_6_A:159 | #2 TURBINE HP STARTING OIL PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
654 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | LUBRICANT SUPPLY PIPING SYSTEM #2 | 3260 | DPU_6_A:33 | #2 TURBINE LUBE OIL PRE | AI | MPa | 0 | 0.25 | 0.015 | 0.045 | 0.7 | 0.15 | 2 | 0
655 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | MAIN OIL TANK #2 | 3321 | DPU_6_A:87 | #2 TURBINE OIL TANK LEVEL | AI | mm | -200 | 200 | -200 | 0 | -150 | 200 | 0 | 150
656 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2A | 3348 | DPU_6_A:246 | #2 TURBINE OIL COOLER INLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
657 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2A | 3348 | DPU_6_A:252 | #2 TURBINE OIL COOLER OUTLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
658 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2A | 3348 | DPU_6_A:258 | #2 TURBINE OIL COOLER INLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
659 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2A | 3348 | DPU_6_A:264 | #2 TURBINE OIL COOLER OUTLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
660 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2B | 3349 | DPU_6_A:249 | #2 TURBINE OIL COOLER INLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
661 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2B | 3349 | DPU_6_A:255 | #2 TURBINE OIL COOLER OUTLET WATER TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
662 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2B | 3349 | DPU_6_A:261 | #2 TURBINE OIL COOLER INLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
663 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | OIL COOLER SYSTEM #2B | 3349 | DPU_6_A:267 | #2 TURBINE OIL COOLER OUTLET OIL TEMP | AI | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
664 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | STEAM TURBINE MAIN OIL PUMP #2 | 3261 | DPU_6_A:12 | #2 TURBINE MAIN OIL PUMP OUTLET PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0.8 | 0 | 0 | 0
665 | PLTU Belitung 2 | LUBRICATION SUPPLY SYSTEM #2 | STEAM TURBINE MAIN OIL PUMP #2 | 3261 | DPU_6_A:60 | #2 TURBINE MAIN OIL PUMP INTLET PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0.8 | 0 | 0 | 0
666 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #1 | 3323
667 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3325
668 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3324 | DPU_4_A:15 | #2 BOILER MAIN STEAM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
669 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3324 | DPU_4_A:369 | #2 BOILER MAIN STEAM TEMPERATURE | AI | C | 0 | 600 | 0 | 0 | 465 | 490 | 0 | 491
670 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3324 | DPU_4_A:714 | #2 BOILER MAIN STEAM FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
671 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3324 | DPU_6_A:480 | #2 TURBINE MAIN STEAM PRE.BEF ELEC MSV | AI | MPa | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
672 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 3324 | DPU_6_A:336 | #2 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | AI | C | 0 | 600 | 0 | 0 | 455 | 488 | 0 | 0
673 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:3 | #2 TURBINE STARTING OIL PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
674 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:6 | #2 TURBINE SAFETY OIL PRE | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
675 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:516 | #2 TURBINE EXHAUST STEAM PRE | AI | MPa | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
676 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:15 | #2 TURBINE VELOCITY STAGE PRE | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
677 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:54 | #2 TURBINE AST OIL PRE | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
678 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:57 | #2 TURBINE OPC OIL PRE | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
679 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:165 | #2 TURBINE #1 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
680 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:168 | #2 TURBINE #2 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
681 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:171 | #2 TURBINE #3 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
682 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:174 | #2 TURBINE #4 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
683 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:177 | #2 TURBINE #5 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
684 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:180 | #2 TURBINE #6 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
685 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:183 | #2 TURBINE #7 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
686 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:186 | #2 TURBINE #8 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
687 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:189 | #2 TURBINE #9 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
688 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:192 | #2 TURBINE #10 THRUST BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
689 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:195 | #2 TURBINE #1 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
690 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:198 | #2 TURBINE #2 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
691 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:201 | #2 TURBINE #3 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
692 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:204 | #2 TURBINE #4 BEARING TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 110 | 0 | 0
693 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:207 | #2 TURBINE #1 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
694 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:210 | #2 TURBINE #2 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
695 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:477 | #2 TURBINE #3 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
696 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:216 | #2 TURBINE #4 BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
697 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:219 | #2 TURBINE #1 POSITIVE THRUST BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
698 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:222 | #2 TURBINE #1 NEGATIVE THRUST BEARING RETURN OIL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 75 | 0 | 0
699 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:342 | #2 TURBINE CYLINDER WALL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
700 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:345 | #2 TURBINE CYLINDER WALL TEMP | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
701 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:348 | #2 TURBINE EXTRACTION 1 STEAM PRE | AI | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
702 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:102 | #2 TURBINE AXIAL POSITION 1 | AI | mm | -2 | 2 | -0.7 | 0 | -0.6 | 1 | 0 | 1.3
703 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:126 | #2 TURBINE AXIAL POSITION 2 | AI | mm | -2 | 2 | -0.7 | 0 | -0.6 | 1 | 0 | 1.3
704 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:105 | #2 TURBINE STEAM TURBINE SPEED 1 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
705 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:129 | #2 TURBINE STEAM TURBINE SPEED 2 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
706 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:132 | #2 TURBINE STEAM TURBINE SPEED 3 | AI | RPM | 0 | 4000 | 0 | 0 | 0 | 3150 | 0 | 3300
707 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:114 | #2 TURBINE STEAM TURBINE FRONT SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
708 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 3326 | DPU_6_A:150 | #2 TURBINE STEAM TURBINE BACK SHAFT VIBRATION | AI | um | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 80
709 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 TO SEALING STEAM SYSTEM | 3327 | DPU_6_A:45 | #2 TURBINE MAIN STEAM PRE.BEF MSV | AI | MPa | 0 | 10 | 0 | 0 | 4.62 | 5.2 | 0 | 0
710 | PLTU Belitung 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 TO SEALING STEAM SYSTEM | 3327 | DPU_6_A:339 | #2 TURBINE MAIN STEAM TEMP. BEF MSV | AI | C | 0 | 600 | 0 | 0 | 455 | 488 | 0 | 0
711 | PLTU Belitung 2 | Sealing Steam System #2 | MAIN STEAM PIPING SYSTEM #2 (ELECTRIC MSV SYSTEM) | 3345
712 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #2 | 3328 | DPU_6_A:231 | #2 TURBINE CONDENSER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 60 | 80 | 0 | 0
713 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #2 | 3328 | DPU_6_A:234 | #2 TURBINE CONDENSER INLET STEAM TEMP | AI | C | 0 | 400 | 0 | 0 | 60 | 80 | 0 | 0
714 | PLTU Belitung 2 | TURBINE EXTRACTION SYSTEM #2 | STEAM TURBINE EXTRACTION PIPING TO DEAERATOR #2 | 3328 | DPU_5_A:27 | DEAERATOR STEAM PIPELINE PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
715 | PLTU Belitung 2 | Turbine System #2 | EXTRACTION STEAM PIPING FOR HP FEED WATER PIPING #2 | 3391
716 | PLTU Belitung 2 | Turbine System #2 | EXTRACTION STEAM PIPING LP CONDENSATE WATER PIPING #2 | 3393
717 | PLTU Belitung 2 | Turbine System #2 | HP TURBINE #2 | 3369
718 | PLTU Belitung 2 | Turbine System #2 | TURBINE BEARING 1 #2 | 3373
719 | PLTU Belitung 2 | Turbine System #2 | TURBINE BEARING 2 #2 | 3371
720 | PLTU Belitung 2 | Turbine System #2 | TURBINE BEARING THRUST #2 | 3375