## UNIT#1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | A1FT107_A | A1FT107_A |  | #1 SECONDARY AIR FLOW OF #1 BOILER | AI | 0 | 60000 | m3/h | [6 empty] | TOTAL
2 | Manipulated Variable | Secondary Air Flow | A1FT107_B | A1FT107_B |  | #2 SECONDARY AIR FLOW OF #1 BOILER | AI | 0 | 60000 | m3/h
3 | Disturbance Variable | Coal Flow | 1M905 | 1M905 |  | #1 BOILER COAL FLOW | CALC | 0 | 300 | t/h
4 | Disturbance Variable | Load | A1G_Power | A1G_Power |  | #1 GENERATOR ACTIVE POWER | AI | 0 | 20 | MW
5 | Disturbance Variable | Primary Air Flow | A1FT104_A | A1FT104_A |  | #1 PRIMARY AIR FLOW OF #1 BOILER | AI | 0 | 40000 | m3/h | [6 empty] | TOTAL
6 | Disturbance Variable | Primary Air Flow | A1FT104B | A1FT104B |  | #2 PRIMARY AIR FLOW OF #1 BOILER | AI | 0 | 40000 | m3/h
7 | Constrain Variable | Oxygen Sensor | A1AT102 | A1AT102 |  | GAS FLUE INLET O2% OF #1 BOILER | AI | 0 | 21 | %
8 | Constrain Variable | Furnace Pressure | A1PT117A | A1PT117A |  | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa | [6 empty] | AVERAGE
9 | Constrain Variable | Furnace Pressure | A1PT117B | A1PT117B |  | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa
10 | Constrain Variable | Furnace Pressure | A1PT119A | A1PT119A |  | #1 BOILER FURNACE OUTLET PRESSURE | AI | -500 | 500 | Pa | -500 | 0 | -150 | 10 | 0 | 50 | AVERAGE
11 | Constrain Variable | Furnace Pressure | A1PT119B | A1PT119B |  | #1 BOILER FURNACE OUTLET PRESSURE | AI | -500 | 500 | Pa | -500 | 0 | -150 | 10 | 0 | 50
12 | Constrain Variable | Furnace Differential Pressure | A1PdT134A | A1PdT134A |  | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa | [6 empty] | AVERAGE
13 | Constrain Variable | Furnace Differential Pressure | A1PdT134B | A1PdT134B |  | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa
14 | Constrain Variable | Bed Differential Pressure | A1PdT135A | A1PdT135A |  | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | 0 | 16 | KPa | [6 empty] | AVERAGE
15 | Constrain Variable | Bed Differential Pressure | A1PdT135B | A1PdT135B |  | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | 0 | 16 | KPa
16 | Constrain Variable | Bed Temperature | A1TE115A | A1TE115A |  | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
17 | Constrain Variable | Bed Temperature | A1TE115B | A1TE115B |  | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
18 | Constrain Variable | Bed Temperature | A1TE115C | A1TE115C |  | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
19 | Constrain Variable | Bed Temperature | A1TE115D | A1TE115D |  | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
20 | Constrain Variable | Bed Temperature | A1TE116A | A1TE116A |  | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
21 | Constrain Variable | Bed Temperature | A1TE116B | A1TE116B |  | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | 0 | 1200 | °C
22 | Constrain Variable | Bed Temperature | 1TE915 | 1TE915 |  | #1 BOILER BED TEMPERATURE | CALC | 0 | 1200 | °C
23 | Constrain Variable | Furnace Temperature | A1TE118A | A1TE118A |  | #1 BOILER FURNACE OUTLET TEMPERATURE | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
24 | Constrain Variable | Furnace Temperature | A1TE118B | A1TE118B |  | #1 BOILER FURNACE OUTLET TEMPERATURE | TC | 0 | 1200 | °C
25 | Constrain Variable | Stack NOx |  |  |  | N/A
26 | Constrain Variable | Stack CO |  |  |  | N/A
27 | Efficiency Variable | Coal Flow | 1M905 | 1M905 |  | #1 BOILER COAL FLOW | CALC | 0 | 300 | t/h
28 | Efficiency Variable | Main Steam Pressure | A1PT201A | A1PT201A |  | #1 TURBINE MAIN STEAM PRE. BEF ELEC MSV | AI | 0 | 10 | MPa |  |  |  | 5.098
29 | Efficiency Variable | Main Steam Pressure | A1PT105A | A1PT105A |  | #1 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa |  |  | 4.61 | 5.1
30 | Efficiency Variable | Feed Water Pressure | A1PT101 | A1PT101 |  | #1 BOILER UPSTREAM-CONTROL VALVE PRESSURE | AI | 0 | 16 | MPa
31 | Efficiency Variable | Feed Water Pressure | A1PT304 | A1PT304 |  | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | 0 | 20 | MPa
32 | Efficiency Variable | SH Spray Water Pressure | A1PT304 | A1PT304 |  | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | 0 | 20 | MPa
33 | Efficiency Variable | Main Steam Temperature | A1TE101A | A1TE101A |  | #1 BOILER MAIN STEAM TEMPERATURE | TC | 0 | 600 | °C |  |  | 465 | 490 |  | 491
34 | Efficiency Variable | Main Steam Temperature | A1TE201A | A1TE201A |  | #1 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | TC | 0 | 600 | °C |  |  | 400 | 540
35 | Efficiency Variable | Feed Water Temperature | A1TE217 | A1TE217 |  | #1 TURBINE HP HEATER OUTLET WATER TEMP | RTD | 0 | 200 | °C
36 | Efficiency Variable | Feed Water Temperature | A1TE102 | A1TE102 |  | #1 BOILER FEEDWATER TEMPERATURE | RTD | 0 | 200 | °C
37 | Efficiency Variable | SH Spray Temperature | A1TE217 | A1TE217 |  | #1 TURBINE HP HEATER OUTLET WATER TEMP | RTD | 0 | 200 | °C
38 | Efficiency Variable | Main Steam Flow | A1FT101_1 | A1FT101_1 |  | #1 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h
39 | Efficiency Variable | Feed Water Flow | A1FT102_1 | A1FT102_1 |  | #1 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h
40 | Efficiency Variable | SH Spray Water Flow | A1FT103A_1 | A1FT103A_1 |  | #1 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h | [6 empty] | TOTAL
41 | Efficiency Variable | SH Spray Water Flow | A1FT103B_1 | A1FT103B_1 |  | #1 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h
42 | Control Variable | FD Fan Air Flow | S02_E007.MV | S02_E007.MV |  | CONTROL SIGNAL OF #1 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %
43 | Control Variable | FD Fan Air Flow | S02_E008.MV | S02_E008.MV |  | CONTROL SIGNAL OF #1 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %

## UNIT#2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Secondary Air Flow | A2FT107_A | A2FT107_A |  | #1 SECONDARY AIR FLOW OF #2 BOILER | AI | 0 | 60000 | m3/h | [6 empty] | TOTAL
2 | Manipulated Variable | Secondary Air Flow | A2FT107_B | A2FT107_B |  | #2 SECONDARY AIR FLOW OF #2 BOILER | AI | 0 | 60000 | m3/h
3 | Disturbance Variable | Coal Flow | 2M905 | 2M905 |  | #2 BOILER COAL FLOW | CALC | 0 | 300 | t/h
4 | Disturbance Variable | Load | A2G_Power | A2G_Power |  | #2 GENERATOR ACTIVE POWER | AI | 0 | 20 | MW
5 | Disturbance Variable | Primary Air Flow | A2FT104_A | A2FT104_A |  | #1 PRIMARY AIR FLOW OF #2 BOILER | AI | 0 | 40000 | m3/h | [6 empty] | TOTAL
6 | Disturbance Variable | Primary Air Flow | A2FT104_B | A2FT104_B |  | #2 PRIMARY AIR FLOW OF #2 BOILER | AI | 0 | 40000 | m3/h
7 | Constrain Variable | Oxygen Sensor | A2AT102 | A2AT102 |  | GAS FLUE INLET O2% OF #2 BOILER | AI | 0 | 21 | %
8 | Constrain Variable | Furnace Pressure | A2PT117A | A2PT117A |  | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa | [6 empty] | AVERAGE
9 | Constrain Variable | Furnace Pressure | A2PT117B | A2PT117B |  | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | 0 | 3000 | Pa
10 | Constrain Variable | Furnace Pressure | A2PT119A | A2PT119A |  | #2 BOILER FURNACE OUTLET PRESSURE | AI | -500 | 500 | Pa | -500 | 0 | -150 | 10 | 0 | 50 | AVERAGE
11 | Constrain Variable | Furnace Pressure | A2PT119B | A2PT119B |  | #2 BOILER FURNACE OUTLET PRESSURE | AI | -500 | 500 | Pa | -500 | 0 | -150 | 10 | 0 | 50
12 | Constrain Variable | Furnace Pressure | A2PdT134A | A2PdT134A |  | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa | [6 empty] | AVERAGE
13 | Constrain Variable | Furnace Pressure | A2PdT134B | A2PdT134B |  | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | 0 | 2000 | Pa
14 | Constrain Variable | Bed Differential Pressure | A2PdT135A | A2PdT135A |  | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | 0 | 16 | KPa | [6 empty] | AVERAGE
15 | Constrain Variable | Bed Differential Pressure | A2PdT135B | A2PdT135B |  | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | 0 | 16 | KPa
16 | Constrain Variable | Bed Temperature | A2TE115A | A2TE115A |  | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
17 | Constrain Variable | Bed Temperature | A2TE115B | A2TE115B |  | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
18 | Constrain Variable | Bed Temperature | A2TE115C | A2TE115C |  | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
19 | Constrain Variable | Bed Temperature | A2TE115D | A2TE115D |  | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | 0 | 1200 | °C
20 | Constrain Variable | Bed Temperature | A2TE116A | A2TE116A |  | #2 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
21 | Constrain Variable | Bed Temperature | A2TE116B | A2TE116B |  | #2 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | 0 | 1200 | °C
22 | Constrain Variable | Bed Temperature | 2TE915 | 2TE915 |  | #2 BOILER BED TEMPERATURE | CALC | 0 | 1200 | °C
23 | Constrain Variable | Furnace Temperature | A2TE118A | A2TE118A |  | #2 BOILER FURNACE OUTLET TEMPERATURE | TC | 0 | 1200 | °C | [6 empty] | AVERAGE
24 | Constrain Variable | Furnace Temperature | A2TE118B | A2TE118B |  | #2 BOILER FURNACE OUTLET TEMPERATURE | TC | 0 | 1200 | °C
25 | Constrain Variable | Stack NOx |  |  |  | N/A
26 | Constrain Variable | Stack CO |  |  |  | N/A
27 | Efficiency Variable | Coal Flow | 2M905 | 2M905 |  | #2 BOILER COAL FLOW | CALC | 0 | 300 | t/h
28 | Efficiency Variable | Main Steam Pressure | A2PT201A | A2PT201A |  | #2 TURBINE MAIN STEAM PRE. BEF ELEC MSV | AI | 0 | 10 | MPa |  |  |  | 5.098
29 | Efficiency Variable | Main Steam Pressure | A2PT105A | A2PT105A |  | #2 BOILER MAIN STEAM PRESSURE | AI | 0 | 10 | MPa |  |  | 4.61 | 5.1
30 | Efficiency Variable | Feed Water Pressure | A2PT101 | A2PT101 |  | #2 BOILER UPSTREAM-CONTROL VALVE PRESSURE | AI | 0 | 16 | MPa
31 | Efficiency Variable | Feed Water Pressure | A2PT304 | A2PT304 |  | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | 0 | 20 | MPa
32 | Efficiency Variable | SH Spray Water Pressure | A2PT304 | A2PT304 |  | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | 0 | 20 | MPa
33 | Efficiency Variable | Main Steam Temperature | A2TE101A | A2TE101A |  | #2 BOILER MAIN STEAM TEMPERATURE | TC | 0 | 600 | °C |  |  | 465 | 490 |  | 491
34 | Efficiency Variable | Main Steam Temperature | A2TE201A | A2TE201A |  | #2 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | TC | 0 | 600 | °C |  |  | 400 | 540
35 | Efficiency Variable | Feed Water Temperature | A2TE217 | A2TE217 |  | #2 TURBINE HP HEATER OUTLET WATER TEMP | RTD | 0 | 200 | °C
36 | Efficiency Variable | Feed Water Temperature | A2TE102 | A2TE102 |  | #2 BOILER FEEDWATER TEMPERATURE | RTD | 0 | 200 | °C
37 | Efficiency Variable | SH Spray Temperature | A2TE217 | A2TE217 |  | #2 TURBINE HP HEATER OUTLET WATER TEMP | RTD | 0 | 200 | °C
38 | Efficiency Variable | Main Steam Flow | B1FT101_1 | B1FT101_1 |  | #2 BOILER MAIN STEAM FLOW | AI | 0 | 100 | t/h
39 | Efficiency Variable | Feed Water Flow | B1FT102_1 | B1FT102_1 |  | #2 BOILER FEEDWATER FLOW | AI | 0 | 100 | t/h
40 | Efficiency Variable | SH Spray Water Flow | B1FT103A_1 | B1FT103A_1 |  | #2 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h | [6 empty] | TOTAL
41 | Efficiency Variable | SH Spray Water Flow | B1FT103B_1 | B1FT103B_1 |  | #2 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | 0 | 6 | t/h
42 | Control Variable | FD Fan Air Flow | S08_E007.MV | S08_E007.MV |  | CONTROL SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %
43 | Control Variable | FD Fan Air Flow | S08_E008.MV | S08_E008.MV |  | CONTROL SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | 0 | 100 | %

## 2022-09-14 10 15 MariaDB_soketd
NO | UNIT | SYSTEM | EQUIPMENT | f_equipment_id | Tag Name | Description | Tag Type | Tag Unit | Range Lo | Range Hi | L3 | L2 | L1 | H1 | H2 | H3
1 | PLTU Bolok 1 | TURBINE SYSTEM #1 | HP OIL PUMP #1 | 2191 | A1PT220 | #1 TURBINE HP STARTING OIL PUMP OUTLET PRE. | AI | MPa | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
2 | PLTU Bolok 1 | TURBINE SYSTEM #1 | HP OIL PUMP #1 | 2191 | A1M202_A | #1 TURBINE HP STARTING OIL PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
3 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1B | 2190 | A1TE211B | #1 TURBINE OIL COOLER INLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
4 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1B | 2190 | A1TE212B | #1 TURBINE OIL COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
5 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1B | 2190 | A1TE213B | #1 TURBINE OIL COOLER INLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
6 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1B | 2190 | A1TE214B | #1 TURBINE OIL COOLER OUTLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
7 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE GOVERNOR VALVE #1 | 2180 | A1DEH22AB | #1 TURBINE SPC POSITION FEEDBACK | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
8 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1PT108 | #1 BOILER SECONDARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
9 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1PT109A | #1 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
10 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1PT109B | #1 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
11 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1PT123A | #1 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1PT123B | #1 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1TE114A | #1 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
14 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1TE114B | #1 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
15 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1TE125A | #1 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | RTD | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
16 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | SECONDARY AIR PREHEATER SYSTEM #1 | 2156 | A1TE125B | #1 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | RTD | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
17 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | A1FT107_A | #1 SECONDARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
18 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | A1CV102A_F | FEEDBACK SIGNAL OF #1 BOILER #1 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
19 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | A1M103A_A | #1 BOILER #1 SA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
20 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | S02_E007.MV | CONTROL SIGNAL OF #1 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
21 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | A1TE130A | FRONT BEARING TEMP OF #1 BOILER #1 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
22 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN A #1 | 2153 | A1TE130B | BACK BEARING TEMP OF #1 BOILER #1 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
23 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1C | 2146 | A1M105C_A1 | #1 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
24 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1C | 2146 | A1M105C_A2 | #1 BOILER #3 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
25 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1C | 2146 | A1M105CMV | #1 BOILER #3 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
26 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | DRUM SLAG COOLER B #1 | 2140 | A1M106B_A1 | #1 BOILER #2 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
27 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | DRUM SLAG COOLER B #1 | 2140 | A1M106BMV | #1 BOILER #2 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
28 | PLTU Bolok 1 | COOLING SYSTEM #1 | VACUUM PUMP SK-16 #1 | 2275 | A1M211_A | #1 TURBINE VACUUM PUMP SK-6 CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
29 | PLTU Bolok 1 | TURBINE SYSTEM #1 | CONDENSATE WATER FOR EXTRACTION VALVE CONTROL WATER SYSTEM #1 | 2174 | A1PT215A | #1 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
30 | PLTU Bolok 1 | TURBINE SYSTEM #1 | CONDENSATE WATER FOR EXTRACTION VALVE CONTROL WATER SYSTEM #1 | 2174 | A1PT215B | #1 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
31 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 TO SEALING STEAM SYSTEM | 2169 | A1PT214 | #1 TURBINE AVERAGE PRE. TANK PRE. | AI | KPa | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
32 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 TO SEALING STEAM SYSTEM | 2169 | A1CV202_F | FEEDBACK SIGNAL OF #1 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
33 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 TO SEALING STEAM SYSTEM | 2169 | 1CV902 | #1 Diff ctrl and FB turbine GSH press ctrl valve | CALC | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
34 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | HP HEATER #1 | 2167 | A1LT203 | #1 TURBINE HP HEATER LEVEL | AI | mm | 0 | 900 | 0 | 0 | 150 | 900 | 0 | 0
35 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | HP HEATER #1 | 2167 | A1TE215 | #1 TURBINE HP HEATER INLET WATER TEMP | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
36 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | HP HEATER #1 | 2167 | A1TE216 | #1 TURBINE HP HEATER INLET STEAM TEMP | RTD | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
37 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | HP HEATER #1 | 2167 | A1TE217 | #1 TURBINE HP HEATER OUTLET WATER TEMP | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
38 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | HP HEATER #1 | 2167 | 1TE916 | TTD HPH #1 | CALC | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
39 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN B #1 | 2162 | A1CV103B_F | FEEDBACK SIGNAL OF #1 BOILER #2 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
40 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN B #1 | 2162 | A1M101B_A | #1 BOILER #2 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
41 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN B #1 | 2162 | S02_E018.MV | CONTROL SIGNAL OF #1 BOILER #2 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
42 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN B #1 | 2162 | A1TE133A | FRONT BEARING TEMP OF #1 BOILER #2 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
43 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN B #1 | 2162 | A1TE133B | BACK BEARING TEMP OF #1 BOILER #2 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
44 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1PT126A | #1 BOILER #1 INDUCED DRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1PT126B | #1 BOILER #2 INDUCED DRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1FT109 | #1 BOILER INDUCED AIR FLOW | AI | m3/h | 0 | 200000 | 0 | 0 | 0 | 0 | 0 | 0
47 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1CV103A_F | FEEDBACK SIGNAL OF #1 BOILER #1 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
48 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1M101A_A | #1 BOILER #1 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
49 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | S02_E004.MV | CONTROL SIGNAL OF #1 BOILER #1 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
50 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1TE132A | FRONT BEARING TEMP OF #1 BOILER #1 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
51 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | INDUCED DRAFT FAN A #1 | 2161 | A1TE132B | BACK BEARING TEMP OF #1 BOILER #1 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
52 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1B | 2145 | A1M105B_A1 | #1 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
53 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1B | 2145 | A1M105B_A2 | #1 BOILER #2 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
54 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1B | 2145 | A1M105BMV | #1 BOILER #2 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
55 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1A | 2144 | A1M105A_A1 | #1 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
56 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1A | 2144 | A1M105A_A2 | #1 BOILER #1 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
57 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1A | 2144 | A1M105AMV | #1 BOILER #1 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
58 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL FEEDER #1A | 2144 | 1M905 | #1 BOILER COAL FLOW | CALC | t/h | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
59 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1PT122A | #1 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1PT122B | #1 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1AT102 | GAS FLUE INLET O2% OF #1 BOILER | AI | % | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0
62 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1TE102 | #1 BOILER FEEDWATER TEMPERATURE | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
63 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1TE123A | #1 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | TC | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
64 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ECONOMIZER #1 | 2133 | A1TE123B | #1 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | TC | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
65 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR BEARING #1 | 2277
66 | PLTU Bolok 1 | COOLING SYSTEM #1 | COOLING WATER PUMP A #1 - SERVICE PUMP #1A | 2202 | A1PT234 | INDUSTRIAL WATER PUMP OUTLET HEADER PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
67 | PLTU Bolok 1 | COOLING SYSTEM #1 | COOLING WATER PUMP A #1 - SERVICE PUMP #1A | 2202 | A1M209A_A | #1 TURBINE #1 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
68 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | FRONT BEARING GENERATOR #1 | 2197 | A1VB201C | #1 TURBINE GENERATOR FRONT SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
69 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | FRONT BEARING GENERATOR #1 | 2197 | A1TE203M | #1 TURBINE #3 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
70 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | VACUUM PUMP #1B | 2187 | A1M207BB | #1 TURBINE #2 VACUUM PUMP CURRENT INDICATE | AI | A | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
71 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1PT210A | #1 TURBINE CONDENSER VACUUM | AI | KPa | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1PT210B | #1 TURBINE CONDENSER VACUUM | AI | KPa | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1LT201 | #1 TURBINE CONDENSER LEVEL | AI | mm | 0 | 1025 | 0 | -430 | -380 | 380 | 430 | 0
74 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1CV201_F | FEEDBACK SIGNAL OF #1 TURBINE CONDENSER LEVEL CONTROL VALVE 1 | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
75 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | S04_E000.MV | CONTROL SIGNAL OF #1 TURBINE CONDENSER LEVEL CONTROL VALVE 1 | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
76 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1TE208A | #1 TURBINE CONDENSER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
77 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1TE208B | #1 TURBINE CONDENSER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
78 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSER #1 | 2185 | A1TE210 | #1 TURBINE CONDENSATION WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
79 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DRAIN PUMP #1 | 2178 | A1PT306 | DRAIN PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
80 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP B#1 | 2176 | A1PT219B | #1 TURBINE #2 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
81 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP B#1 | 2176 | A1M201B_A | #1 TURBINE #2 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
82 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 2170 | A1PT202 | #1 TURBINE MAIN STEAM PRE. BEF MSV | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
83 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 2170 | A1PT203 | #1 TURBINE STARTING OIL PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
84 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (HYDRAULIC MSV SYSTEM) | 2170 | A1TE202 | #1 TURBINE MAIN STEAM TEMP. BEF MSV | TC | C | 0 | 600 | 0 | 0 | 455 | 480 | 0 | 0
85 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | A1FT107_B | #2 SECONDARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
86 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | A1CV102B_F | FEEDBACK SIGNAL OF #1 BOILER #2 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
87 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | A1M103B_A | #1 BOILER #2 SA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
88 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | S02_E008.MV | CONTROL SIGNAL OF #1 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
89 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | A1TE131A | FRONT BEARING TEMP OF #1 BOILER #2 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
90 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SECONDARY AIR FAN B #1 | 2154 | A1TE131B | BACK BEARING TEMP OF #1 BOILER #2 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
91 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | A1FT104_A | #1 PRIMARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
92 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | A1CV101A_F | FEEDBACK SIGNAL OF #1 BOILER #1 PA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
93 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | A1M102A_A | #1 BOILER #1 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
94 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | S02_E005.MV | CONTROL SIGNAL OF #1 BOILER #1 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
95 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | A1TE128A | FRONT BEARING TEMP OF #1 BOILER #1 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
96 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN A #1 | 2151 | A1TE128B | BACK BEARING TEMP OF #1 BOILER #1 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
97 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | A1PT401 | #1 BOILER FEEDING OIL PRESSURE | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
98 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | A1FT401 | #1 BOILER FEEDING OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
99 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | A1FT402 | #1 BOILER RETURN OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
100 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | S02_E020.MV | CONTROL SIGNAL OF #1 BOILER RETURN OIL FLOW REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
101 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | A1CV401_F | FEEDBACK SIGNAL OF #1 BOILER RETURN OIL FLOW REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
102 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | IGNITION PIPING SYSTEM #1 | 2150 | 1FT901 | #1 BOILER FEEDING-RETURN DIFF. OIL FLOW | CALC | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
103 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE MAIN OIL PUMP #1 | 2194 | A1PT204 | #1 TURBINE SAFETY OIL PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
104 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE MAIN OIL PUMP #1 | 2194 | A1PT206 | #1 TURBINE MAIN OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
105 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE MAIN OIL PUMP #1 | 2194 | A1PT207A | #1 TURBINE MAIN OIL PUMP INLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
106 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1PT303B | #2 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
107 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1M301B_A | #1 TURBINE #2 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
108 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1TE305A | FRONT BEARING TEMP OF #2 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
109 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1TE305B | BACK BEARING TEMP OF #2 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
110 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1TE306A | MOTOR STATOR TEMP 1 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
111 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1TE306B | MOTOR STATOR TEMP 2 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
112 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP B #1 | 2165 | A1TE306C | MOTOR STATOR TEMP 3 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
113 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RETURN FAN B #1 | 2159 | A1M104B_A | #1 BOILER #2 RETURN FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
114 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | A1FT104B | #2 PRIMARY AIR FLOW OF #1 BOILER | AI | m3/h | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
115 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | A1CV101B_F | FEEDBACK SIGNAL OF #1 BOILER #2 PA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
116 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | A1M102B_A | #1 BOILER #2 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
117 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | S02_E006.MV | CONTROL SIGNAL OF #1 BOILER #2 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
118 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | A1TE129A | FRONT BEARING TEMP OF #1 BOILER #2 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
119 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | PRIMARY AIR FAN B #1 | 2152 | A1TE129B | BACK BEARING TEMP OF #1 BOILER #2 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
120 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2148 | A1PT110 | #1 BOILER LEFT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
121 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2148 | A1FT10_5 | #1 BOILER AIR FLOW OF LEFT WIND BOX | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
122 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2148 | A1TE112 | #1 BOILER LEFT WIND BOX TEMPERATURE | TC | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
123 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT115 | #1 BOILER RIGHT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
124 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT116 | #1 BOILER RIGHT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
125 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT130 | THE LOWER PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
126 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT131 | THE FEEDING BACK PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
127 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT132 | THE MIDDLE PRESSURE OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
128 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PT133B | #1 BOILER RIGHT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PdT138 | THE FEEDING BACK DP OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
130 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1PdT139 | THE LOOSE DP OF #1 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
131 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1TE120 | #1 BOILER RIGHT CYCLONE REVERT TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
132 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2142 | A1TE127B | #1 BOILER SEPARATOR INLET GAS TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
133 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT113 | #1 BOILER LEFT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
134 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT114 | #1 BOILER LEFT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
135 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT127 | THE LOWER PRESSURE OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
136 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT128 | THE FEEDING BACK PRESSURE OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
137 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT129 | THE MIDDLE PRESSURE OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
138 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PT133A | #1 BOILER LEFT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PdT136 | THE FEEDING BACK DP OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
140 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1PdT137 | THE LOOSE DP OF #1 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
141 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1TE119 | #1 BOILER LEFT CYCLONE REVERT TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
142 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #1 | 2141 | A1TE127A | #1 BOILER SEPARATOR INLET GAS TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
143 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | DRUM SLAG COOLER A #1 | 2139 | A1M106A_A1 | #1 BOILER #1 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
144 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | DRUM SLAG COOLER A #1 | 2139 | A1M106AMV | #1 BOILER #1 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
145 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR COOLING #1 | 2279
146 | PLTU Bolok 1 | COOLING SYSTEM #1 | PIPE PRESSURE PUMP A #1 (BOOSTER PUMP) | 2204 | A1M210A_A | #1 TURBINE #1 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
147 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1PT501A | #1 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
148 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1PT502 | #1,2 CIRCULATING WATER PUMP OUTLET MAIN PIPE PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
149 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1FT501 | #1,2 CIRCULATING WATER PUMP OUTLET MAIN PIPE FLOW | AI | t/h | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0
150 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1M501A_A | #1 TURBINE #1 CIRCULATING WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
151 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1TE501A | FRONT BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
152 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1TE501B | BACK BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
153 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1TE502A | MOTOR STATOR TEMP 1 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
154 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1TE502B | MOTOR STATOR TEMP 2 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
155 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1A | 2200 | A1TE502C | MOTOR STATOR TEMP 3 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
156 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1PT223 | #1 TURBINE BALL CIRCULATING PUMP OUTLET PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
157 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1TE207A | #1 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
158 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1TE207B | #1 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
159 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1TE209A | #1 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
160 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1TE209B | #1 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
161 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | A1TE223 | #1 TURBINE AIR COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 40 | 0 | 0
162 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | 1TE909A | #1 DIFF Temp CW A | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
163 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | 1TE909B | #1 DIFF Temp CW B | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
164 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | 1TE909 | Average CW inlet temp #1 | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
165 | PLTU Bolok 1 | COOLING SYSTEM #1 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #1 | 2199 | 1TE907 | Average CW outlet temp #1 | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
166 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1PT212A | #1 TURBINE LUBE OIL PRE. | AI | MPa | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
167 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204A | #1 TURBINE #1 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
168 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204B | #1 TURBINE #2 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
169 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204C | #1 TURBINE #3 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
170 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204D | #1 TURBINE #4 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
171 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204E | #1 TURBINE #1 POSITIVE THRUST BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
172 | PLTU Bolok 1 | TURBINE SYSTEM #1 | LUBRYCANT SUPPLY PIPING SYSTEM #1 | 2188 | A1TE204F | #1 TURBINE #1 NEGATIVE THRUST BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
173 | PLTU Bolok 1 | TURBINE SYSTEM #1 | AST SOLENOID VALVE FOR STEAM TURBINE NO.1 #1 | 2181 | A1PT217 | #1 TURBINE AST OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
174 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP A #1 | 2175 | A1PT219A | #1 TURBINE #1 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
175 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP A #1 | 2175 | A1FT202_1 | #1 TURBINE CONDENSATION WATER FLOW | AI | t/h | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0
176 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | CONDENSATE PUMP A #1 | 2175 | A1M201A_A | #1 TURBINE #1 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
177 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | EXTRACTION PIPING OF GLAND STEAM HEATER SYSTEM #1 | 2173 | A1PT213 | #1 TURBINE EXTRACTION STM PRE. OF GLAND STM HEATER | AI | KPa | -100 | 150 | 0 | 0 | 0 | 0 | 0 | 0
178 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1PT301 | DEAERATOR PRESSURE | AI | MPa | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
179 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1PT305 | DEAERATOR STEAM PIPELINE PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
180 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1LT301 | DEAERATOR LEVEL | AI | mm | 0 | 2000 | 0 | 0 | 900 | 2021 | 0 | 0
181 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1LT302 | DEAERATOR LEVEL | AI | mm | 0 | 2000 | 0 | 0 | 900 | 2021 | 0 | 0
182 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1CV301_F | FEEDBACK SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
183 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1CV302_F | FEEDBACK SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
184 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | S04_E002.MV | CONTROL SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
185 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | S04_E005.MV | CONTROL SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
186 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1TE301 | DEAERATOR TEMPERATURE | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
187 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | DAERATOR TANK #1 | 2163 | A1TE302 | DEAERATOR STEAM PIPELINE TEMPERATURE | RTD | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
188 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL BUNKER #1 | 2143 | A1LT104A | #1 BOILER #1 COAL BUNKER LEVEL | AI | m | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0
189 | PLTU Bolok 1 | COAL FEEDER SYSTEM #1 | COAL BUNKER #1 | 2143 | A1LT104B | #1 BOILER #2 COAL BUNKER LEVEL | AI | m | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0
190 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | REAR BEARING GENERATOR #1 | 2198 | A1VB201D | #1 TURBINE GENERATOR BACK SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
191 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | REAR BEARING GENERATOR #1 | 2198 | A1VB201Y4 | #1 VIBRASI_TUR_Y4 | AI | ?m | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0
192 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | REAR BEARING GENERATOR #1 | 2198 | A1VB201X4 | #1 VIBRASI_TUR_X4 | AI | ?m | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0
193 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | REAR BEARING GENERATOR #1 | 2198 | A1TE203N | #1 TURBINE #4 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
194 | PLTU Bolok 1 | TURBINE SYSTEM #1 | DC OIL PUMP #1 | 2192 | A1PT222 | #1 TURBINE DC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
195 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (ELECTRIC MSV SYSTEM) | 2168 | A1PT201A | #1 TURBINE MAIN STEAM PRE. BEF ELEC MSV | AI | MPa | 0 | 10 | 0 | 0 | 0 | 5.098 | 0 | 0
196 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | MAIN STEAM PIPING SYSTEM #1 (ELECTRIC MSV SYSTEM) | 2168 | A1TE201A | #1 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | TC | C | 0 | 600 | 0 | 0 | 400 | 540 | 0 | 0
197 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1PT302 | LP FEED WATER PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
198 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1PT303A | #1 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
199 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1PT304 | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
200 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1M301A_A | #1 TURBINE #1 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
201 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1TE303A | FRONT BEARING TEMP OF #1 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
202 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1TE303B | BACK BEARING TEMP OF #1 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
203 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1TE304A | MOTOR STATOR TEMP 1 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
204 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1TE304B | MOTOR STATOR TEMP 2 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
205 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP A #1 | 2164 | A1TE304C | MOTOR STATOR TEMP 3 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
206 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT106 | #1 BOILER PRIMARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
207 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT107A | #1 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
208 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT107B | #1 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
209 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT124A | #1 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT124B | #1 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT125A | BOILER OUTLET GAS PRESSURE OF #1 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1PT125B | BOILER OUTLET GAS PRESSURE OF #1 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1AT101 | BOILER OUTLET GAS O2% OF #1 BOILER | AI | % | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0
214 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE111A | #1 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
215 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE111B | #1 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
216 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE124A | #1 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
217 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE124B | #1 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
218 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE126A | BOILER OUTLET GAS TEMPERATURE OF #1 BOILER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
219 | PLTU Bolok 1 | FLUE GAS SYSTEM #1 | PRIMARY AIR PREHEATER SYSTEM #1 | 2155 | A1TE126B | BOILER OUTLET GAS TEMPERATURE OF #1 BOILER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
220 | PLTU Bolok 1 | COOLING SYSTEM #1 | COOLING WATER PUMP B #1 - SERVICE PUMP #1B | 2203 | A1M209B_A | #1 TURBINE #2 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
221 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1G_Power | #1 GENERATOR ACTIVE POWER | AI | MW | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
222 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1G_Freq | #1 GENERATOR FREQUENCY | AI | Hz | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
223 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1G_Factor | #1 GENERATORPOWER FACTOR | AI | pF | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
224 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE221A | #1 TURBINE GENERATOR OUTLET WIND TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 40 | 0 | 0
225 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE221B | #1 TURBINE GENERATOR OUTLET WIND TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 40 | 0 | 0
226 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE222 | #1 TURBINE GENERATOR INLET WIND TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
227 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224A | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
228 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224B | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
229 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224C | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 3 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
230 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224D | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 4 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
231 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224E | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 5 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
232 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE224F | #1 TURBINE GENERATOR STATOR WINDINGS TEMP 6 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
233 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225A | #1 TURBINE GENERATOR STATOR CORE TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
234 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225B | #1 TURBINE GENERATOR STATOR CORE TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
235 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225C | #1 TURBINE GENERATOR STATOR CORE TEMP 3 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
236 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225D | #1 TURBINE GENERATOR STATOR CORE TEMP 4 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
237 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225E | #1 TURBINE GENERATOR STATOR CORE TEMP 5 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
238 | PLTU Bolok 1 | GENERATOR SYSTEM #1 | GENERATOR #1 | 2196 | A1TE225F | #1 TURBINE GENERATOR STATOR CORE TEMP 6 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
239 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1A | 2189 | A1TE211A | #1 TURBINE OIL COOLER INLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
240 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1A | 2189 | A1TE212A | #1 TURBINE OIL COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
241 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1A | 2189 | A1TE213A | #1 TURBINE OIL COOLER INLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
242 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OIL COOLER #1A | 2189 | A1TE214A | #1 TURBINE OIL COOLER OUTLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
243 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | VACUUM PUMP #1A | 2186 | A1PT224 | #1 TURBINE VACUUM PUMP INLET PRE. | AI | KPa | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | VACUUM PUMP #1A | 2186 | A1M207AA | #1 TURBINE #1 VACUUM PUMP CURRENT INDICATE | AI | A | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
245 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.2 #1 | 2184 | A1VB201B | #1 TURBINE STEAM TURBINE BACK SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
246 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.2 #1 | 2184 | A1TE203L | #1 TURBINE #2 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
247 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1VB201A | #1 TURBINE STEAM TURBINE FRONT SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
248 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203A | #1 TURBINE #1 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
249 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203B | #1 TURBINE #2 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
250 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203C | #1 TURBINE #3 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
251 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203D | #1 TURBINE #4 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
252 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203E | #1 TURBINE #5 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
253 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203F | #1 TURBINE #6 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
254 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203G | #1 TURBINE #7 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
255 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203H | #1 TURBINE #8 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
256 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203I | #1 TURBINE #9 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
257 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203J | #1 TURBINE #10 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
258 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE BEARING NO.1 #1 | 2183 | A1TE203K | #1 TURBINE #1 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
259 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 2171 | A1PT105A | #1 BOILER MAIN STEAM PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
260 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 2171 | A1FT101_1 | #1 BOILER MAIN STEAM FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
261 | PLTU Bolok 1 | MAIN STEAM SYSTEM #1 | BOILER MAIN STEAM PIPING SYSTEM #1 | 2171 | A1TE101A | #1 BOILER MAIN STEAM TEMPERATURE | TC | C | 0 | 600 | 600 | 0 | 465 | 490 | 0 | 491
262 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RETURN FAN A #1 | 2157 | A1PT112 | #1 BOILER REFEED AIR FAN OUTLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
263 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RETURN FAN A #1 | 2157 | A1FT108A | #1 BOILER AIR FLOW OF LEFT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
264 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RETURN FAN A #1 | 2157 | A1FT108B | #1 BOILER AIR FLOW OF RIGHT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
265 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | RETURN FAN A #1 | 2157 | A1M104A_A | #1 BOILER #1 RETURN FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
266 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT117A | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
267 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT117B | UPPER PRESSURE OF #1 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
268 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT118A | #1 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
269 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT118B | #1 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | -1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
270 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT119A | #1 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -150 | 10 | 0 | 50
271 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PT119B | #1 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -150 | 10 | 0 | 50
272 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PdT134A | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
273 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PdT134B | #1 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
274 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PdT135A | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
275 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1PdT135B | #1 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
276 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE115A | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
277 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE115B | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
278 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE115C | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
279 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE115D | #1 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
280 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE116A | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
281 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE116B | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
282 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE117A | #1 BOILER MIDDLE FURNACE TEMPERATURE | TC | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
283 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE117B | #1 BOILER MIDDLE FURNACE TEMPERATURE | TC | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
284 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE118A | #1 BOILER FURNACE OUTLET TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
285 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | A1TE118B | #1 BOILER FURNACE OUTLET TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
286 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | FURNACE #1 | 2147 | 1TE915 | #1 BOILER BED TEMPERATURE | CALC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
287 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LOW TEMPERATURE SUPERHEATER SYSTEM #1 | 2138 | A1PT121A | #1 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LOW TEMPERATURE SUPERHEATER SYSTEM #1 | 2138 | A1PT121B | #1 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LOW TEMPERATURE SUPERHEATER SYSTEM #1 | 2138 | A1TE122A | #1 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | TC | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
290 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | LOW TEMPERATURE SUPERHEATER SYSTEM #1 | 2138 | A1TE122B | #1 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | TC | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
291 | PLTU Bolok 1 | COOLING SYSTEM #1 | PIPE PRESSURE PUMP B #1 (BOOSTER PUMP) | 2205 | A1M210B_A | #1 TURBINE #2 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
292 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1PT501B | #2 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
293 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1M501B_A | #1 TURBINE #2 CIRCULATING WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
294 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1TE503A | FRONT BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
295 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1TE503B | BACK BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
296 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1TE504A | MOTOR STATOR TEMP 1 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
297 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1TE504B | MOTOR STATOR TEMP 2 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
298 | PLTU Bolok 1 | COOLING SYSTEM #1 | CWP PUMP #1B | 2201 | A1TE504C | MOTOR STATOR TEMP 3 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
299 | PLTU Bolok 1 | TURBINE SYSTEM #1 | MAIN OIL TANK #1 | 2195 | A1LT204 | #1 TURBINE OIL TANK LEVEL | AI | mm | -200 | 200 | 0 | 0 | 0 | 0 | 0 | 0
300 | PLTU Bolok 1 | TURBINE SYSTEM #1 | AC OIL PUMP #1 | 2193 | A1PT221 | #1 TURBINE AC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
301 | PLTU Bolok 1 | TURBINE SYSTEM #1 | OPC SOLENOID VALVE FOR STEAM TURBINE NO.1 #1 | 2182 | A1PT218 | #1 TURBINE OPC OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
302 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1PT205 | #1 TURBINE EXHAUST STEAM PRE. | AI | MPa | -0.1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0
303 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1PT208 | #1 TURBINE VELOCITY STAGE PRE. | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
304 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1RP201A | #1 TURBINE AXIAL POSITION 1 | AI | mm | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
305 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1RP201B | #1 TURBINE AXIAL POSITION 2 | AI | mm | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
306 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1SD201A | #1 TURBINE STEAM TURBINE SPEED 1 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
307 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1SD201B | #1 TURBINE STEAM TURBINE SPEED 2 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
308 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1SD201C | #1 TURBINE STEAM TURBINE SPEED 3 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
309 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1HE201A | #1 TURBINE STEAM TURBINE HEAT EXPANSION 1 | AI | mm | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
310 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1HE201B | #1 TURBINE STEAM TURBINE HEAT EXPANSION 2 | AI | mm | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
311 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1DE201A_1 | #1 TURBINE STEAM TURBINE DIFFERENTIAL EXPANSION 1 | AI | mm | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0
312 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1DE201B_1 | #1 TURBINE STEAM TURBINE DIFFERENTIAL EXPANSION 2 | AI | mm | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0
313 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1TE205A | #1 TURBINE CYLINDER WALL TEMP | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
314 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | A1TE205B | #1 TURBINE CYLINDER WALL TEMP | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
315 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | 1SD901 | #1 STEAM TURBINE SPEED OUTPUT | CALC | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
316 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE SYSTEM #1 | 2179 | 1TE905 | #1 TURBINE ST METAL TEMPERATURE | CALC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
317 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | A1PT216 | #1 TURBINE LP HEATER INLET STEAM PRE. | AI | MPa | -0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
318 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | A1TE218 | #1 TURBINE LP HEATER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
319 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | A1TE219 | #1 TURBINE LP HEATER INLET WATER TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
320 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | A1TE220 | #1 TURBINE LP HEATER OUTLET WATER TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
321 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | 1TE920 | Diff temp LPH #1 | CALC | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
322 | PLTU Bolok 1 | CONDENSATE SYSTEM #1 | LP HEATER #1 | 2177 | 1TE919 | TTD LPH #1 | CALC | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
323 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #1 | 2172 | A1PT209 | #1 TURBINE EXTRACTION STEAM PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
324 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #1 | 2172 | A1FT201_1 | #1 TURBINE EXTRACTION 1 STEAM FLOW | AI | t/h | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
325 | PLTU Bolok 1 | TURBINE SYSTEM #1 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #1 | 2172 | A1TE206 | #1 TURBINE EXTRACTION 1 STEAM TEMP | TC | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
326 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1PT303C | #3 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
327 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1M301C_A | #1 TURBINE #3 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
328 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1TE307A | FRONT BEARING TEMP OF #3 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
329 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1TE307B | BACK BEARING TEMP OF #3 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
330 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1TE308A | MOTOR STATOR TEMP 1 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
331 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1TE308B | MOTOR STATOR TEMP 2 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
332 | PLTU Bolok 1 | FEED WATER SYSTEM #1 | BOILER FEED WATER PUMP C #1 | 2166 | A1TE308C | MOTOR STATOR TEMP 3 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
333 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2149 | A1PT111 | #1 BOILER RIGHT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
334 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2149 | A1FT10_6 | #1 BOILER AIR FLOW OF RIGHT WIND BOX | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
335 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | WINDBOX #1 | 2149 | A1TE113 | #1 BOILER RIGHT WIND BOX TEMPERATURE | TC | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
336 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1PT104 | #1 BOILER SUPERHEATER OUTLET HEADER PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
337 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1PT120A | #1 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1PT120B | #1 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE106A | #1 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
340 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE106B | #1 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
341 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE107 | #1 BOILER SUPERHEATER INTERMEDIATE HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
342 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE108 | #1 BOILER SUPERHEATER OUTLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
343 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE121A | #1 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
344 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | HIGH TEMPERATURE SUPERHEATER #1 | 2137 | A1TE121B | #1 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
345 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1FT103A_1 | #1 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
346 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1FT103B_1 | #1 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
347 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1CV106A_F | FEEDBACK SIGNAL OF #1 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
348 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1CV106B_F | FEEDBACK SIGNAL OF #1 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
349 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | S02_E015.MV | CONTROL SIGNAL OF #1 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
350 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | S02_E017.MV | CONTROL SIGNAL OF #1 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
351 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1TE104 | #1 BOILER FRONT ATTEMPERATOR TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
352 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | ATTEMPERATOR SUPERHEATER #1 | 2136 | A1TE105 | #1 BOILER BACK ATTEMPERATOR TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
353 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | SWING PIPE SUPERHEATER SYSTEM #1 | 2135 | A1TE103 | #1 BOILER SWING PIPE INLET HEADER TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
354 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1PT101 | #1 BOILER UPSTREAM-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
355 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1PT102 | #1 BOILER DOWNSTREAM-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
356 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1PT103A | #1 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
357 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1PT103B | #1 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
358 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1LT101A_1 | #1 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
359 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1LT101B_1 | #1 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
360 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1FT102_1 | #1 BOILER FEEDWATER FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
361 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1CV104_F | FEEDBACK SIGNAL OF #1 BOILER MAIN FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
362 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1CV105_F | FEEDBACK SIGNAL OF #1 BOILER SUBSIDIARY FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
363 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1CV104MV | CONTROL SIGNAL OF #1 BOILER MAIN FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
364 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1CV105MV | CONTROL SIGNAL OF #1 BOILER SUBSIDIARY FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
365 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1TE134A | UPPER #1 STEAM DRUM TEMPERATURE | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
366 | PLTU Bolok 1 | BOILER FURNACE SYSTEM #1 | STEAM DRUM #1 | 2134 | A1TE134B | LOWER #1 STEAM DRUM TEMPERATURE | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
367 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | VACUUM PUMP #2B | 2256 | A2C207BB | #2 VACUUM PUMP B AMPERE INDICATION | AI | A | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
368 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.2 #2 | 2253 | A2VB201B | #2 TURBINE STEAM TURBINE BACK SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
369 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.2 #2 | 2253 | A2TE203L | #2 TURBINE #2 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
370 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.2 #2 | 2253 | A2VB201Y2 | #2 STEAM TURBINE BACK SHAFT DE VIBRATION Y DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
371 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.2 #2 | 2253 | A2VB201X2 | #2 STEAM TURBINE BACK SHAFT DE VIBRATION X DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
372 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.2 #2 | 2253 | A2VB201X4 | #2 GENERATOR BACK SHAFT NDE VIBRATION X DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
373 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DRAIN PUMP #2 | 2247 | A2PT306 | DRAIN PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
374 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2PT301 | DEAERATOR PRESSURE | AI | MPa | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
375 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2PT305 | DEAERATOR STEAM PIPELINE PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
376 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2LT301 | DEAERATOR LEVEL | AI | mm | 0 | 2000 | 0 | 0 | 900 | 2021 | 0 | 0
377 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2LT302 | DEAERATOR LEVEL | AI | mm | 0 | 2000 | 0 | 0 | 900 | 2021 | 0 | 0
378 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2CV301_F | FEEDBACK SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
379 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2CV302_F | FEEDBACK SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
380 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | S10_E002.MV | CONTROL SIGNAL OF DEAERATOR PRE. REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
381 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | S10_E003.MV | CONTROL SIGNAL OF DEAERATOR LEVEL REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
382 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2TE301 | DEAERATOR TEMPERATURE | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
383 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | DAERATOR TANK #2 | 2232 | A2TE302 | DEAERATOR STEAM PIPELINE TEMPERATURE | RTD | C | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
384 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | A2PT401 | #2 BOILER FEEDING OIL PRESSURE | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
385 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | A2FT401 | #2 BOILER FEEDING OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
386 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | A2FT402 | #2 BOILER RETURN OIL FLOW | AI | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
387 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | A2CV401_F | FEEDBACK SIGNAL OF #2 BOILER RETURN OIL FLOW REGULATOR VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
388 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | S08_E020.MV | CONTROL SIGNAL OF #2 BOILER RETURN OIL FLOW REGULATOR VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
389 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | IGNITION PIPING SYSTEM #2 | 2223 | 2FT901 | #2 BOILER FEEDING-RETURN DIFF. OIL FLOW | CALC | m3/h | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
390 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT117A | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
391 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT117B | UPPER PRESSURE OF #2 BOILER DENSE-PHASE BED | AI | Pa | 0 | 3000 | 0 | 0 | 0 | 0 | 0 | 0
392 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT118A | #2 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
393 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT118B | #2 BOILER MIDDLE FURNACE PRESSURE | AI | Pa | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
394 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT119A | #2 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -500 | 500 | -500 | 0 | -150 | 10 | 0 | 50
395 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PT119B | #2 BOILER FURNACE OUTLET PRESSURE | AI | Pa | -1000 | 1000 | -500 | 0 | -150 | 10 | 0 | 50
396 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PdT134A | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
397 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PdT134B | #2 BOILER FURNACE DIFFERENTIAL PRESSURE | AI | Pa | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0
398 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PdT135A | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
399 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2PdT135B | #2 BOILER BED OF MATERIAL DIFFERENTIAL PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
400 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE115A | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
401 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE115B | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
402 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE115C | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
403 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE115D | #2 BOILER BED OF MATERIAL TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
404 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE116A | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
405 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE116B | #1 BOILELR UPPER TEMPERATURE OF BOILING BED | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
406 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE117A | #2 BOILER MIDDLE FURNACE TEMPERATURE | TC | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
407 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE117B | #2 BOILER MIDDLE FURNACE TEMPERATURE | TC | C | 0 | 1200 | 600 | 0 | 700 | 900 | 0 | 1000
408 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE118A | #2 BOILER FURNACE OUTLET TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
409 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | A2TE118B | #2 BOILER FURNACE OUTLET TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
410 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | FURNACE #2 | 2220 | 2TE915 | #2 BOILER BED TEMPERATURE | CALC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
411 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LOW TEMPERATURE SUPERHEATER SYSTEM #2 | 2211 | A2PT121A | #2 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LOW TEMPERATURE SUPERHEATER SYSTEM #2 | 2211 | A2PT121B | #2 BOILER GAS PRE. BEFORE LOW TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
413 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LOW TEMPERATURE SUPERHEATER SYSTEM #2 | 2211 | A2TE122A | #2 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | TC | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
414 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LOW TEMPERATURE SUPERHEATER SYSTEM #2 | 2211 | A2TE122B | #2 BOILER GAS TEMP BEFORE LOW TEMP SUPERHEATER | TC | C | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
415 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR COOLING #2 | 2280
416 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR BEARING #2 | 2278
417 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2PT501B | #2 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
418 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2M501B_A | #2 TURBINE #2 CIRCULATING WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
419 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2TE503A | FRONT BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
420 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2TE503B | BACK BEARING TEMP OF #2 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
421 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2TE504A | MOTOR STATOR TEMP 1 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
422 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2TE504B | MOTOR STATOR TEMP 2 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
423 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2B | 2270 | A2TE504C | MOTOR STATOR TEMP 3 OF #2 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
424 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE MAIN OIL PUMP #2 | 2263 | A2PT204 | #2 TURBINE SAFETY OIL PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
425 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE MAIN OIL PUMP #2 | 2263 | A2PT206 | #2 TURBINE MAIN OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
426 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE MAIN OIL PUMP #2 | 2263 | A2PT207A | #2 TURBINE MAIN OIL PUMP INLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
427 | PLTU Bolok 2 | TURBINE SYSTEM #2 | DC OIL PUMP #2 | 2261 | A2PT222 | #2 TURBINE DC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
428 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2PT210A | #2 TURBINE CONDENSER VACUUM | AI | KPa | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
429 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2PT210B | #2 TURBINE CONDENSER VACUUM | AI | KPa | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2LT201 | #2 TURBINE CONDENSER LEVEL | AI | mm | 0 | 1025 | 0 | -430 | -380 | 380 | 430 | 0
431 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2CV201_F | FEEDBACK SIGNAL OF #2 TURBINE CONDENSER LEVEL CONTROL VALVE 1 | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
432 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | S10_E000.MV | CONTROL SIGNAL OF #2 TURBINE CONDENSER LEVEL CONTROL VALVE 1 | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
433 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2TE208A | #2 TURBINE CONDENSER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
434 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2TE208B | #2 TURBINE CONDENSER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
435 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSER #2 | 2254 | A2TE210 | #2 TURBINE CONDENSATION WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
436 | PLTU Bolok 2 | TURBINE SYSTEM #2 | AST SOLENOID VALVE FOR STEAM TURBINE NO.1 #2 | 2250 | A2PT217 | #2 TURBINE AST OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
437 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #2 | 2241 | A2PT209 | #2 TURBINE EXTRACTION STEAM PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
438 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #2 | 2241 | A2FT201_1 | #2 TURBINE EXTRACTION 1 STEAM FLOW | AI | t/h | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
439 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE EXTRACTION TO HP HEATER SYSTEM #2 | 2241 | A2TE206 | #2 TURBINE EXTRACTION 1 STEAM TEMP | TC | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
440 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | A2FT104_B | #2 PRIMARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
441 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | A2CV101B_F | FEEDBACK SIGNAL OF #2 BOILER #2 PA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
442 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | A2M102B_A | #2 BOILER #2 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
443 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | S08_E006.MV | CONTROL SIGNAL OF #2 BOILER #2 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
444 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | A2TE129A | FRONT BEARING TEMP OF #2 BOILER #2 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
445 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN B #2 | 2225 | A2TE129B | BACK BEARING TEMP OF #2 BOILER #2 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
446 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SLAG COOLER A #2 | 2212 | A2M106A_A1 | #2 BOILER #1 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
447 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SLAG COOLER A #2 | 2212 | B1M106AMV | #2 BOILER #1 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
448 | PLTU Bolok 2 | COOLING SYSTEM #2 | VACUUM PUMP SK-16 #2 | 2276 | A2M211_A | #2 TURBINE VACUUM PUMP SK-6 CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
449 | PLTU Bolok 2 | TURBINE SYSTEM #2 | MAIN OIL TANK #2 | 2264 | A2LT204 | #2 TURBINE OIL TANK LEVEL | AI | mm | -200 | 200 | 0 | 0 | 0 | 0 | 0 | 0
450 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2VB201A | #2 TURBINE STEAM TURBINE FRONT SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
451 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203A | #2 TURBINE #1 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
452 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203B | #2 TURBINE #2 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
453 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203C | #2 TURBINE #3 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
454 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203D | #2 TURBINE #4 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
455 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203E | #2 TURBINE #5 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
456 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203F | #2 TURBINE #6 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
457 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203G | #2 TURBINE #7 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
458 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203H | #2 TURBINE #8 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
459 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203I | #2 TURBINE #9 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
460 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203J | #2 TURBINE #10 THRUST BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
461 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2TE203K | #2 TURBINE #1 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
462 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2VB201Y1 | #2 STEAM TURBINE FRONT SHAFT NDE VIBRATION Y DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
463 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2VB201Y3 | #2 STEAM TURBINE FRONT SHAFT VIBRATION Y DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
464 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2VB201X1 | #2 STEAM TURBINE FRONT SHAFT NDE VIBRATION X DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
465 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE BEARING NO.1 #2 | 2252 | A2VB201X3 | #2 STEAM TURBINE FRONT SHAFT VIBRATION X DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
466 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OPC SOLENOID VALVE FOR STEAM TURBINE NO.1 #2 | 2251 | A2PT218 | #2 TURBINE OPC OIL PRE. | AI | MPa | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
467 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE GOVERNOR VALVE #2 | 2249 | A2DEH22AB | #2 TURBINE SPC POSITION FEEDBACK | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
468 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP A #2 | 2244 | A2PT219A | #2 TURBINE #1 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
469 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP A #2 | 2244 | A2FT202_1 | #2 TURBINE CONDENSATION WATER FLOW | AI | t/h | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0
470 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP A #2 | 2244 | A2M201A_A | #2 TURBINE #1 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
471 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 2240 | A2PT105A | #2 BOILER MAIN STEAM PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
472 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 2240 | B1FT101_1 | #2 BOILER MAIN STEAM FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
473 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | BOILER MAIN STEAM PIPING SYSTEM #2 | 2240 | A2TE101A | #2 BOILER MAIN STEAM TEMPERATURE | TC | C | 0 | 600 | 600 | 0 | 465 | 490 | 0 | 491
474 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2PT303B | #2 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
475 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2M301B_A | #2 TURBINE #2 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
476 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2TE305A | FRONT BEARING TEMP OF #2 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
477 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2TE305B | BACK BEARING TEMP OF #2 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
478 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2TE306A | MOTOR STATOR TEMP 1 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
479 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2TE306B | MOTOR STATOR TEMP 2 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
480 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP B #2 | 2234 | A2TE306C | MOTOR STATOR TEMP 3 OF #2 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
481 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2PT302 | LP FEED WATER PRESSURE | AI | MPa | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
482 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2PT303A | #1 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
483 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2PT304 | FEED WATER PUMP OUTLET MAIN-PIPE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
484 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2M301A_A | #2 TURBINE #1 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
485 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2TE303A | FRONT BEARING TEMP OF #1 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
486 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2TE303B | BACK BEARING TEMP OF #1 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
487 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2TE304A | MOTOR STATOR TEMP 1 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
488 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2TE304B | MOTOR STATOR TEMP 2 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
489 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP A #2 | 2233 | A2TE304C | MOTOR STATOR TEMP 3 OF #1 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
490 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SWING PIPE SUPERHEATER SYSTEM #2 | 2208 | A2TE103 | #2 BOILER SWING PIPE INLET HEADER TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
491 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2PT101 | #2 BOILER UPSTREAM-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
492 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2PT102 | #2 BOILER DOWNSTREAM-CONTROL VALVE PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
493 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2PT103A | #2 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
494 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2PT103B | #2 BOILER DRUM PRESSURE | AI | MPa | 0 | 10 | 3.7 | 0 | 4.85 | 6.04 | 0 | 6.27
495 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | B1LT101A_1 | #2 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
496 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | B1LT101B_1 | #2 BOILER DRUM LEVEL | AI | mm | -300 | 300 | -100 | -75 | -50 | 50 | 75 | 100
497 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | B1FT102_1 | #2 BOILER FEEDWATER FLOW | AI | t/h | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
498 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2CV104_F | FEEDBACK SIGNAL OF #2 BOILER MAIN FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
499 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | A2CV105_F | FEEDBACK SIGNAL OF #2 BOILER SUBSIDIARY FEED-REGULATING VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
500 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | B1CV104MV | CONTROL SIGNAL OF #2 BOILER MAIN FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
501 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | STEAM DRUM #2 | 2207 | B1CV105MV | CONTROL SIGNAL OF #2 BOILER SUBSIDIARY FEED-REGULATING VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
502 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2G_Power | #2 GENERATOR ACTIVE POWER | AI | MW | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
503 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2G_Freq | #2 GENERATOR FREQUENCY | AI | Hz | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
504 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2G_Factor | #2 GENERATORPOWER FACTOR | AI | pF | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
505 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE221A | #2 TURBINE GENERATOR OUTLET WIND TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 40 | 0 | 0
506 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE221B | #2 TURBINE GENERATOR OUTLET WIND TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 40 | 0 | 0
507 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE222 | #2 TURBINE GENERATOR INLET WIND TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
508 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224A | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
509 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224B | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
510 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224C | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 3 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
511 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224D | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 4 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
512 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224E | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 5 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
513 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE224F | #2 TURBINE GENERATOR STATOR WINDINGS TEMP 6 | RTD | C | 0 | 150 | 0 | 0 | 0 | 105 | 0 | 0
514 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225A | #2 TURBINE GENERATOR STATOR CORE TEMP 1 | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0
515 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225B | #2 TURBINE GENERATOR STATOR CORE TEMP 2 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
516 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225C | #2 TURBINE GENERATOR STATOR CORE TEMP 3 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
517 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225D | #2 TURBINE GENERATOR STATOR CORE TEMP 4 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
518 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225E | #2 TURBINE GENERATOR STATOR CORE TEMP 5 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
519 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2TE225F | #2 TURBINE GENERATOR STATOR CORE TEMP 6 | RTD | C | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0
520 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2G_mvar | #2 STEAM TURBINE MVAR | AI | MVAR | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0
521 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | GENERATOR #2 | 2265 | A2G_tan | #2 STEAM TURBINE TANGEN FASA | AI |  | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
522 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2B | 2259 | A2TE211B | #2 TURBINE OIL COOLER INLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
523 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2B | 2259 | A2TE212B | #2 TURBINE OIL COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
524 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2B | 2259 | A2TE213B | #2 TURBINE OIL COOLER INLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
525 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2B | 2259 | A2TE214B | #2 TURBINE OIL COOLER OUTLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
526 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2A | 2258 | A2TE211A | #2 TURBINE OIL COOLER INLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
527 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2A | 2258 | A2TE212A | #2 TURBINE OIL COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
528 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2A | 2258 | A2TE213A | #2 TURBINE OIL COOLER INLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
529 | PLTU Bolok 2 | TURBINE SYSTEM #2 | OIL COOLER #2A | 2258 | A2TE214A | #2 TURBINE OIL COOLER OUTLET OIL TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
530 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2PT205 | #2 TURBINE EXHAUST STEAM PRE. | AI | MPa | -0.1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0
531 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2PT208 | #2 TURBINE VELOCITY STAGE PRE. | AI | MPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
532 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2RP201A | #2 TURBINE AXIAL POSITION 1 | AI | mm | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
533 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2RP201B | #2 TURBINE AXIAL POSITION 2 | AI | mm | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
534 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2SD201A | #2 TURBINE STEAM TURBINE SPEED 1 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
535 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2SD201B | #2 TURBINE STEAM TURBINE SPEED 2 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
536 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2SD201C | #2 TURBINE STEAM TURBINE SPEED 3 | AI | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
537 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2HE201A | #2 TURBINE STEAM TURBINE HEAT EXPANSION 1 | AI | mm | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
538 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2HE201B | #2 TURBINE STEAM TURBINE HEAT EXPANSION 2 | AI | mm | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0
539 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2DE201A | #2 TURBINE STEAM TURBINE DIFFERENTIAL EXPANSION 1 | AI | mm | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0
540 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2DE201B | #2 TURBINE STEAM TURBINE DIFFERENTIAL EXPANSION 2 | AI | mm | -5 | 5 | 0 | 0 | 0 | 0 | 0 | 0
541 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2TE205A | #2 TURBINE CYLINDER WALL TEMP | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
542 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | A2TE205B | #2 TURBINE CYLINDER WALL TEMP | TC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
543 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | 2SD901 | #2 STEAM TURBINE SPEED OUTPUT | CALC | r/min | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
544 | PLTU Bolok 2 | TURBINE SYSTEM #2 | STEAM TURBINE SYSTEM #2 | 2248 | 2TE905 | #2 TURBINE ST METAL TEMPERATURE | CALC | C | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0
545 | PLTU Bolok 2 | TURBINE SYSTEM #2 | CONDENSATE WATER FOR EXTRACTION VALVE CONTROL WATER SYSTEM #2 | 2243 | A2PT215A | #2 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
546 | PLTU Bolok 2 | TURBINE SYSTEM #2 | CONDENSATE WATER FOR EXTRACTION VALVE CONTROL WATER SYSTEM #2 | 2243 | A2PT215B | #2 TURBINE CONTROL WATER PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
547 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | EXTRACTION PIPING OF GLAND STEAM HEATER SYSTEM #2 | 2242 | A2PT213 | #2 TURBINE EXTRACTION STM PRE. OF GLAND STM HEATER | AI | MPa | -0.1 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0
548 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 2239 | A2PT202 | #2 TURBINE MAIN STEAM PRE. BEF MSV | AI | MPa | 0 | 10 | 0 | 0 | 4.61 | 5.1 | 0 | 0
549 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 2239 | A2PT203 | #2 TURBINE STARTING OIL PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
550 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (HYDRAULIC MSV SYSTEM) | 2239 | A2TE202 | #2 TURBINE MAIN STEAM TEMP. BEF MSV | TC | C | 0 | 600 | 0 | 0 | 455 | 480 | 0 | 0
551 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2PT303C | #3 FEED WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
552 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2M301C_A | #2 TURBINE #3 FEED WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
553 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2TE307A | FRONT BEARING TEMP OF #3 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
554 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2TE307B | BACK BEARING TEMP OF #3 FEED WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
555 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2TE308A | MOTOR STATOR TEMP 1 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
556 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2TE308B | MOTOR STATOR TEMP 2 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
557 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | BOILER FEED WATER PUMP C #2 | 2235 | A2TE308C | MOTOR STATOR TEMP 3 OF #3 FEED WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
558 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2221 | A2PT110 | #2 BOILER LEFT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
559 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2221 | A2FT10_5 | #2 BOILER AIR FLOW OF LEFT WIND BOX | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
560 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2221 | A2TE112 | #2 BOILER LEFT WIND BOX TEMPERATURE | TC | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
561 | PLTU Bolok 2 | COOLING SYSTEM #2 | PIPE PRESSURE PUMP B #2 (BOOSTER PUMP) | 2274 | A2M210B_A | #2 TURBINE #2 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
562 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 TO SEALING STEAM SYSTEM | 2238 | A2PT214 | #2 TURBINE AVERAGE PRE. TANK PRE. | AI | MPa | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
563 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 TO SEALING STEAM SYSTEM | 2238 | A2CV202_F | FEEDBACK SIGNAL OF #2 TURBINE GLAND STEAM HEATER PRE CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
564 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 TO SEALING STEAM SYSTEM | 2238 | 2CV902 | #2 Diff ctrl and FB turbine GSH press ctrl valve | CALC | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
565 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2222 | A2PT111 | #2 BOILER RIGHT WIND BOX PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
566 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2222 | A2FT10_6 | #2 BOILER AIR FLOW OF RIGHT WIND BOX | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
567 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | WINDBOX #2 | 2222 | A2TE113 | #2 BOILER RIGHT WIND BOX TEMPERATURE | TC | C | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
568 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | B1FT103A_1 | #2 BOILER FRONT DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
569 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | B1FT103B_1 | #2 BOILER BACK DESUPERHEATER SPRAY FLOW | AI | t/h | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
570 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | A2CV106A_F | FEEDBACK SIGNAL OF #2 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
571 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | A2CV106B_F | FEEDBACK SIGNAL OF #2 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
572 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | S08_E015.MV | CONTROL SIGNAL OF #2 BOILER FRONT ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
573 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | S08_E017.MV | CONTROL SIGNAL OF #2 BOILER BACK ATTEMPERATING WATER CONTROL VALVE | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
574 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | A2TE104 | #2 BOILER FRONT ATTEMPERATOR TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
575 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ATTEMPERATOR SUPERHEATER #2 | 2209 | A2TE105 | #2 BOILER BACK ATTEMPERATOR TEMPERATURE | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
576 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | REAR BEARING GENERATOR #2 | 2267 | A2VB201D | #2 TURBINE GENERATOR BACK SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
577 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | REAR BEARING GENERATOR #2 | 2267 | A2TE203N | #2 TURBINE #4 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
578 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | REAR BEARING GENERATOR #2 | 2267 | A2VB201Y4 | #2 GENERATOR BACK SHAFT NDE VIBRATION Y DIRECTION | AI | ?m | 0 | 400 | 0 | 0 | 0 | 126.984 | 253.968 | 0
579 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | FRONT BEARING GENERATOR #2 | 2266 | A2VB201C | #2 TURBINE GENERATOR FRONT SHAFT VIBRATION | AI | ?m | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
580 | PLTU Bolok 2 | GENERATOR SYSTEM #2 | FRONT BEARING GENERATOR #2 | 2266 | A2TE203M | #2 TURBINE #3 BEARING TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 110
581 | PLTU Bolok 2 | TURBINE SYSTEM #2 | AC OIL PUMP #2 | 2262 | A2PT221 | #2 TURBINE AC LUBE OIL PUMP OUTLET PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
582 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | HP HEATER #2 | 2236 | A2LT203 | #2 TURBINE HP HEATER LEVEL | AI | mm | 0 | 900 | 0 | 0 | 150 | 900 | 0 | 0
583 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | HP HEATER #2 | 2236 | A2TE215 | #2 TURBINE HP HEATER INLET WATER TEMP | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
584 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | HP HEATER #2 | 2236 | A2TE216 | #2 TURBINE HP HEATER INLET STEAM TEMP | RTD | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
585 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | HP HEATER #2 | 2236 | A2TE217 | #2 TURBINE HP HEATER OUTLET WATER TEMP | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
586 | PLTU Bolok 2 | FEED WATER SYSTEM #2 | HP HEATER #2 | 2236 | 2TE916 | TTD HPH #2 | CALC | C | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
587 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT106 | #2 BOILER PRIMARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
588 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT107A | #2 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
589 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT107B | #2 BOILER PRIMARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
590 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT124A | #2 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
591 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT124B | #2 BOILER GAS PRE. BEFORE PRIMARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
592 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT125A | BOILER OUTLET GAS PRESSURE OF #2 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2PT125B | BOILER OUTLET GAS PRESSURE OF #2 BOILER | AI | Pa | -7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
594 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2AT101 | BOILER OUTLET GAS O2% OF #2 BOILER | AI | % | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0
595 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE111A | #2 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
596 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE111B | #2 BOILER PRIMARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
597 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE124A | #2 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
598 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE124B | #2 BOILER GAS TEMP BEFORE PRIMARY AIR PREHEATER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
599 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE126A | BOILER OUTLET GAS TEMPERATURE OF #2 BOILER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
600 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | PRIMARY AIR PREHEATER SYSTEM #2 | 2228 | A2TE126B | BOILER OUTLET GAS TEMPERATURE OF #2 BOILER | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
601 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | A2FT107_A | #1 SECONDARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
602 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | A2CV102A_F | FEEDBACK SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
603 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | A2M103A_A | #2 BOILER #1 SA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
604 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | S08_E007.MV | CONTROL SIGNAL OF #2 BOILER #1 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
605 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | A2TE130A | FRONT BEARING TEMP OF #2 BOILER #1 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
606 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN A #2 | 2226 | A2TE130B | BACK BEARING TEMP OF #2 BOILER #1 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
607 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2C | 2219 | A2M105C_A1 | #2 BOILER #3 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
608 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2C | 2219 | A2M105C_A2 | #2 BOILER #3 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
609 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2C | 2219 | B1M105CMV | #2 BOILER #3 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
610 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2A | 2217 | A2M105A_A1 | #2 BOILER #1 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
611 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2A | 2217 | A2M105A_A2 | #2 BOILER #1 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
612 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2A | 2217 | B1M105AMV | #2 BOILER #1 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
613 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2A | 2217 | 2M905 | #2 BOILER COAL FLOW | CALC | t/h | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0
614 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL BUNKER #2 | 2216 | A2LT104A | #2 BOILER #1 COAL BUNKER LEVEL | AI | m | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0
615 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL BUNKER #2 | 2216 | A2LT104B | #2 BOILER #2 COAL BUNKER LEVEL | AI | m | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0
616 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2PT104 | #2 BOILER SUPERHEATER OUTLET HEADER PRESSURE | AI | MPa | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
617 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2PT120A | #2 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2PT120B | #2 BOILER GAS PRE. BEFORE HIGH TEMP SUPERHEATER | AI | Pa | -4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE106A | #2 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
620 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE106B | #2 BOILER HIGH TEMP SUPERHEATER INLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
621 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE107 | #2 BOILER SUPERHEATER INTERMEDIATE HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
622 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE108 | #2 BOILER SUPERHEATER OUTLET HEADER TEMP | TC | C | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0
623 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE121A | #2 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
624 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | HIGH TEMPERATURE SUPERHEATER #2 | 2210 | A2TE121B | #2 BOILER GAS TEMP BEFORE HIGH TEMP SUPERHEATER | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
625 | PLTU Bolok 2 | COOLING SYSTEM #2 | COOLING WATER PUMP B #2 - SERVICE PUMP #2B | 2272 | A2M209B_A | #2 TURBINE #2 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
626 | PLTU Bolok 2 | COOLING SYSTEM #2 | COOLING WATER PUMP A #2 - SERVICE PUMP #2A | 2271 | A2PT234 | INDUSTRIAL WATER PUMP OUTLET HEADER PRE. | AI | MPa | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
627 | PLTU Bolok 2 | COOLING SYSTEM #2 | COOLING WATER PUMP A #2 - SERVICE PUMP #2A | 2271 | A2M209A_A | #2 TURBINE #1 SERVICE WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
628 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2PT223 | #2 TURBINE BALL CIRCULATING PUMP OUTLET PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
629 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2TE207A | #2 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
630 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2TE207B | #2 TURBINE CONDENSER CIRCULATING WATER OUTLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
631 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2TE209A | #2 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
632 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2TE209B | #2 TURBINE CONDENSER CIRCULATING WATER INLET TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
633 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | A2TE223 | #2 TURBINE AIR COOLER OUTLET WATER TEMP | RTD | C | 0 | 100 | 0 | 0 | 0 | 40 | 0 | 0
634 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | 2TE909A | #2 DIFF Temp CW A | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
635 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | 2TE909B | #2 DIFF Temp CW B | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
636 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | 2TE909 | Average CW inlet temp #2 | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
637 | PLTU Bolok 2 | COOLING SYSTEM #2 | CIRCULATING WATER COOLING PIPING FOR CONDENSOR #2 | 2268 | 2TE907 | Average CW outlet temp #2 | CALC | C | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
638 | PLTU Bolok 2 | TURBINE SYSTEM #2 | HP OIL PUMP #2 | 2260 | A2PT220 | #2 TURBINE HP STARTING OIL PUMP OUTLET PRE. | AI | MPa | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
639 | PLTU Bolok 2 | TURBINE SYSTEM #2 | HP OIL PUMP #2 | 2260 | A2M202_A | #2 TURBINE HP STARTING OIL PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
640 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2PT212A | #2 TURBINE LUBE OIL PRE. | AI | MPa | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
641 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204A | #2 TURBINE #1 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
642 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204B | #2 TURBINE #2 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
643 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204C | #2 TURBINE #3 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
644 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204D | #2 TURBINE #4 BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
645 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204E | #2 TURBINE #1 POSITIVE THRUST BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
646 | PLTU Bolok 2 | TURBINE SYSTEM #2 | LUBRYCANT SUPPLY PIPING SYSTEM #2 | 2257 | A2TE204F | #2 TURBINE #1 NEGATIVE THRUST BEARING RETURN OIL TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 65 | 0 | 75
647 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN B #2 | 2231 | A2CV103B_F | FEEDBACK SIGNAL OF #2 BOILER #2 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
648 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN B #2 | 2231 | A2M101B_A | #2 BOILER #2 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
649 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN B #2 | 2231 | S08_E018.MV | CONTROL SIGNAL OF #2 BOILER #2 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
650 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN B #2 | 2231 | A2TE133A | FRONT BEARING TEMP OF #2 BOILER #2 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
651 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN B #2 | 2231 | A2TE133B | BACK BEARING TEMP OF #2 BOILER #2 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
652 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2PT108 | #2 BOILER SECONDARY AIR PREHEATER INLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
653 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2PT109A | #2 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
654 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2PT109B | #2 BOILER SECONDARY AIR PREHEATER OUTLET PRESSURE | AI | KPa | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
655 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2PT123A | #2 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2PT123B | #2 BOILER GAS PRE. BEFORE SECONDARY AIR PREHEATER | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2TE114A | #2 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
658 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2TE114B | #2 BOILER SECONDARY AIR PREHEATER OUTLET TEMP | RTD | C | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0
659 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2TE125A | #2 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | RTD | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
660 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | SECONDARY AIR PREHEATER SYSTEM #2 | 2229 | A2TE125B | #2 BOILER GAS TEMP BEFORE SECONDARY AIR PREHEATER | RTD | C | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0
661 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | A2FT104_A | #1 PRIMARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0
662 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | A2CV101A_F | FEEDBACK SIGNAL OF #2 BOILER #1 PA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
663 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | A2M102A_A | #2 BOILER #1 PA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
664 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | S08_E005.MV | CONTROL SIGNAL OF #2 BOILER #1 PA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
665 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | A2TE128A | FRONT BEARING TEMP OF #2 BOILER #1 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
666 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | PRIMARY AIR FAN A #2 | 2224 | A2TE128B | BACK BEARING TEMP OF #2 BOILER #1 PRIMARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
667 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2B | 2218 | A2M105B_A1 | #2 BOILER #2 COAL FEEDER INSTANTANEOUS COAL FEED | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
668 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2B | 2218 | A2M105B_A2 | #2 BOILER #2 COAL FEEDER ROTATIONAL SPEED INPUT | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
669 | PLTU Bolok 2 | COAL FEEDER SYSTEM #2 | COAL FEEDER #2B | 2218 | B1M105BMV | #2 BOILER #2 COAL FEEDER ROTATIONAL SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
670 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT113 | #2 BOILER LEFT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
671 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT114 | #2 BOILER LEFT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
672 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT127 | THE LOWER PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
673 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT128 | THE FEEDING BACK PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
674 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT129 | THE MIDDLE PRESSURE OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
675 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PT133A | #2 BOILER LEFT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PdT136 | THE FEEDING BACK DP OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
677 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2PdT137 | THE LOOSE DP OF #2 BOILER LEFT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
678 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2TE119 | #2 BOILER LEFT CYCLONE REVERT TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
679 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | LEFT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2214 | A2TE127A | #2 BOILER SEPARATOR INLET GAS TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
680 | PLTU Bolok 2 | COOLING SYSTEM #2 | PIPE PRESSURE PUMP A #2 (BOOSTER PUMP) | 2273 | A2M210A_A | #2 TURBINE #1 PIPELINE BOOSTER PUMP CURRENT INDICATE | AI | A | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
681 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2PT501A | #1 CIRCULATING WATER PUMP OUTLET PRESSURE | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
682 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2PT502 | #1,2 CIRCULATING WATER PUMP OUTLET MAIN PIPE PRE. | AI | MPa | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
683 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2FT501 | #1,2 CIRCULATING WATER PUMP OUTLET MAIN PIPE FLOW | AI | t/h | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0
684 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2M501A_A | #2 TURBINE #1 CIRCULATING WATER PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
685 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2TE501A | FRONT BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
686 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2TE501B | BACK BEARING TEMP OF #1 CIRCULATING WATER PUMP MOTOR | RTD | C | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0
687 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2TE502A | MOTOR STATOR TEMP 1 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
688 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2TE502B | MOTOR STATOR TEMP 2 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
689 | PLTU Bolok 2 | COOLING SYSTEM #2 | CWP PUMP #2A | 2269 | A2TE502C | MOTOR STATOR TEMP 3 OF #1 CIRCULATING WATER PUMP | RTD | C | 0 | 300 | 0 | 0 | 0 | 120 | 0 | 0
690 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | VACUUM PUMP #2A | 2255 | A2PT224 | #2 TURBINE VACUUM PUMP INLET PRE. | AI | KPa | -160 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | VACUUM PUMP #2A | 2255 | A2C207AA | #2 VACUUM PUMP A AMPERE INDICATION | AI | A | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0
692 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | A2PT216 | #2 TURBINE LP HEATER INLET STEAM PRE. | AI | MPa | -0.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
693 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | A2TE218 | #2 TURBINE LP HEATER INLET STEAM TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
694 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | A2TE219 | #2 TURBINE LP HEATER INLET WATER TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
695 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | A2TE220 | #2 TURBINE LP HEATER OUTLET WATER TEMP | RTD | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
696 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | 2TE920 | Diff temp LPH #2 | CALC | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
697 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | LP HEATER #2 | 2246 | 2TE919 | TTD LPH #2 | CALC | C | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0
698 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP B#2 | 2245 | A2PT219B | #2 TURBINE #2 CONDENSATE PUMP OUTLET PRE. | AI | MPa | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0
699 | PLTU Bolok 2 | CONDENSATE SYSTEM #2 | CONDENSATE PUMP B#2 | 2245 | A2M201B_A | #2 TURBINE #2 CONDENSATE PUMP CURRENT INDICATE | AI | A | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
700 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (ELECTRIC MSV SYSTEM) | 2237 | A2PT201A | #2 TURBINE MAIN STEAM PRE. BEF ELEC MSV | AI | MPa | 0 | 10 | 0 | 0 | 0 | 5.098 | 0 | 0
701 | PLTU Bolok 2 | MAIN STEAM SYSTEM #2 | MAIN STEAM PIPING SYSTEM #2 (ELECTRIC MSV SYSTEM) | 2237 | A2TE201A | #2 TURBINE MAIN STEAM TEMP. BEF ELEC MSV | TC | C | 0 | 600 | 0 | 0 | 400 | 540 | 0 | 0
702 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2PT126A | #2 BOILER #1 INDUCED DRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
703 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2PT126B | #2 BOILER #2 INDUCED DRAFT FAN INLET PRESSURE | AI | Pa | -8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
704 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2FT109 | #2 BOILER INDUCED AIR FLOW | AI | m3/h | 0 | 200000 | 0 | 0 | 0 | 0 | 0 | 0
705 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2CV103A_F | FEEDBACK SIGNAL OF #2 BOILER #1 ID FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
706 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2M101A_A | #2 BOILER #1 IDF CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
707 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | S08_E004.MV | CONTROL SIGNAL OF #2 BOILER #1 ID FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
708 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2TE132A | FRONT BEARING TEMP OF #2 BOILER #1 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
709 | PLTU Bolok 2 | FLUE GAS SYSTEM #2 | INDUCED DRAFT FAN A #2 | 2230 | A2TE132B | BACK BEARING TEMP OF #2 BOILER #1 INDUCED DRAFT FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
710 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | A2FT107_B | #2 SECONDARY AIR FLOW OF #2 BOILER | AI | m3/h | 0 | 60000 | 0 | 0 | 0 | 0 | 0 | 0
711 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | A2CV102B_F | FEEDBACK SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
712 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | A2M103B_A | #2 BOILER #2 SA FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
713 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | S08_E008.MV | CONTROL SIGNAL OF #2 BOILER #2 SA FAN INLET DAMPER REGULATOR | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
714 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | A2TE131A | FRONT BEARING TEMP OF #2 BOILER #2 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
715 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SECONDARY AIR FAN B #2 | 2227 | A2TE131B | BACK BEARING TEMP OF #2 BOILER #2 SECONDARY AIR FAN | RTD | C | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 0
716 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT115 | #2 BOILER RIGHT REFEED LOOSE WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
717 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT116 | #2 BOILER RIGHT REFEED WIND BOX PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
718 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT130 | THE LOWER PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
719 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT131 | THE FEEDING BACK PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0
720 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT132 | THE MIDDLE PRESSURE OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | Pa | -400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
721 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PT133B | #2 BOILER RIGHT CYCLONE SEPARATOR INLET PRESSURE | AI | Pa | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PdT138 | THE FEEDING BACK DP OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
723 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2PdT139 | THE LOOSE DP OF #2 BOILER RIGHT CYCLONE SEPARATOR | AI | KPa | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0
724 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2TE120 | #2 BOILER RIGHT CYCLONE REVERT TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
725 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RIGHT CYCLONE SEPARATOR (INCLUDE CYLINDER AND REFRACTORY) #2 | 2215 | A2TE127B | #2 BOILER SEPARATOR INLET GAS TEMPERATURE | TC | C | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0
726 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SLAG COOLER B #2 | 2213 | A2M106B_A1 | #2 BOILER #2 COLD SLAG ROTATIONAL SPEED | AI | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
727 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | SLAG COOLER B #2 | 2213 | B1M106BMV | #2 BOILER #2 COLD SLAG REMOTE SPEED CONTROL | AO | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0
728 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2PT122A | #2 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2PT122B | #2 BOILER GAS PRESSURE BEFORE ECONOMIZER | AI | Pa | -5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
730 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2AT102 | GAS FLUE INLET O2% OF #2 BOILER | AI | % | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0
731 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2TE102 | #2 BOILER FEEDWATER TEMPERATURE | RTD | C | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0
732 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2TE123A | #2 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | TC | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
733 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | ECONOMIZER #2 | 2206 | A2TE123B | #2 BOILER GAS TEMPERATURE BEFORE ECONOMIZER | TC | C | 0 | 800 | 0 | 0 | 0 | 0 | 0 | 0
734 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RETURN FAN B #2 | 2160 | A2M104B_A | #2 BOILER #2 RETURN FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0
735 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RETURN FAN A #2 | 2158 | A2PT112 | #2 BOILER REFEED AIR FAN OUTLET PRESSURE | AI | KPa | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0
736 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RETURN FAN A #2 | 2158 | A2FT108A | #2 BOILER AIR FLOW OF LEFT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
737 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RETURN FAN A #2 | 2158 | A2FT108B | #2 BOILER AIR FLOW OF RIGHT REFEED | AI | m3/h | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0
738 | PLTU Bolok 2 | BOILER FURNACE SYSTEM #2 | RETURN FAN A #2 | 2158 | A2M104A_A | #2 BOILER #1 RETURN FAN CURRENT INDICATE | AI | A | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0