## UNIT#1
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062202.PNT | 1FAI:AI062202.PNT | 10HHA10KV001XB12 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
2 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062203.PNT | 1FAI:AI062203.PNT | 10HHA10KV002XB12 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
3 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062204.PNT | 1FAI:AI062204.PNT | 10HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
4 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062205.PNT | 1FAI:AI062205.PNT | 10HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
5 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062301.PNT | 1FAI:AI062301.PNT | 10HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
6 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062302.PNT | 1FAI:AI062302.PNT | 10HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
7 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062303.PNT | 1FAI:AI062303.PNT | 10HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
8 | Manipulated Variable | Burner Tilt Position | OPC.AW1002.1FAI.AI062304.PNT | 1FAI:AI062304.PNT | 10HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
9 | Manipulated Variable | Secondary Air Flow | OPC.AW1002.1EAI.AI051105.PNT | 1EAI:AI051105.PNT | 10HLA10CF201 | FURNACE A-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | (AVG(10HLA10CF201);(10HLA10CF202))+(AVG(10HLA20CF201);(10HLA20CF202))
10 | Manipulated Variable | Secondary Air Flow | OPC.AW1002.1EAI.AI051202.PNT | 1EAI:AI051202.PNT | 10HLA10CF202 | FURNACE A-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h
11 | Manipulated Variable | Secondary Air Flow | OPC.AW1002.1EAI.AI051106.PNT | 1EAI:AI051106.PNT | 10HLA20CF201 | FURNACE B-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h
12 | Manipulated Variable | Secondary Air Flow | OPC.AW1002.1EAI.AI051203.PNT | 1EAI:AI051203.PNT | 10HLA20CF202 | FURNACE B-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h
13 | Manipulated Variable | FDF Fan Air Flow | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NO SENSOR AVAILABLE
14 | Manipulated Variable | Coal Flow | OPC.AW1002.1E_FUELC.CALCA1OUT.PNT | 1E_FUELC:CALCA1OUT.PNT | 10HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
15 | Disturbance Variable | Load | OPC.AW1002.1EAI.AI052407.PNT | 1EAI:AI052407.PNT | 10DEHDCSAI02 | GENERATOR LOAD | AI | 0 | 519.6 | MW
16 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMA1AIN.PNT | 1E_AIRFLOW:MSMA1AIN.PNT | 10HFE51CF201 | MSM A INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | (AVG(10HFE51CF201);(10HFE51CF202))+(AVG(10HFE52CF201);(10HFE52CF202))+(AVG(10HFE53CF201);(10HFE53CF202))+(AVG(10HFE54CF201);(10HFE54CF202))+(AVG(10HFE55CF201);(10HFE55CF202))
17 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMA2AIN.PNT | 1E_AIRFLOW:MSMA2AIN.PNT | 10HFE51CF202 | MSM A INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
18 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMB1AIN.PNT | 1E_AIRFLOW:MSMB1AIN.PNT | 10HFE52CF201 | MSM B INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
19 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMB2AIN.PNT | 1E_AIRFLOW:MSMB2AIN.PNT | 10HFE52CF202 | MSM B INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
20 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMC1AIN.PNT | 1E_AIRFLOW:MSMC1AIN.PNT | 10HFE53CF201 | MSM C INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
21 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMC2AIN.PNT | 1E_AIRFLOW:MSMC2AIN.PNT | 10HFE53CF202 | MSM C INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
22 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMD1AIN.PNT | 1E_AIRFLOW:MSMD1AIN.PNT | 10HFE54CF201 | MSM D INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
23 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSMD2AIN.PNT | 1E_AIRFLOW:MSMD2AIN.PNT | 10HFE54CF202 | MSM D INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
24 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSME1AIN.PNT | 1E_AIRFLOW:MSME1AIN.PNT | 10HFE55CF201 | MSM E INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
25 | Disturbance Variable | Mill PA Flow | OPC.AW1002.1E_AIRFLOW.MSME2AIN.PNT | 1E_AIRFLOW:MSME2AIN.PNT | 10HFE55CF202 | MSM E INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
26 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1GAI.AI070107.PNT | 1GAI:AI070107.PNT | 10HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC10CT015);(10HFC10CT016);(10HFC10CT017))
27 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050501.PNT | 1EAI:AI050501.PNT | 10HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
28 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050601.PNT | 1EAI:AI050601.PNT | 10HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
29 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1GAI.AI070307.PNT | 1GAI:AI070307.PNT | 10HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC20CT015);(10HFC20CT016);(10HFC20CT017))
30 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050502.PNT | 1EAI:AI050502.PNT | 10HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
31 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050602.PNT | 1EAI:AI050602.PNT | 10HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
32 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1HAI.AI090107.PNT | 1HAI:AI090107.PNT | 10HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC30CT015);(10HFC30CT016);(10HFC30CT017))
33 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050503.PNT | 1EAI:AI050503.PNT | 10HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
34 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050603.PNT | 1EAI:AI050603.PNT | 10HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
35 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1HAI.AI090307.PNT | 1HAI:AI090307.PNT | 10HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC40CT015);(10HFC40CT016);(10HFC40CT017))
36 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050504.PNT | 1EAI:AI050504.PNT | 10HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
37 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050604.PNT | 1EAI:AI050604.PNT | 10HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
38 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1IAI.AI100107.PNT | 1IAI:AI100107.PNT | 10HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC50CT015);(10HFC50CT016);(10HFC50CT017))
39 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050505.PNT | 1EAI:AI050505.PNT | 10HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
40 | Constrain Variable | Mill Outlet Temperature | OPC.AW1002.1EAI.AI050605.PNT | 1EAI:AI050605.PNT | 10HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
41 | Constrain Variable | Oxygen Sensor | OPC.AW1002.1EAI.AI051707.PNT | 1EAI:AI051707.PNT | 10H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | (AVG(10H10CQ201);(10H10CQ202);(10H20CQ201);(10H20CQ202))
42 | Constrain Variable | Oxygen Sensor | OPC.AW1002.1EAI.AI052105.PNT | 1EAI:AI052105.PNT | 10H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
43 | Constrain Variable | Oxygen Sensor | OPC.AW1002.1EAI.AI052304.PNT | 1EAI:AI052304.PNT | 10H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
44 | Constrain Variable | Oxygen Sensor | OPC.AW1002.1EAI.AI052401.PNT | 1EAI:AI052401.PNT | 10H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
45 | Constrain Variable | Furnace Pressure | OPC.AW1002.1E_IDF.SIGSEL1OUT.PNT | 1E_IDF:SIGSEL1OUT.PNT | 10H10CP201C1 | FURNACE PRESSURE | AI | -250 | 250 | Pa
46 | Constrain Variable | Stack Nox | OPC.AW1002.1LAI.AI142703.PNT | 1LAI:AI142703.PNT | 10HNEAI003 | NOX CONCENTRATION | AI | 0 | 1000 | mg/m3 | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
47 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW1002.1FAI.AI061106.PNT | 1FAI:AI061106.PNT | 10HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
48 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW1002.1FAI.AI061305.PNT | 1FAI:AI061305.PNT | 10HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
49 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW1002.1FAI.AI061504.PNT | 1FAI:AI061504.PNT | 10HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
50 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW1002.1FAI.AI061703.PNT | 1FAI:AI061703.PNT | 10HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
51 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW1002.1EAI.AI051307.PNT | 1EAI:AI051307.PNT | 10H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | (AVG(10H10DP201);(10H10DP202))
52 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW1002.1EAI.AI051401.PNT | 1EAI:AI051401.PNT | 10H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
53 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW1002.1EAI.AI051403.PNT | 1EAI:AI051403.PNT | 10H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | (AVG(10H20DP201);(10H20DP202))
54 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW1002.1EAI.AI051501.PNT | 1EAI:AI051501.PNT | 10H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
55 | Efficiency Variable | Coal Flow | OPC.AW1002.1E_FUELC.CALCA1OUT.PNT | 1E_FUELC:CALCA1OUT.PNT | 10HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
56 | Efficiency Variable | Main Steam Pressure | OPC.AW1002.1LAI.AI140307.PNT | 1LAI:AI140307.PNT | 10LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa |  |  | 0 | 17.41
57 | Efficiency Variable | Feed Water Pressure | OPC.AW1002.1LAI.AI140606.PNT | 1LAI:AI140606.PNT | 10LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa
58 | Efficiency Variable | SH Spray Water Pressure | OPC.AW1002.1LAI.AI140507.PNT | 1LAI:AI140507.PNT | 10LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa
59 | Efficiency Variable | Reheat Spray Water Pressure | OPC.AW1002.1LAI.AI140506.PNT | 1LAI:AI140506.PNT | 10LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa
60 | Efficiency Variable | Cold Reheat Steam Pressure | OPC.AW1002.1LAI.AI140406.PNT | 1LAI:AI140406.PNT | 10LBC21CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
61 | Efficiency Variable | Cold Reheat Steam Pressure | OPC.AW1002.1LAI.AI140407.PNT | 1LAI:AI140407.PNT | 10LBC22CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
62 | Efficiency Variable | Hot Reheat Steam Pressure | OPC.AW1002.1LAI.AI140505.PNT | 1LAI:AI140505.PNT | 10LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa
63 | Efficiency Variable | Main Steam Temperature | OPC.AW1002.1FAI.AI060206.PNT | 1FAI:AI060206.PNT | 10LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
64 | Efficiency Variable | Main Steam Temperature | OPC.AW1002.1FAI.AI060304.PNT | 1FAI:AI060304.PNT | 10LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
65 | Efficiency Variable | Feed Water Temperature | OPC.AW1002.1MAI.AI163307.PNT | 1MAI:AI163307.PNT | 10LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | ℃
66 | Efficiency Variable | SH Spray Temperature | OPC.AW1002.1LAI.AI142104.PNT | 1LAI:AI142104.PNT | 10LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃
67 | Efficiency Variable | Reheat Spray Temperature | OPC.AW1002.1LAI.AI142103.PNT | 1LAI:AI142103.PNT | 10LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃
68 | Efficiency Variable | Cold Reheat Steam Temperature | OPC.AW1002.1LAI.AI141706.PNT | 1LAI:AI141706.PNT | 10LBC21CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃
69 | Efficiency Variable | Cold Reheat Steam Temperature | OPC.AW1002.1LAI.AI141707.PNT | 1LAI:AI141707.PNT | 10LBC22CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃
70 | Efficiency Variable | Hot Reheat Steam Temperature | OPC.AW1002.1LAI.AI142102.PNT | 1LAI:AI142102.PNT | 10LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
71 | Efficiency Variable | Main Steam Flow | OPC.AW1002.1M_MSTFLOW.SWCH2OUT.PNT | 1M_MSTFLOW:SWCH2OUT.PNT | 10LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h
72 | Efficiency Variable | Feed Water Flow | OPC.AW1002.1M_FLOW.FW1AIN.PNT | 1M_FLOW:FW1AIN.PNT | 10LAB40CF201 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | (AVG(10LAB40CF201);(10LAB40CF202);(10LAB40CF203))
73 | Efficiency Variable | Feed Water Flow | OPC.AW1002.1M_FLOW.FW2AIN.PNT | 1M_FLOW:FW2AIN.PNT | 10LAB40CF202 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
74 | Efficiency Variable | Feed Water Flow | OPC.AW1002.1M_FLOW.FW3AIN.PNT | 1M_FLOW:FW3AIN.PNT | 10LAB40CF203 | FEED WATER FLOW | AI | 0 | 1600 | t/h
75 | Efficiency Variable | SH Spray Water Flow | OPC.AW1002.1F_FLOW.1SHCALCA.RO01 | 1F_FLOW:1SHCALCA.RO01 | 10LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | ((10LAE41CF201)+(10LAE42CF201)+(10LAE43CF201)+(10LAE44CF201)+(10LAE45CF201)+(10LAF61CF201)+(10LAF62CF201)+(10LAF63CF201)+(10LAF61CF201))
76 | Efficiency Variable | SH Spray Water Flow | OPC.AW1002.1F_FLOW.2SHACALCA.RO01 | 1F_FLOW:2SHACALCA.RO01 | 10LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
77 | Efficiency Variable | SH Spray Water Flow | OPC.AW1002.1F_FLOW.2SHBCALCA.RO01 | 1F_FLOW:2SHBCALCA.RO01 | 10LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
78 | Efficiency Variable | SH Spray Water Flow | OPC.AW1002.1F_FLOW.3SHACALCA.RO01 | 1F_FLOW:3SHACALCA.RO01 | 10LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
79 | Efficiency Variable | SH Spray Water Flow | OPC.AW1002.1F_FLOW.3SHBCALCA.RO01 | 1F_FLOW:3SHBCALCA.RO01 | 10LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
80 | Efficiency Variable | Reheat Spray water Flow | OPC.AW1002.1F_FLOW.RHCALCA.RO01 | 1F_FLOW:RHCALCA.RO01 | 10LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | ((10LAF61CF201)+(10LAF62CF201)+(10LAF63CF201)+(10LAF61CF201))
81 | Efficiency Variable | Reheat Spray water Flow | OPC.AW1002.1F_FLOW.RHACALCA.RO01 | 1F_FLOW:RHACALCA.RO01 | 10LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
82 | Efficiency Variable | Reheat Spray water Flow | OPC.AW1002.1F_FLOW.RHBCALCA.RO01 | 1F_FLOW:RHBCALCA.RO01 | 10LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
83 | Efficiency Variable | Reheat Spray water Flow | OPC.AW1002.1F_FLOW.RHCALCA.RO01 | 1F_FLOW:RHCALCA.RO01 | 10LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
84 | Efficiency Variable | Reheat Steam Flow | OPC.AW1002.1PMS.RSFLOW.RO01 | 1PMS:RSFLOW.RO01 | 10LBB10CF101C1 | RH STEAM OUTLET FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | (AVG(10LBB10CF101C1);(10LBB10CF101C2))
85 | Efficiency Variable | Reheat Steam Flow | OPC.AW1002.1PMS.RSFLOW.RO02 | 1PMS:RSFLOW.RO02 | 10LBB10CF101C2 | RH STM FLOW | AI | 0 | 1000 | t/h |  |  | 0
86 | Control Variable | Secondary Air Flow | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NO SENSOR AVAILABLE
87 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063601.BIAS | 1F_RHTEM:AO063601.BIAS | 10HHA10KV001XB11B | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
88 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063602.BIAS | 1F_RHTEM:AO063602.BIAS | 10HHA10KV002XB11B | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
89 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063603.BIAS | 1F_RHTEM:AO063603.BIAS | 10HHA20KV001XB11B | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
90 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063604.BIAS | 1F_RHTEM:AO063604.BIAS | 10HHA20KV002XB11B | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
91 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063605.BIAS | 1F_RHTEM:AO063605.BIAS | 10HHA30KV001XB11B | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
92 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063701.BIAS | 1F_RHTEM:AO063701.BIAS | 10HHA30KV002XB11B | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
93 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063702.BIAS | 1F_RHTEM:AO063702.BIAS | 10HHA40KV001XB11B | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
94 | Control Variable | Burner Tilt | OPC.AW1002.1F_RHTEM.AO063703.BIAS | 1F_RHTEM:AO063703.BIAS | 10HHA40KV002XB11B | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
95 | Control Variable | FD Fan Air Flow | OPC.AW1002.1E_FDF.AO052501.BIAS | 1E_FDF:AO052501.BIAS | 10HLB10AA101XB11B | FDF A INLET VANE CONTROL COMMAND BIAS | AO | 0 | 100 | %
96 | Control Variable | FD Fan Air Flow | OPC.AW1002.1E_FDF.AO052601.BIAS | 1E_FDF:AO052601.BIAS | 10HLB20AA101XB11B | FDF B INLET VANE CONTROL COMMAND BIAS | AO | 0 | 100 | %

## UNIT#2
NO | VARIABLE | VARIABLE DESCRIPTION | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | REMARKS | NOTES
1 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062202.PNT | 2FAI.AI062202.PNT | 20HHA10KV001XB12 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
2 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062203.PNT | 2FAI.AI062203.PNT | 20HHA10KV002XB12 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
3 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062204.PNT | 2FAI.AI062204.PNT | 20HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
4 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062205.PNT | 2FAI.AI062205.PNT | 20HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
5 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062301.PNT | 2FAI.AI062301.PNT | 20HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
6 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062302.PNT | 2FAI.AI062302.PNT | 20HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
7 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062303.PNT | 2FAI.AI062303.PNT | 20HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
8 | Manipulated Variable | Burner Tilt Position | OPC.AW2002.2FAI.AI062304.PNT | 2FAI.AI062304.PNT | 20HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | %
9 | Manipulated Variable | Secondary Air Flow | OPC.AW2002.2EAI.AI051105.PNT | 2EAI.AI051105.PNT | 20HLA10CF201 | FURNACE A-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | (AVG(10HLA10CF201);(10HLA10CF202))+(AVG(10HLA20CF201);(10HLA20CF202))
10 | Manipulated Variable | Secondary Air Flow | OPC.AW2002.2EAI.AI051202.PNT | 2EAI.AI051202.PNT | 20HLA10CF202 | FURNACE A-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h
11 | Manipulated Variable | Secondary Air Flow | OPC.AW2002.2EAI.AI051106.PNT | 2EAI.AI051106.PNT | 20HLA20CF201 | FURNACE B-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h
12 | Manipulated Variable | Secondary Air Flow | OPC.AW2002.2EAI.AI051203.PNT | 2EAI.AI051203.PNT | 20HLA20CF202 | FURNACE B-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h
13 | Manipulated Variable | FDF Fan Air Flow | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NO SENSOR AVAILABLE
14 | Manipulated Variable | Coal Flow | OPC.AW2002.2E_FUELC.CALCA1OUT.PNT | 2E_FUELC.CALCA1OUT.PNT | 20HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
15 | Disturbance Variable | Load | OPC.AW2002.2EAI.AI052407.PNT | 2EAI.AI052407.PNT | 20DEHDCSAI02 | GENERATOR LOAD | AI | 0 | 519.6 | MW
16 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMA1AIN.PNT | 2E_AIRFLOW.MSMA1AIN.PNT | 20HFE51CF201 | MSM A INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | (AVG(10HFE51CF201);(10HFE51CF202))+(AVG(10HFE52CF201);(10HFE52CF202))+(AVG(10HFE53CF201);(10HFE53CF202))+(AVG(10HFE54CF201);(10HFE54CF202))+(AVG(10HFE55CF201);(10HFE55CF202))
17 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMA2AIN.PNT | 2E_AIRFLOW.MSMA2AIN.PNT | 20HFE51CF202 | MSM A INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
18 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMB1AIN.PNT | 2E_AIRFLOW.MSMB1AIN.PNT | 20HFE52CF201 | MSM B INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
19 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMB2AIN.PNT | 2E_AIRFLOW.MSMB2AIN.PNT | 20HFE52CF202 | MSM B INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
20 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMC1AIN.PNT | 2E_AIRFLOW.MSMC1AIN.PNT | 20HFE53CF201 | MSM C INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
21 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMC2AIN.PNT | 2E_AIRFLOW.MSMC2AIN.PNT | 20HFE53CF202 | MSM C INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
22 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMD1AIN.PNT | 2E_AIRFLOW.MSMD1AIN.PNT | 20HFE54CF201 | MSM D INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
23 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSMD2AIN.PNT | 2E_AIRFLOW.MSMD2AIN.PNT | 20HFE54CF202 | MSM D INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
24 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSME1AIN.PNT | 2E_AIRFLOW.MSME1AIN.PNT | 20HFE55CF201 | MSM E INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h
25 | Disturbance Variable | Mill PA Flow | OPC.AW2002.2E_AIRFLOW.MSME2AIN.PNT | 2E_AIRFLOW.MSME2AIN.PNT | 20HFE55CF202 | MSM E INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h
26 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2GAI.AI070107.PNT | 2GAI.AI070107.PNT | 20HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC10CT015);(10HFC10CT016);(10HFC10CT017))
27 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050501.PNT | 2EAI.AI050501.PNT | 20HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
28 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050601.PNT | 2EAI.AI050601.PNT | 20HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
29 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2GAI.AI070307.PNT | 2GAI.AI070307.PNT | 20HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC20CT015);(10HFC20CT016);(10HFC20CT017))
30 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050502.PNT | 2EAI.AI050502.PNT | 20HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
31 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050602.PNT | 2EAI.AI050602.PNT | 20HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
32 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2HAI.AI090107.PNT | 2HAI.AI090107.PNT | 20HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC30CT015);(10HFC30CT016);(10HFC30CT017))
33 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050503.PNT | 2EAI.AI050503.PNT | 20HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
34 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050603.PNT | 2EAI.AI050603.PNT | 20HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
35 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2HAI.AI090307.PNT | 2HAI.AI090307.PNT | 20HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC40CT015);(10HFC40CT016);(10HFC40CT017))
36 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050504.PNT | 2EAI.AI050504.PNT | 20HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
37 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050604.PNT | 2EAI.AI050604.PNT | 20HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
38 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2IAI.AI100107.PNT | 2IAI.AI100107.PNT | 20HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | (AVG(10HFC50CT015);(10HFC50CT016);(10HFC50CT017))
39 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050505.PNT | 2EAI.AI050505.PNT | 20HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
40 | Constrain Variable | Mill Outlet Temperature | OPC.AW2002.2EAI.AI050605.PNT | 2EAI.AI050605.PNT | 20HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71
41 | Constrain Variable | Oxygen Sensor | OPC.AW2002.2EAI.AI051707.PNT | 2EAI.AI051707.PNT | 20H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | (AVG(10H10CQ201);(10H10CQ202);(10H20CQ201);(10H20CQ202))
42 | Constrain Variable | Oxygen Sensor | OPC.AW2002.2EAI.AI052105.PNT | 2EAI.AI052105.PNT | 20H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
43 | Constrain Variable | Oxygen Sensor | OPC.AW2002.2EAI.AI052304.PNT | 2EAI.AI052304.PNT | 20H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
44 | Constrain Variable | Oxygen Sensor | OPC.AW2002.2EAI.AI052401.PNT | 2EAI.AI052401.PNT | 20H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | %
45 | Constrain Variable | Furnace Pressure | OPC.AW2002.2E_IDF.SIGSEL1OUT.PNT | 2E_IDF.SIGSEL1OUT.PNT | 20H10CP201C1 | FURNACE PRESSURE | AI | -250 | 250 | Pa
46 | Constrain Variable | Stack Nox | OPC.AW2002.2LAI.AI142703.PNT | 2LAI.AI142703.PNT | 20HNEAI003 | NOX CONCENTRATION | AI | 0 | 1000 | mg/m3 | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
47 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW2002.2FAI.AI061106.PNT | 2FAI.AI061106.PNT | 20HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
48 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW2002.2FAI.AI061305.PNT | 2FAI.AI061305.PNT | 20HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
49 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW2002.2FAI.AI061504.PNT | 2FAI.AI061504.PNT | 20HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
50 | Constrain Variable | Over-Fire-Air Dampers | OPC.AW2002.2FAI.AI061703.PNT | 2FAI.AI061703.PNT | 20HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | %
51 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW2002.2EAI.AI051307.PNT | 2EAI.AI051307.PNT | 20H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | (AVG(10H10DP201);(10H10DP202))
52 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW2002.2EAI.AI051401.PNT | 2EAI.AI051401.PNT | 20H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
53 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW2002.2EAI.AI051403.PNT | 2EAI.AI051403.PNT | 20H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | (AVG(10H20DP201);(10H20DP202))
54 | Constrain Variable | Windbox-to-Furnace Diff. Press | OPC.AW2002.2EAI.AI051501.PNT | 2EAI.AI051501.PNT | 20H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa
55 | Efficiency Variable | Coal Flow | OPC.AW2002.2E_FUELC.CALCA1OUT.PNT | 2E_FUELC.CALCA1OUT.PNT | 20HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H
56 | Efficiency Variable | Main Steam Pressure | OPC.AW2002.2LAI.AI140307.PNT | 2LAI:AI140307.PNT | 20LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa |  |  | 0 | 17.41
57 | Efficiency Variable | Feed Water Pressure | OPC.AW2002.2LAI.AI140606.PNT | 2LAI:AI140606.PNT | 20LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa
58 | Efficiency Variable | SH Spray Water Pressure | OPC.AW2002.2LAI.AI140507.PNT | 2LAI:AI140507.PNT | 20LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa
59 | Efficiency Variable | Reheat Spray Water Pressure | OPC.AW2002.2LAI.AI140506.PNT | 2LAI:AI140506.PNT | 20LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa
60 | Efficiency Variable | Cold Reheat Steam Pressure | OPC.AW2002.2LAI.AI140406.PNT | 2LAI:AI140406.PNT | 20LBC21CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
61 | Efficiency Variable | Cold Reheat Steam Pressure | OPC.AW2002.2LAI.AI140407.PNT | 2LAI:AI140407.PNT | 20LBC22CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa
62 | Efficiency Variable | Hot Reheat Steam Pressure | OPC.AW2002.2LAI.AI140505.PNT | 2LAI:AI140505.PNT | 20LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa
63 | Efficiency Variable | Main Steam Temperature | OPC.AW2002.2FAI.AI060206.PNT | 2FAI:AI060206.PNT | 20LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
64 | Efficiency Variable | Main Steam Temperature | OPC.AW2002.2FAI.AI060304.PNT | 2FAI:AI060304.PNT | 20LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
65 | Efficiency Variable | Feed Water Temperature | OPC.AW2002.2MAI.AI163307.PNT | 2MAI:AI163307.PNT | 20LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | ℃
66 | Efficiency Variable | SH Spray Temperature | OPC.AW2002.2LAI.AI142104.PNT | 2LAI:AI142104.PNT | 20LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃
67 | Efficiency Variable | Reheat Spray Temperature | OPC.AW2002.2LAI.AI142103.PNT | 2LAI:AI142103.PNT | 20LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃
68 | Efficiency Variable | Cold Reheat Steam Temperature | OPC.AW2002.2LAI.AI141706.PNT | 2LAI:AI141706.PNT | 20LBC21CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃
69 | Efficiency Variable | Cold Reheat Steam Temperature | OPC.AW2002.2LAI.AI141707.PNT | 2LAI:AI141707.PNT | 20LBC22CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃
70 | Efficiency Variable | Hot Reheat Steam Temperature | OPC.AW2002.2LAI.AI142102.PNT | 2LAI:AI142102.PNT | 20LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545
71 | Efficiency Variable | Main Steam Flow | OPC.AW2002.2M_MSTFLOW.SWCH2OUT.PNT | 2M_MSTFLOW.SWCH2OUT.PNT | 20LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h
72 | Efficiency Variable | Feed Water Flow | OPC.AW2002.2M_FLOW.FW1AIN.PNT | 2M_FLOW.FW1AIN.PNT | 20LAB40CF201 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | (AVG(10LAB40CF201);(10LAB40CF202);(10LAB40CF203))
73 | Efficiency Variable | Feed Water Flow | OPC.AW2002.2M_FLOW.FW2AIN.PNT | 2M_FLOW.FW2AIN.PNT | 20LAB40CF202 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
74 | Efficiency Variable | Feed Water Flow | OPC.AW2002.2M_FLOW.FW3AIN.PNT | 2M_FLOW.FW3AIN.PNT | 20LAB40CF203 | FEED WATER FLOW | AI | 0 | 1600 | t/h
75 | Efficiency Variable | SH Spray Water Flow | OPC.AW2002.2F_FLOW.1SHCALCA.RO01 | 2F_FLOW.1SHCALCA.RO01 | 20LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | ((10LAE41CF201)+(10LAE42CF201)+(10LAE43CF201)+(10LAE44CF201)+(10LAE45CF201)+(10LAF61CF201)+(10LAF62CF201)+(10LAF63CF201)+(10LAF61CF201))
76 | Efficiency Variable | SH Spray Water Flow | OPC.AW2002.2F_FLOW.2SHACALCA.RO01 | 2F_FLOW.2SHACALCA.RO01 | 20LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
77 | Efficiency Variable | SH Spray Water Flow | OPC.AW2002.2F_FLOW.2SHBCALCA.RO01 | 2F_FLOW.2SHBCALCA.RO01 | 20LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
78 | Efficiency Variable | SH Spray Water Flow | OPC.AW2002.2F_FLOW.3SHACALCA.RO01 | 2F_FLOW.3SHACALCA.RO01 | 20LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
79 | Efficiency Variable | SH Spray Water Flow | OPC.AW2002.2F_FLOW.3SHBCALCA.RO01 | 2F_FLOW.3SHBCALCA.RO01 | 20LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
80 | Efficiency Variable | Reheat Spray water Flow | OPC.AW2002.2F_FLOW.RHCALCA.RO01 | 2F_FLOW.RHCALCA.RO01 | 20LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | ((10LAF61CF201)+(10LAF62CF201)+(10LAF63CF201)+(10LAF61CF201))
81 | Efficiency Variable | Reheat Spray water Flow | OPC.AW2002.2F_FLOW.RHACALCA.RO01 | 2F_FLOW.RHACALCA.RO01 | 20LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [7 empty] | minta data history ke unit dengan timestamp 1 menit selama 1 tahun
82 | Efficiency Variable | Reheat Spray water Flow | OPC.AW2002.2F_FLOW.RHBCALCA.RO01 | 2F_FLOW.RHBCALCA.RO01 | 20LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
83 | Efficiency Variable | Reheat Spray water Flow | OPC.AW2002.2F_FLOW.RHCALCA.RO01 | 2F_FLOW.RHCALCA.RO01 | 20LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h
84 | Efficiency Variable | Reheat Steam Flow | OPC.AW2002.2PMS.RSFLOW.RO01 | 2PMS.RSFLOW.RO01 | 20LBB10CF101C1 | RH STEAM OUTLET FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | (AVG(10LBB10CF101C1);(10LBB10CF101C2))
85 | Efficiency Variable | Reheat Steam Flow | OPC.AW2002.2PMS.RSFLOW.RO02 | 2PMS.RSFLOW.RO02 | 20LBB10CF101C2 | RH STM FLOW | AI | 0 | 1000 | t/h |  |  | 0
86 | Control Variable | Secondary Air Flow | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NO SENSOR AVAILABLE
87 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063601.BIAS | 2F_RHTEM.AO063601.BIAS | 20HHA10KV001XB11B | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
88 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063602.BIAS | 2F_RHTEM.AO063602.BIAS | 20HHA10KV002XB11B | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
89 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063603.BIAS | 2F_RHTEM.AO063603.BIAS | 20HHA20KV001XB11B | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
90 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063604.BIAS | 2F_RHTEM.AO063604.BIAS | 20HHA20KV002XB11B | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
91 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063605.BIAS | 2F_RHTEM.AO063605.BIAS | 20HHA30KV001XB11B | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
92 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063701.BIAS | 2F_RHTEM.AO063701.BIAS | 20HHA30KV002XB11B | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
93 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063702.BIAS | 2F_RHTEM.AO063702.BIAS | 20HHA40KV001XB11B | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
94 | Control Variable | Burner Tilt | OPC.AW2002.2F_RHTEM.AO063703.BIAS | 2F_RHTEM.AO063703.BIAS | 20HHA40KV002XB11B | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND BIAS | AO | 0 | 100 | %
95 | Control Variable | FD Fan Air Flow | OPC.AW2002.2E_FDF.AO052501.BIAS | 2E_FDF.AO052501.BIAS | 20HLB10AA101XB11B | FDF A INLET VANE CONTROL COMMAND BIAS | AO | 0 | 100 | %
96 | Control Variable | FD Fan Air Flow | OPC.AW2002.2E_FDF.AO052601.BIAS | 2E_FDF.AO052601.BIAS | 20HLB20AA101XB11B | FDF B INLET VANE CONTROL COMMAND BIAS | AO | 0 | 100 | %

## UJPCT#1 (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS
1 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161405.PNT | 1MAI:AI161405.PNT | 10MAG10CL201 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 741.0469 | ok
2 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161501.PNT | 1MAI:AI161501.PNT | 10MAG10CL202 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 730.6875 | ok
3 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161601.PNT | 1MAI:AI161601.PNT | 10MAG10CL203 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 729.6094 | ok
4 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1NAI.AI172205.PNT | 1NAI:AI172205.PNT | 10PAH11GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM A SIDE DIFF.PRESS | AI | -1 | 9 | KPa | [6 empty] | -0.58398 | ok
5 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1NAI.AI172302.PNT | 1NAI:AI172302.PNT | 10PAH12GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM B SIDE DIFF.PRESS | AI | -1 | 9 | KPa | [6 empty] | 0 | ok
6 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI212707.PNT | 1QAI:AI212707.PNT | 10PAH21CP201 | CONDENSER SIDE A CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.11184 | ok
7 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI210202.PNT | 1QAI:AI210202.PNT | 10PAH21CT001 | CONDENSER SIDE A CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.3433 | ok
8 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI213202.PNT | 1QAI:AI213202.PNT | 10PAH22CP201 | CONDENSER SIDE B CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.067797 | ok
9 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI210301.PNT | 1QAI:AI210301.PNT | 10PAH22CT001 | CONDENSER SIDE B CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.4213 | ok
10 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1NAI.AI172204.PNT | 1NAI:AI172204.PNT | 10PAH31AA001XB12 | CONDENSER A SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 49.416 | ok
11 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI213201.PNT | 1QAI:AI213201.PNT | 10PAH31CP201 | CONDENSER SIDE A CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.050109 | ok
12 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI210203.PNT | 1QAI:AI210203.PNT | 10PAH31CT001 | CONDENSER SIDE A CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 32.0996 | ok
13 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1NAI.AI172301.PNT | 1NAI:AI172301.PNT | 10PAH32AA001XB12 | CONDENSER B SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 45.5703 | ok
14 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI213107.PNT | 1QAI:AI213107.PNT | 10PAH32CP201 | CONDENSER SIDE B CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.017273 | ok
15 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-13 | OPC.AW1002.1QAI.AI210302.PNT | 1QAI:AI210302.PNT | 10PAH32CT001 | CONDENSER SIDE B CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 31.7605 | ok
16 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 | F296S-J0201-15 | OPC.AW1002.1VALVE.VACUUM.PNT | 1VALVE:VACUUM.PNT | 10MAG10CP201 | CONDENSER VACUUM | AI | -100 | 150 | KPa |  |  |  | -85.3 | -80.3 |  | -93.6084 | ok
17 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1QAI.AI210101.PNT | 1QAI:AI210101.PNT | 10LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 200 | C | [6 empty] | 39.815 | ok
18 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1QAI.AI212701.PNT | 1QAI:AI212701.PNT | 10LCA12CP201 | CONDENSATE PUMP A OUTLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 2.9212 | ok
19 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI173803.PNT | 1NAI:AI173803.PNT | 10LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa |  |  | 1.3 |  |  |  | 2.9164 | ok
20 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI173105.PNT | 1NAI:AI173105.PNT | 10LCB12AP001XB13 | CONDENSER PUMP A CURRENT | AI | 0 | 200 | A |  |  |  | 110.4 |  |  | -0.042969 | no
21 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172507.PNT | 1NAI:AI172507.PNT | 10LCB12CT001 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 30.3188 | ok
22 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172603.PNT | 1NAI:AI172603.PNT | 10LCB12CT002 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 29.3185 | ok
23 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1OAI.AI192501.PNT | 1OAI:AI192501.PNT | 10LCB12CT003 | CONDENSATE PUMP A MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 30.6306 | ok
24 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1OAI.AI192502.PNT | 1OAI:AI192502.PNT | 10LCB12CT004 | CONDENSATE PUMP A MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 31.384 | ok
25 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172604.PNT | 1NAI:AI172604.PNT | 10LCB12CT005 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 32.3713 | ok
26 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172701.PNT | 1NAI:AI172701.PNT | 10LCB12CT006 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 31.5919 | ok
27 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172605.PNT | 1NAI:AI172605.PNT | 10LCB12CT007 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 31.7608 | ok
28 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172702.PNT | 1NAI:AI172702.PNT | 10LCB12CT008 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 31.8517 | ok
29 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172801.PNT | 1NAI:AI172801.PNT | 10LCB12CT009 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 32.2155 | ok
30 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1NAI.AI172606.PNT | 1NAI:AI172606.PNT | 10LCB12CT010 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 31.8257 | ok
31 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1QAI.AI213307.PNT | 1QAI:AI213307.PNT | 10LCB12CY201X | CONDENSATE PUMP A DRIVING END X DIRECTION VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.16016 | ok
32 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 2 | CEP #1A | F296S-J0201-07 | OPC.AW1002.1QAI.AI213401.PNT | 1QAI:AI213401.PNT | 10LCB12CY201Y | CONDENSATE PUMP A DRIVING END X DIRECTION VIBRATION Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.10039 | ok
33 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1QAI.AI213101.PNT | 1QAI:AI213101.PNT | 10LCA13CP201 | CONDENSATE PUMP B OUTLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 2.9173 | ok
34 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172202.PNT | 1NAI:AI172202.PNT | 10LCB13AP001XB13 | CONDENSER PUMP B CURRENT | AI | 0 | 200 | A |  |  |  | 110.4 |  |  | 91 | ok
35 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172607.PNT | 1NAI:AI172607.PNT | 10LCB13CT001 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 62.2247 | ok
36 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172703.PNT | 1NAI:AI172703.PNT | 10LCB13CT002 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 59.4571 | ok
37 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1PAI.AI202501.PNT | 1PAI:AI202501.PNT | 10LCB13CT003 | CONDENSATE PUMP B MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 42.4392 | ok
38 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1PAI.AI202502.PNT | 1PAI:AI202502.PNT | 10LCB13CT004 | CONDENSATE PUMP B MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 58.2359 | ok
39 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172704.PNT | 1NAI:AI172704.PNT | 10LCB13CT005 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 76.6309 | ok
40 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172802.PNT | 1NAI:AI172802.PNT | 10LCB13CT006 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 78.0209 | ok
41 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172705.PNT | 1NAI:AI172705.PNT | 10LCB13CT007 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 74.7602 | ok
42 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172803.PNT | 1NAI:AI172803.PNT | 10LCB13CT008 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 78.0599 | ok
43 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172706.PNT | 1NAI:AI172706.PNT | 10LCB13CT009 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 77.0206 | ok
44 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI172804.PNT | 1NAI:AI172804.PNT | 10LCB13CT010 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 76.1112 | ok
45 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1QAI.AI213302.PNT | 1QAI:AI213302.PNT | 10LCB13CY201X | CONDENSATE PUMP B DRIVING END X DIRECTION VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.023828 | ok
46 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1QAI.AI213402.PNT | 1QAI:AI213402.PNT | 10LCB13CY201Y | CONDENSATE PUMP B DRIVING END X DIRECTION VIBRATION Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 2.4898 | ok
47 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1NAI.AI173107.PNT | 1NAI:AI173107.PNT | 10MAJ21AP001XB13 | VACUUM PUMP A CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | -0.61719 | no
48 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1NAI.AI173207.PNT | 1NAI:AI173207.PNT | 10MAJ21AP002XB13 | VACUUM PUMP A RECIRCULATING PUMP CURRENT | AI | 0 | 10 | A |  |  |  | 6.5 |  |  | 3.691 | ok
49 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210204.PNT | 1QAI:AI210204.PNT | 10MAJ21CT001 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 25.863 | ok
50 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210303.PNT | 1QAI:AI210303.PNT | 10MAJ21CT002 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
51 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210205.PNT | 1QAI:AI210205.PNT | 10MAJ21CT003 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 26.2787 | ok
52 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210304.PNT | 1QAI:AI210304.PNT | 10MAJ21CT004 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
53 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210206.PNT | 1QAI:AI210206.PNT | 10MAJ21CT005 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 26.0708 | ok
54 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210305.PNT | 1QAI:AI210305.PNT | 10MAJ21CT006 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
55 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210207.PNT | 1QAI:AI210207.PNT | 10MAJ21CT007 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 25.5252 | ok
56 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW1002.1QAI.AI210306.PNT | 1QAI:AI210306.PNT | 10MAJ21CT008 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 25.5512 | ok
57 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 4 | AIR REMOVAL #1 - VACUUM PUMP A | F296S-J0201-14 | OPC.AW1002.1RAI.AI230201.PNT | 1RAI:AI230201.PNT | 10PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 26.3306 | ok
58 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210307.PNT | 1QAI:AI210307.PNT | 10MAJ21CT009 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 73.0324 | ok
59 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210401.PNT | 1QAI:AI210401.PNT | 10MAJ21CT010 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
60 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210501.PNT | 1QAI:AI210501.PNT | 10MAJ21CT011 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 73.9678 | ok
61 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210402.PNT | 1QAI:AI210402.PNT | 10MAJ21CT012 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
62 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210502.PNT | 1QAI:AI210502.PNT | 10MAJ21CT013 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 73.4221 | ok
63 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210403.PNT | 1QAI:AI210403.PNT | 10MAJ21CT014 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
64 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210503.PNT | 1QAI:AI210503.PNT | 10MAJ21CT015 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 54.6635 | ok
65 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1QAI.AI210404.PNT | 1QAI:AI210404.PNT | 10MAJ21CT016 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 42.0105 | ok
66 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1NAI.AI172305.PNT | 1NAI:AI172305.PNT | 10MAJ22AP001XB13 | VACUUM PUMP B CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | 162.7031 | ok
67 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW1002.1NAI.AI172306.PNT | 1NAI:AI172306.PNT | 10MAJ22AP002XB13 | VACUUM PUMP B RECIRCULATING PUMP CURRENT | AI | 0 | 10 | A |  |  |  | 6.5 |  |  | 3.9809 | ok
68 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1OAI.AI191303.PNT | 1OAI:AI191303.PNT | 10LBW20AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN A CURRENT | AI | 0 | 50 | A |  |  |  | 21.3 |  |  | -0.22363 | no
69 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1PAI.AI202108.PNT | 1PAI:AI202108.PNT | 10LBW21AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN B CURRENT | AI | 0 | 50 | A |  |  |  | 21.3 |  |  | 9.0752 | ok
70 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI160102.PNT | 1MAI:AI160102.PNT | 10LBW22CT001 | GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | RTD | 0 | 300 | C | [6 empty] | 157.3236 | ok
71 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI161301.PNT | 1MAI:AI161301.PNT | 10LBW24CP201 | GLAND MAIN PIPE PRESS | AI | 0 | 0.13 | MPa | [6 empty] | 0.044213 | ok
72 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1QAI.AI212205.PNT | 1QAI:AI212205.PNT | 10LBW24CT001 | GLAND MAIN PIPE TEMP(BEFORE TEMPERATURE REDUCING DEVICE) | TC | 0 | 600 | C | [6 empty] | 359.5837 | ok
73 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210102.PNT | 1QAI:AI210102.PNT | 10LCA10CT001 | GLAND STEAM CONDENSER INLET TEMP | RTD | 0 | 200 | C | [6 empty] | 40.1138 | ok
74 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210103.PNT | 1QAI:AI210103.PNT | 10LCA10CT002 | GLAND STEAM CONDENSER OUTLET MAIN PIPE TEMP | RTD | 0 | 200 | C | [6 empty] | 41.5428 | ok
75 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI213108.PNT | 1QAI:AI213108.PNT | 10LCE10CP201 | TEMP REDUCE MAIN MAIN PIPE PRESS | AI | 0 | 3 | MPa | [6 empty] | 2.7706 | ok
76 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 | F296S-J0201-10 | OPC.AW1002.1QAI.AI212706.PNT | 1QAI:AI212706.PNT | 10MAV80CP201 | GLAND STEAM CONDENSER INLET STEAM PRESS | AI | -100 | 600 | KPa | [6 empty] | -3.2578 | ok
77 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212605.PNT | 1QAI:AI212605.PNT | 10LBS80CP201 | #8 EXTRACTION STEAM PRESS(LEFT) | AI | -0.1 | 0.15 | MPa | [6 empty] | -0.018755 | ok
78 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212506.PNT | 1QAI:AI212506.PNT | 10LBS80CP202 | #8 EXTRACTION STEAM PRESS(RIGHT) | AI | -0.1 | 0.15 | MPa | [6 empty] | -0.042354 | ok
79 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211607.PNT | 1QAI:AI211607.PNT | 10LBS80CT001 | #8 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 95 | C | [8 empty] | TIDAK DIPAKAI
80 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211701.PNT | 1QAI:AI211701.PNT | 10LBS80CT002 | #8 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 95 | C | [8 empty] | TIDAK DIPAKAI
81 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI212702.PNT | 1QAI:AI212702.PNT | 10LCA10CP201 | #8 LP HEATER INLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 0.69586 | ok
82 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210104.PNT | 1QAI:AI210104.PNT | 10LCA10CT003 | #8 LP HEATER INLET WATER TEMP | RTD | 0 | 200 | C | [6 empty] | 41.6078 | ok
83 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.232.RO01 | 1PMS:232.RO01 | 10LCA10CT003C1 | #7&8 LP TEMP RISE | RTD | -50 | 200 | C | [6 empty] | 56.7303 | ok
84 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.241.RO01 | 1PMS:241.RO01 | 10LCA10CT003C2 | #7&8 LP DIFF. TEMP | RTD | -50 | 200 | C | [6 empty] | -29.8046 | ok
85 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI160706.PNT | 1MAI:AI160706.PNT | 10LCC80CL201 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -18.8574 | ok
86 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP8LVL_1.SIGSEL1OUT.PNT | 1M_LP8LVL_1:SIGSEL1OUT.PNT | 10LCC80CL201C1 | #8 LP HEATER LEVEL SIGSEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -17.4795 | ok
87 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161106.PNT | 1MAI:AI161106.PNT | 10LCC80CL202 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -17.4795 | ok
88 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161206.PNT | 1MAI:AI161206.PNT | 10LCC80CL203 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -16.9648 | ok
89 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP8LVL.AO163201.OUT | 1M_LP8LVL:AO163201.OUT | 10LCJ80AA101XB11 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 43.1351 | ok
90 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162203.PNT | 1MAI:AI162203.PNT | 10LCJ80AA101XB12 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 46.1777 | ok
91 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1QAI.AI211707.PNT | 1QAI:AI211707.PNT | 10LCJ80CT001 | #8 LP HEATER DRAIN WATER TEMP | TC | 0 | 300 | C | [6 empty] | 46.0719 | ok
92 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP8LVL.AO163202.OUT | 1M_LP8LVL:AO163202.OUT | 10LCJ81AA101XB11 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
93 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162204.PNT | 1MAI:AI162204.PNT | 10LCJ81AA101XB12 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.18164 | no
94 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212604.PNT | 1QAI:AI212604.PNT | 10LBS70CP201 | #7 EXTRACTION STEAM PRESS(LEFT) | AI | -0.1 | 0.15 | MPa | [6 empty] | 0.038369 | ok
95 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212505.PNT | 1QAI:AI212505.PNT | 10LBS70CP202 | #7 EXTRACTION STEAM PRESS(RIGHT) | AI | -0.1 | 0.15 | MPa | [6 empty] | 0.035571 | ok
96 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211606.PNT | 1QAI:AI211606.PNT | 10LBS70CT001 | #7 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 140 | C | [8 empty] | TIDAK DIPAKAI
97 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211507.PNT | 1QAI:AI211507.PNT | 10LBS70CT002 | #7 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 140 | C | [8 empty] | TIDAK DIPAKAI
98 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210105.PNT | 1QAI:AI210105.PNT | 10LCA20CT001 | #7 LP HEATER OUTLET WATER TEMP | RTD | 0 | 120 | C | [6 empty] | 98.3381 | ok
99 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI160705.PNT | 1MAI:AI160705.PNT | 10LCC70CL201 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -1.8408 | ok
100 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP7LVL_1.SIGSEL1OUT.PNT | 1M_LP7LVL_1:SIGSEL1OUT.PNT | 10LCC70CL201C1 | #7 LP HEATER LEVEL SIGSEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -5.2275 | ok
101 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161105.PNT | 1MAI:AI161105.PNT | 10LCC70CL202 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -5.2939 | ok
102 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161205.PNT | 1MAI:AI161205.PNT | 10LCC70CL203 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -5.2607 | ok
103 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP7LVL.AO162707.OUT | 1M_LP7LVL:AO162707.OUT | 10LCJ70AA101XB11 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 26.7701 | ok
104 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162201.PNT | 1MAI:AI162201.PNT | 10LCJ70AA101XB12 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 25.3281 | ok
105 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1QAI.AI212106.PNT | 1QAI:AI212106.PNT | 10LCJ70CT001 | #7 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 77.7048 | ok
106 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP7LVL.AO163105.OUT | 1M_LP7LVL:AO163105.OUT | 10LCJ71AA101XB11 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.004372 | ok
107 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162202.PNT | 1MAI:AI162202.PNT | 10LCJ71AA101XB12 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.91992 | no
108 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212603.PNT | 1QAI:AI212603.PNT | 10LBS60CP201 | #6 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.4 | MPa | [6 empty] | 0.092256 | ok
109 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212504.PNT | 1QAI:AI212504.PNT | 10LBS60CP202 | #6 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.4 | MPa | [6 empty] | 0.095094 | ok
110 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211604.PNT | 1QAI:AI211604.PNT | 10LBS60CT001 | #6 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 240.7122 | ok
111 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211605.PNT | 1QAI:AI211605.PNT | 10LBS60CT002 | #6 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 189.144 | ok
112 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211506.PNT | 1QAI:AI211506.PNT | 10LBS60CT003 | #6 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 214.9926 | ok
113 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211505.PNT | 1QAI:AI211505.PNT | 10LBS60CT004 | #6 EXTRACTION STEAM TEMP (LP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 239.0992 | ok
114 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210106.PNT | 1QAI:AI210106.PNT | 10LCA30CT001 | #6 LP HEATER OUTLET WATER TEMP | RTD | 0 | 160 | C | [6 empty] | 118.4006 | ok
115 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.240.RO01 | 1PMS:240.RO01 | 10LCA30CT001C1 | #6 LP DIFF. TEMP | RTD | -50 | 160 | C | [6 empty] | -22.1033 | ok
116 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.231.RO01 | 1PMS:231.RO01 | 10LCA30CT001C2 | #6 LP TEMP RISE | RTD | -50 | 160 | C | [6 empty] | 20.0625 | ok
117 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI160704.PNT | 1MAI:AI160704.PNT | 10LCC60CL201 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -1.0547 | ok
118 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP6LVL_1.SIGSEL1OUT.PNT | 1M_LP6LVL_1:SIGSEL1OUT.PNT | 10LCC60CL201C1 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -5.1914 | ok
119 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161104.PNT | 1MAI:AI161104.PNT | 10LCC60CL202 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -5.168 | ok
120 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161204.PNT | 1MAI:AI161204.PNT | 10LCC60CL203 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -5.25 | ok
121 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP6LVL.AO162706.OUT | 1M_LP6LVL:AO162706.OUT | 10LCJ60AA101XB11 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 48.0854 | ok
122 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162106.PNT | 1MAI:AI162106.PNT | 10LCJ60AA101XB12 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 47.3848 | ok
123 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1QAI.AI211706.PNT | 1QAI:AI211706.PNT | 10LCJ60CT001 | #6 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 99.6495 | ok
124 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP6LVL.AO163104.OUT | 1M_LP6LVL:AO163104.PNT | 10LCJ61AA101XB11 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok | REVISI TAG
125 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162107.PNT | 1MAI:AI162107.PNT | 10LCJ61AA101XB12 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.0019531 | no
126 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212602.PNT | 1QAI:AI212602.PNT | 10LBS50CP201 | #5 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.6 | MPa | [6 empty] | 0.25257 | ok
127 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212503.PNT | 1QAI:AI212503.PNT | 10LBS50CP202 | #5 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.6 | MPa | [6 empty] | 0.25275 | ok
128 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211602.PNT | 1QAI:AI211602.PNT | 10LBS50CT001 | #5 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 292.7988 | ok
129 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211603.PNT | 1QAI:AI211603.PNT | 10LBS50CT002 | #5 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 232.2936 | ok
130 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211504.PNT | 1QAI:AI211504.PNT | 10LBS50CT003 | #5 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 275.5076 | ok
131 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211503.PNT | 1QAI:AI211503.PNT | 10LBS50CT004 | #5 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 288.2794 | ok
132 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210107.PNT | 1QAI:AI210107.PNT | 10LCA40CT001 | #5 LP HEATER OUTLET WATER TEMP | RTD | 0 | 160 | C | [6 empty] | 129.0192 | ok
133 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.239.RO01 | 1PMS:239.RO01 | 10LCA40CT001C1 | #5 LP DIFF. TEMP | RTD | -50 | 160 | C | [6 empty] | -2.4104 | ok
134 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-07 | OPC.AW1002.1PMS.230.RO01 | 1PMS:230.RO01 | 10LCA40CT001C2 | #5 LP TEMP RISE | RTD | -50 | 160 | C | [6 empty] | 10.6186 | ok
135 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI160703.PNT | 1MAI:AI160703.PNT | 10LCC50CL201 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -6.8555 | ok
136 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP5LVL_1.SIGSEL1OUT.PNT | 1M_LP5LVL_1:SIGSEL1OUT.PNT | 10LCC50CL201C1 | #5 LP HEATER LEVEL SIGSEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -7.0664 | ok
137 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161103.PNT | 1MAI:AI161103.PNT | 10LCC50CL202 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -1.9453 | ok
138 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161203.PNT | 1MAI:AI161203.PNT | 10LCC50CL203 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -14.9766 | ok
139 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP5LVL.AO162705.OUT | 1M_LP5LVL:AO162705.OUT | 10LCJ50AA101XB11 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 13.0343 | ok
140 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI161707.PNT | 1MAI:AI161707.PNT | 10LCJ50AA101XB12 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 14.834 | ok
141 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1QAI.AI212105.PNT | 1QAI:AI212105.PNT | 10LCJ50CT001 | #5 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 117.7767 | ok
142 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1M_LP5LVL.AO163103.OUT | 1M_LP5LVL:AO163103.OUT | 10LCJ51AA101XB11 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
143 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 | F296S-J0201-09(2/2) | OPC.AW1002.1MAI.AI162105.PNT | 1MAI:AI162105.PNT | 10LCJ51AA101XB12 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.57422 | no
144 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-09(1/2) | OPC.AW1002.1NAI.AI172203.PNT | 1NAI:AI172203.PNT | 10LAA40AA501XB12 | DEARATOR EXHAUST MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 6.5684 | ok
145 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-09(1/2) | OPC.AW1002.1NAI.AI172107.PNT | 1NAI:AI172107.PNT | 10LAA40AA502XB12 | DEARATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 7.9785 | ok
146 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-09(1/2) | OPC.AW1002.1NAI.AI172108.PNT | 1NAI:AI172108.PNT | 10LAA40AA503XB12 | DEARATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 7.3691 | ok
147 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI160405.PNT | 1MAI:AI160405.PNT | 10LAA40CL201 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2465.2932 | ok
148 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI160505.PNT | 1MAI:AI160505.PNT | 10LAA40CL202 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2469.3127 | ok
149 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI160605.PNT | 1MAI:AI160605.PNT | 10LAA40CL203 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2462.4221 | ok
150 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI210201.PNT | 1QAI:AI210201.PNT | 10LAA40CT001 | DEARATOR TANK TEMP | RTD | 0 | 500 | C | [6 empty] | 143.1382 | ok
151 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-06 | OPC.AW1002.1M_DAPRESS.AO162402.OUT | 1M_DAPRESS:AO162402.OUT | 10LBG17AA101XB11 | AUXILIARY HEADER TO DEARATOR SUPPLY STEAM CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
152 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-06 | OPC.AW1002.1MAI.AI161402.PNT | 1MAI:AI161402.PNT | 10LBG17AA101XB12 | AUXILIARY HEADER TO DEARATOR SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.3555 | ok
153 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI172105.PNT | 1NAI:AI172105.PNT | 10LBS40AA005XB12 | AUXILIARY STEAM HEADER TO DEARATOR INCHING MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 13.2539 | ok
154 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI173801.PNT | 1NAI:AI173801.PNT | 10LBS40CP201 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (TURBINE SIDE) | AI | 0 | 1 | MPa | [6 empty] | 0.50072 | ok
155 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI173802.PNT | 1NAI:AI173802.PNT | 10LBS40CP202 | #4 EXTRACTION STEAM PIPE 1 PRESS 2 (TURBINE SIDE) | AI | 0 | 1 | MPa | [6 empty] | 0.50004 | ok
156 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1MAI.AI160403.PNT | 1MAI:AI160403.PNT | 10LBS40CP203 | DEARATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.31573 | ok
157 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1MAI.AI160503.PNT | 1MAI:AI160503.PNT | 10LBS40CP204 | DEARATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.31648 | ok
158 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211305.PNT | 1QAI:AI211305.PNT | 10LBS40CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 600 | C | [6 empty] | 337.1784 | ok
159 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211306.PNT | 1QAI:AI211306.PNT | 10LBS40CT002 | #4 EXTRACTION STEAM PIPE 1 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 266.4918 | ok
160 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211406.PNT | 1QAI:AI211406.PNT | 10LBS40CT003 | #4 EXTRACTION STEAM PIPE 1 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 325.6064 | ok
161 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211501.PNT | 1QAI:AI211501.PNT | 10LBS40CT004 | #4 EXTRACTION STEAM PIPE TEMP (DEAERATOR SIDE) | TC | 0 | 600 | C | [6 empty] | 336.5603 | ok
162 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI172106.PNT | 1NAI:AI172106.PNT | 10LBS43AA001XB12 | OPEN #4 EXTRACTION STEAM PIPE TO DEARATOR INCHING MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 6.5762 | ok
163 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173103.PNT | 1NAI:AI173103.PNT | 10LCA10AA004XB12 | DEARATOR LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.16797 | no
164 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1M_DALVL.AO162406.OUT | 1M_DALVL:AO162406.OUT | 10LCA10AA101XB11 | DEARATOR WATER LEVEL CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10.8043 | ok
165 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161407.PNT | 1MAI:AI161407.PNT | 10LCA10AA101XB12 | DEARATOR WATER LEVEL CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 10.4238 | ok
166 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1M_DALVL.AO162501.OUT | 1M_DALVL:AO162501.OUT | 10LCA10AA102XB11 | DEARATOR WATER LEVEL CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
167 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 16 | DEAERATOR #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161502.PNT | 1MAI:AI161502.PNT | 10LCA10AA102XB12 | DEARATOR WATER LEVEL CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 0.26953 | ok
168 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_FLOW.COND1OUT.PNT | 1M_FLOW:COND1OUT.PNT | 10LCA40CF201 | CONDENSATE WATER FLOW | AI | 0 | 1000 | t/h | [6 empty] | 479.9478 | ok
169 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_FLOW.COND2OUT.PNT | 1M_FLOW:COND2OUT.PNT | 10LCA40CF202 | CONDENSATE WATER FLOW | AI | 0 | 1000 | t/h | [6 empty] | 479.3341 | ok
170 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173102.PNT | 1NAI:AI173102.PNT | 10LCA42AA001XB12 | OPEN CONDENSATE RECIRCULATING CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.32617 | no
171 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_CNREC.AO162405.OUT | 1M_CNREC:AO162405.OUT | 10LCA42AA101XB11 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 71 | ok
172 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_CNREC.ZT161602.PNT | 1M_CNREC:ZT161602.PNT | 10LCA42AA101XB12 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 71.1074 | ok
173 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 17 | CONDENSATE PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_FLOW.CNRAIN.PNT | 1M_FLOW:CNRAIN.PNT | 10LCA42CF201 | CONDENSATE WATER RECIRCULATING FLOW | AI | 0 | 1000 | t/h | [6 empty] | 726.9939 | ok
174 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1M_CNMKUP.AO162408.OUT | 1M_CNMKUP:AO162408.OUT | 10LCA21AA101XB91 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
175 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173101.PNT | 1NAI:AI173101.PNT | 10LCA21AA101XB92C1 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.24219 | ok | REVISI TAG
176 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173101.PNT | 1NAI:AI173101.PNT | 10LCA21AA101XB92 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.24219 | ok
177 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1M_CNMKUP.AO162506.OUT | 1M_CNMKUP:AO162506.OUT | 10LCD10AA101XB11 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | -2 | no
178 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161604.PNT | 1MAI:AI161604.PNT | 10LCD10AA101XB12 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.78516 | ok
179 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1M_CNLVL.AO162507.OUT | 1M_CNLVL:AO162507.OUT | 10LCP10AA101XB11 | CONDENSER WATER LEVEL CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 2.323 | ok
180 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161605.PNT | 1MAI:AI161605.PNT | 10LCP10AA101XB12 | CONDENSER WATER LEVEL CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 3.5645 | ok
181 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173108.PNT | 1NAI:AI173108.PNT | 10LCP10AP001XB13 | CONDENSATE MAKE-UP WATER PUMP CURRENT | AI | 0 | 100 | A | [6 empty] | 0 | ok
182 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1Q_FLOW.CNMAKEAIN.PNT | 1Q_FLOW:CNMAKEAIN.PNT | 10LCP10CF201 | CONDENSATE MAKE-UP WATER FLOW | AI | 0 | 80 | t/h | [6 empty] | 1.425 | ok
183 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161406.PNT | 1MAI:AI161406.PNT | 10LCP10CL201 | CONDENSATE MAKE-UP TANK LEVEL | AI | 0 | 4500 | mm |  | 500 | 800 | 3200 | 3400 |  | 2792.2852 | ok
184 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1QAI.AI213102.PNT | 1QAI:AI213102.PNT | 10LCP10CP201 | CONDENSATE MAKE-UP WATER PUMP OUTLET PRESS | AI | 0 | 0.8 | MPa | [6 empty] | 0.1 | ok
185 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173104.PNT | 1NAI:AI173104.PNT | 10LCP11AA001XB12 | CONDENSER WATER LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.54883 | ok
186 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 18 | CONDENSATE MAKE-UP SYSYEM #1 | F296S-J0201-07 | OPC.AW1002.1NAI.AI173106.PNT | 1NAI:AI173106.PNT | 10LCP20AP001XB13 | BOILER STARTUP FEEDWATER PUMP CURRENT | AI | 0 | 200 | A | [6 empty] | 0 | ok
187 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 19 | PRIMING PUMP #1 | F296S-J0201-15 | OPC.AW1002.1NAI.AI173208.PNT | 1NAI:AI173208.PNT | 10MAJ30AP001XB13 | CONDENSER WATER BOX VACUUM PUMP CURRENT | AI | 0 | 25 | A |  |  |  | 15.6 |  |  | -0.083984 | no
188 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230601.PNT | 1RAI:AI230601.PNT | 10LCT10CT001 | NO.1 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 103.6717 | ok
189 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230701.PNT | 1RAI:AI230701.PNT | 10LCT10CT002 | NO.2 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 40.6758 | ok
190 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230602.PNT | 1RAI:AI230602.PNT | 10LCT10CT003 | NO.3 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 215.9056 | ok
191 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230702.PNT | 1RAI:AI230702.PNT | 10LCT10CT004 | NO.4 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 368.0111 | ok
192 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230603.PNT | 1RAI:AI230603.PNT | 10LCT10CT005 | NO.5 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 177.3537 | ok
193 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230703.PNT | 1RAI:AI230703.PNT | 10LCT10CT006 | NO.6 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 43.9129 | ok
194 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 20 | DRAIN FLASH TANK 1 #1 | F296S-J0201-12 | OPC.AW1002.1RAI.AI230604.PNT | 1RAI:AI230604.PNT | 10LCT10CT007 | NO.7 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 180 | C | [6 empty] | 36.3542 | ok
195 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173804.PNT | 1NAI:AI173804.PNT | 10PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.4 | MPa | [6 empty] | 0.031688 | ok
196 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1RAI.AI230101.PNT | 1RAI:AI230101.PNT | 10PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.5512 | ok
197 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172406.PNT | 1NAI:AI172406.PNT | 10PCC21AP001XB13 | CIRCULATING-WATER BOOSTER PUMP A CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | -2.125 | no
198 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI171103.PNT | 1NAI:AI171103.PNT | 10PCC21CT001 | CIRCULATING WATER BOOSTER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 48.4799 | ok
199 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173402.PNT | 1NAI:AI173402.PNT | 10PCC21CT002 | CIRCULATING WATER BOOSTER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 38.464 | ok
200 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI171104.PNT | 1NAI:AI171104.PNT | 10PCC21CT003 | CIRCULATING WATER BOOSTER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
201 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173403.PNT | 1NAI:AI173403.PNT | 10PCC21CT004 | CLOSED CIRCULATING WATER BOOSTER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
202 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI171105.PNT | 1NAI:AI171105.PNT | 10PCC21CT005 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.1 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
203 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173404.PNT | 1NAI:AI173404.PNT | 10PCC21CT006 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.2 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
204 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI171106.PNT | 1NAI:AI171106.PNT | 10PCC21CT007 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.3 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
205 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173405.PNT | 1NAI:AI173405.PNT | 10PCC21CT008 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.4 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
206 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI171107.PNT | 1NAI:AI171107.PNT | 10PCC21CT009 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.5 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
207 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173406.PNT | 1NAI:AI173406.PNT | 10PCC21CT010 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.6 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
208 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI172303.PNT | 1NAI:AI172303.PNT | 10PCC22AP001XB13 | CIRCULATING-WATER BOOSTER PUMP B CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | 0 | ok
209 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173407.PNT | 1NAI:AI173407.PNT | 10PCC22CT001 | CIRCULATING WATER BOOSTER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 27.253 | ok
210 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173408.PNT | 1NAI:AI173408.PNT | 10PCC22CT002 | CIRCULATING WATER BOOSTER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 27.7077 | ok
211 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173301.PNT | 1NAI:AI173301.PNT | 10PCC22CT003 | CIRCULATING WATER BOOSTER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
212 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173302.PNT | 1NAI:AI173302.PNT | 10PCC22CT004 | CLOSED CIRCULATING WATER BOOSTER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
213 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173303.PNT | 1NAI:AI173303.PNT | 10PCC22CT005 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.1 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
214 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173304.PNT | 1NAI:AI173304.PNT | 10PCC22CT006 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.2 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
215 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173305.PNT | 1NAI:AI173305.PNT | 10PCC22CT007 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.3 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
216 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173306.PNT | 1NAI:AI173306.PNT | 10PCC22CT008 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.4 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
217 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173307.PNT | 1NAI:AI173307.PNT | 10PCC22CT009 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.5 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
218 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173308.PNT | 1NAI:AI173308.PNT | 10PCC22CT010 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.6 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
219 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CWHE #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173201.PNT | 1NAI:AI173201.PNT | 10PCB31AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A SEA WATER SIDE OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.30859 | no
220 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CWHE #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173205.PNT | 1NAI:AI173205.PNT | 10PGA21AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A COOLING WATER INLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.48438 | no
221 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CWHE #1A | F296S-J0201-14 | OPC.AW1002.1RAI.AI231101.PNT | 1RAI:AI231101.PNT | 10PGA21CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.47327 | ok
222 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 3 | CWHE #1A | F296S-J0201-14 | OPC.AW1002.1RAI.AI230102.PNT | 1RAI:AI230102.PNT | 10PGA21CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.6034 | ok
223 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CWHE #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173202.PNT | 1NAI:AI173202.PNT | 10PCB32AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B SEA WATER SIDE OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.4473 | ok
224 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CWHE #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173206.PNT | 1NAI:AI173206.PNT | 10PGA22AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B COOLING WATER INLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.2129 | ok
225 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CWHE #1B | F296S-J0201-14 | OPC.AW1002.1RAI.AI231201.PNT | 1RAI:AI231201.PNT | 10PGA22CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.56128 | ok
226 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 4 | CWHE #1B | F296S-J0201-14 | OPC.AW1002.1RAI.AI230202.PNT | 1RAI:AI230202.PNT | 10PGA22CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.4735 | ok
227 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173203.PNT | 1NAI:AI173203.PNT | 10PGA11AA001XB12 | CLOSED CIRCULATING-WATER PUMP A OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.9199 | ok
228 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172407.PNT | 1NAI:AI172407.PNT | 10PGA11AP001XB13 | CLOSED CIRCULATING-WATER PUMP A CURRENT | AI | 0 | 200 | A |  |  |  | 32.5 |  |  | -0.027344 | no
229 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172707.PNT | 1NAI:AI172707.PNT | 10PGA11CT001 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 100 | C |  |  |  | 75 | 85 |  | 27.5128 | ok
230 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172805.PNT | 1NAI:AI172805.PNT | 10PGA11CT002 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 100 | C |  |  |  | 75 | 85 |  | 26.1877 | ok
231 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172806.PNT | 1NAI:AI172806.PNT | 10PGA11CT003 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 90 | 95 |  | 27.8116 | ok
232 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170101.PNT | 1NAI:AI170101.PNT | 10PGA11CT004 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 29.3445 | ok
233 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170102.PNT | 1NAI:AI170102.PNT | 10PGA11CT005 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.2146 | ok
234 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170201.PNT | 1NAI:AI170201.PNT | 10PGA11CT006 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.3055 | ok
235 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170103.PNT | 1NAI:AI170103.PNT | 10PGA11CT007 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.4484 | ok
236 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170202.PNT | 1NAI:AI170202.PNT | 10PGA11CT008 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.3055 | ok
237 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170104.PNT | 1NAI:AI170104.PNT | 10PGA11CT009 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.1496 | ok
238 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI170203.PNT | 1NAI:AI170203.PNT | 10PGA11CT010 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 28.9418 | ok
239 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 5 | CCWP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI173805.PNT | 1NAI:AI173805.PNT | 10PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 0.8 | MPa |  |  | 0.5 |  |  |  | 0.5617 | ok
240 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173204.PNT | 1NAI:AI173204.PNT | 10PGA12AA001XB12 | CLOSED CIRCULATING-WATER PUMP B OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.498 | ok
241 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI172304.PNT | 1NAI:AI172304.PNT | 10PGA12AP001XB13 | CLOSED CIRCULATING-WATER PUMP B CURRENT | AI | 0 | 200 | A |  |  |  | 32.5 |  |  | 29.4141 | ok
242 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170105.PNT | 1NAI:AI170105.PNT | 10PGA12CT001 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 80 | 85 |  | 45.2192 | ok
243 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170204.PNT | 1NAI:AI170204.PNT | 10PGA12CT002 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 80 | 85 |  | 31.9426 | ok
244 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170106.PNT | 1NAI:AI170106.PNT | 10PGA12CT003 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 49.5841 | ok
245 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170205.PNT | 1NAI:AI170205.PNT | 10PGA12CT004 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 36.8532 | ok
246 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170107.PNT | 1NAI:AI170107.PNT | 10PGA12CT005 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 90.7778 | ok
247 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170206.PNT | 1NAI:AI170206.PNT | 10PGA12CT006 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 77.6182 | ok
248 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI170207.PNT | 1NAI:AI170207.PNT | 10PGA12CT007 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 76.0853 | ok
249 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI171101.PNT | 1NAI:AI171101.PNT | 10PGA12CT008 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 74.6953 | ok
250 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI171102.PNT | 1NAI:AI171102.PNT | 10PGA12CT009 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 74.9941 | ok
251 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173401.PNT | 1NAI:AI173401.PNT | 10PGA12CT010 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 75.6955 | ok
252 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1NAI.AI172402.PNT | 1NAI:AI172402.PNT | 10PGA31AA002XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 97.2793 | ok
253 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI231202.PNT | 1RAI:AI231202.PNT | 10PGA31CP201 | TURBINE HOUSE COOLING WATER INLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.45632 | ok
254 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230204.PNT | 1RAI:AI230204.PNT | 10PGA31CT001 | TURBINE HOUSE COOLING WATER INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.7463 | ok
255 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230105.PNT | 1RAI:AI230105.PNT | 10PGA31CT002 | TURBINE HOUSER COOLING RETURN WATER TEMP 1 | RTD | 0 | 50 | C | [6 empty] | 26.2444 | ok
256 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230106.PNT | 1RAI:AI230106.PNT | 10PGA31CT004 | TURBINE HOUSER COOLING RETURN WATER TEMP 2 | RTD | 0 | 50 | C | [6 empty] | 26.9152 | ok
257 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1NAI.AI172405.PNT | 1NAI:AI172405.PNT | 10PGA33AA001XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 96.7598 | ok
258 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI231102.PNT | 1RAI:AI231102.PNT | 10PGA40CP201 | BOILER HOUSE COOLING WATER MAIN PIPE INLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.46518 | ok
259 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230103.PNT | 1RAI:AI230103.PNT | 10PGA40CT001 | BOILER HOUSE COOLING WATER MAIN PIPE INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.5515 | ok
260 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1NAI.AI172401.PNT | 1NAI:AI172401.PNT | 10PGA50AA001XB12 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 93.4668 | ok
261 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230203.PNT | 1RAI:AI230203.PNT | 10PGA50CT001 | BOILER HOUSE COOLING RENTURN WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 27.214 | ok
262 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230104.PNT | 1RAI:AI230104.PNT | 10PGA50CT002 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE TEMP | RTD | 0 | 50 | C | [6 empty] | 28.695 | ok
263 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | F296S-J0201-07 | OPC.AW1002.1M_CWEXTNK.AO162505.OUT | 1M_CWEXTNK:AO162505.OUT | 10LCE18AA101XB11 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAN | AO | 0 | 100 | % | [6 empty] | 0 | ok
264 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161507.PNT | 1MAI:AI161507.PNT | 10LCE18AA101XB12 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.18555 | ok
265 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 8 | CW EXPANSION TANK #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI231401.PNT | 1RAI:AI231401.PNT | 10PGA10CL201 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK LEVEL | AI | 0 | 2500 | mm |  | 540 | 940 | 1600 | 1800 |  | 1898.291 | ok
266 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #1A - BOOSTER PUMP | F296S-J0201-08 | OPC.AW1002.1OAI.AI192102.PNT | 1OAI:AI192102.PNT | 10LAC11AP001XB13 | BOOSTER PUMP FOR T-BFP A CURRENT | AI | 0 | 400 | A |  |  |  | 237 |  |  | 152.2109 | ok
267 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #1A - BOOSTER PUMP | F296S-J0201-31 | OPC.AW1002.1OAI.AI193106.PNT | 1OAI:AI193106.PNT | 10LAC11CT001 | BOOSTER PUMP FOR T-BFP A DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 41.3739 | ok
268 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 1 | T-BFP #1A - BOOSTER PUMP | F296S-J0201-31 | OPC.AW1002.1OAI.AI193107.PNT | 1OAI:AI193107.PNT | 10LAC11CT002 | BOOSTER PUMP FOR T-BFP A FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 47.1678 | ok
269 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-08 | OPC.AW1002.1M_TFPAREC.AO162603.OUT | 1M_TFPAREC:AO162603.OUT | 10LAB11AA101XB11 | T-BFP A MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
270 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-08 | OPC.AW1002.1MAI.AI161607.PNT | 1MAI:AI161607.PNT | 10LAB11AA101XB12 | T-BFP A MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.0019531 | ok
271 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-08 | OPC.AW1002.1M_FLOW.BFPAAIN.PNT | 1M_FLOW:BFPAAIN.PNT | 10LAB11CF201 | T-BFP A INLET WATER FLOW | AI | 0 | 800 | t/h |  | 120 | 140 |  |  |  | 307.5159 | ok
272 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-08 | OPC.AW1002.1OAI.AI193502.PNT | 1OAI:AI193502.PNT | 10LAB11CP201 | T-BFP A INLET WATER PRESS | AI | 0 | 2 | MPa |  | 1.25 | 1.4 |  |  |  | 1.0839 | ok
273 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-08 | OPC.AW1002.1QAI.AI212704.PNT | 1QAI:AI212704.PNT | 10LAB11CP202 | T-BFP A OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 13.4346 | ok
274 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193204.PNT | 1OAI:AI193204.PNT | 10LAC11CT003 | T-BFP A INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 49.8179 | ok
275 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193205.PNT | 1OAI:AI193205.PNT | 10LAC11CT004 | T-BFP A OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 56.0665 | ok
276 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193206.PNT | 1OAI:AI193206.PNT | 10LAC11CT005 | T-BFP A THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 46.8431 | ok
277 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193207.PNT | 1OAI:AI193207.PNT | 10LAC11CT006 | T-BFP A THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 51.5327 | ok
278 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193301.PNT | 1OAI:AI193301.PNT | 10LAC11CT007 | T-BFP A INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 36.6063 | ok
279 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193302.PNT | 1OAI:AI193302.PNT | 10LAC11CT008 | T-BFP A OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 38.503 | ok
280 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193303.PNT | 1OAI:AI193303.PNT | 10LAC11CT009 | T-BFP A WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 131.6376 | ok
281 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193304.PNT | 1OAI:AI193304.PNT | 10LAC11CT010 | T-BFP A WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 128.7525 | ok
282 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193305.PNT | 1OAI:AI193305.PNT | 10LAC11CT011 | T-BFP A WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 135.2308 | ok
283 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-31 | OPC.AW1002.1OAI.AI193306.PNT | 1OAI:AI193306.PNT | 10LAC11CT012 | T-BFP A WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 132.7463 | ok
284 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1RAI.AI231601.PNT | 1RAI:AI231601.PNT | 10LAC11CY201X | T-BFP A WATER INLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
285 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1RAI.AI231701.PNT | 1RAI:AI231701.PNT | 10LAC11CY202Y | T-BFP A WATER INLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
286 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1RAI.AI231602.PNT | 1RAI:AI231602.PNT | 10LAC11CY203X | T-BFP A WATER OUTLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
287 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1RAI.AI231702.PNT | 1RAI:AI231702.PNT | 10LAC11CY204Y | T-BFP A WATER OUTLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
288 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-04 | OPC.AW1002.1Q_FLOW.BFPSTMAIN.PNT | 1Q_FLOW:BFPSTMAIN.PNT | 10LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | t/h | [6 empty] | 3.7717 | ok
289 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1Q_FLOW.BFPSTMAAIN.PNT | 1Q_FLOW:BFPSTMAAIN.PNT | 10LBR21CF201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30 | t/h | [6 empty] | 9.9971 | ok
290 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI212407.PNT | 1QAI:AI212407.PNT | 10LBR21CP201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.78367 | ok
291 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI211601.PNT | 1QAI:AI211601.PNT | 10LBR21CT001 | BFP TURBINE A INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 600 | C | [6 empty] | 311.3318 | ok
292 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI212601.PNT | 1QAI:AI212601.PNT | 10LBR31CP201 | BFP TURBINE A EXHAUST STEAM PRESS | AI | -100 | 100 | KPa |  |  |  | -67.71 | -47.45 |  | -88.8789 | ok
293 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1NAI.AI172503.PNT | 1NAI:AI172503.PNT | 10LBR31CT001 | BFP TURBINE A EXHAUST STEAM TEMP | RTD | 0 | 200 | C | [6 empty] | 39.7111 | ok
294 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1NAI.AI172504.PNT | 1NAI:AI172504.PNT | 10LBR31CT002 | BFP TURBINE A EXHAUST STEAM TEMP 1 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 39.9579 | ok
295 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1NAI.AI172601.PNT | 1NAI:AI172601.PNT | 10LBR31CT003 | BFP TURBINE A EXHAUST STEAM TEMP 2 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 39.828 | ok
296 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI212307.PNT | 1QAI:AI212307.PNT | 10LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.504 | ok
297 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI211405.PNT | 1QAI:AI211405.PNT | 10LBS41CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 342.1165 | ok
298 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI211307.PNT | 1QAI:AI211307.PNT | 10LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 272.6427 | ok
299 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-05 | OPC.AW1002.1QAI.AI211407.PNT | 1QAI:AI211407.PNT | 10LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 266.0258 | ok
300 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1OAI.AI192103.PNT | 1OAI:AI192103.PNT | 10MAV50AP101XB13 | BFP TURBINE A LUBE-OIL SYSTEM MAIN OIL PUMP A CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | -0.048047 | no
301 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1OAI.AI192104.PNT | 1OAI:AI192104.PNT | 10MAV50AP102XB13 | BFP TURBINE A LUBE-OIL SYSTEM MAIN OIL PUMP B CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | 20.0824 | ok
302 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1OAI.AI192105.PNT | 1OAI:AI192105.PNT | 10MAV50AP103XB13 | BFP TURBINE A LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 40.8 |  |  | 0.63672 | ok
303 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI213405.PNT | 1QAI:AI213405.PNT | 10MAV50CL201 | BFP TURBINE A LUBE-OIL TANK LEVEL | AI | 0 | 1050 | mm |  | 195 | 322 | 525 | 1050 |  | 424.6523 | ok
304 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1QAI.AI210406.PNT | 1QAI:AI210406.PNT | 10MAV50CT001 | BFP TURBINE A LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 46.5443 | ok
305 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1QAI.AI210506.PNT | 1QAI:AI210506.PNT | 10MAV50CT002 | BFP TURBINE A LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 33.6574 | ok
306 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1OAI.AI192503.PNT | 1OAI:AI192503.PNT | 10MAV50CT003 | BFP TURBINE A LUBE-OIL TANK TEMP. | RTD | 0 | 100 | C | [6 empty] | 46.5053 | ok
307 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1OAI.AI192504.PNT | 1OAI:AI192504.PNT | 10MAV50CT009 | BFP TURBINE A SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 46.2844 | ok
308 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1OAI.AI192505.PNT | 1OAI:AI192505.PNT | 10MAV50CT010 | BFP TURBINE A THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 46.5702 | ok
309 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F290S-J0201-20 | OPC.AW1002.1OAI.AI192506.PNT | 1OAI:AI192506.PNT | 10MAV50CT011 | BFP TURBINE A #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | C | [6 empty] | 42.0105 | ok
310 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1OAI.AI191403.PNT | 1OAI:AI191403.PNT | 10MAV50GC001AI01 | BFP TURBINE A TURNING GEAR CURRENT | AI | 0 | 50 | A | [6 empty] | 0 | ok
311 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1MAI.AI162206.PNT | 1MAI:AI162206.PNT | 10MEHADCS01 | BFP TURBINE A SPEED SET POINT SIGNAL | AI | 0 | 100 | % | [6 empty] | 37.4453 | ok
312 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231706.PNT | 1RAI:AI231706.PNT | 10MTSIADCS01 | BFP TURBINE A SPEED (4~20mA) | AI | 0 | 10000 | rpm | [6 empty] | 4000.0547 | ok
313 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231607.PNT | 1RAI:AI231607.PNT | 10MTSIADCS02 | BFP TURBINE A NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 40.4824 | ok
314 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231707.PNT | 1RAI:AI231707.PNT | 10MTSIADCS03 | BFP TURBINE A NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 42.832 | ok
315 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231801.PNT | 1RAI:AI231801.PNT | 10MTSIADCS04 | BFP TURBINE A NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 29.124 | ok
316 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI232101.PNT | 1RAI:AI232101.PNT | 10MTSIADCS05 | BFP TURBINE A NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 29.8682 | ok
317 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231802.PNT | 1RAI:AI231802.PNT | 10MTSIADCS06 | BFP TURBINE A NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 22.7695 | ok
318 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI232102.PNT | 1RAI:AI232102.PNT | 10MTSIADCS07 | BFP TURBINE A NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 24.7676 | ok
319 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231803.PNT | 1RAI:AI231803.PNT | 10MTSIADCS08 | BFP TURBINE A NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 10.3359 | ok
320 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI232103.PNT | 1RAI:AI232103.PNT | 10MTSIADCS09 | BFP TURBINE A NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 9.8818 | ok
321 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231804.PNT | 1RAI:AI231804.PNT | 10MTSIADCS10 | BFP TURBINE A AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | -0.14309 | ok
322 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI232104.PNT | 1RAI:AI232104.PNT | 10MTSIADCS11 | BFP TURBINE A AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | -0.12034 | ok
323 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-K0611-02 | OPC.AW1002.1RAI.AI231805.PNT | 1RAI:AI231805.PNT | 10MTSIADCS12 | BFP TURBINE A ECCENTRICTIY (4~20mA) | AI | 0 | 100 | um |  |  |  | 30 |  |  | 0.044922 | ok
324 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-14 | OPC.AW1002.1NAI.AI172404.PNT | 1NAI:AI172404.PNT | 10PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 97.1602 | ok
325 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-14 | OPC.AW1002.1RAI.AI230205.PNT | 1RAI:AI230205.PNT | 10PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.9542 | ok
326 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210407.PNT | 1QAI:AI210407.PNT | 10XAC11CT001 | BFP TURBINE A POSITION THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 49.6361 | ok
327 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210507.PNT | 1QAI:AI210507.PNT | 10XAC11CT002 | BFP TURBINE A POSITION THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 46.1415 | ok
328 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210601.PNT | 1QAI:AI210601.PNT | 10XAC11CT003 | BFP TURBINE A WORK THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 49.2074 | ok
329 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210701.PNT | 1QAI:AI210701.PNT | 10XAC11CT004 | BFP TURBINE A WORK THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 54.4816 | ok
330 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210602.PNT | 1QAI:AI210602.PNT | 10XAC11CT005 | BFP TURBINE A SUPPORT PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 65.9655 | ok
331 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210702.PNT | 1QAI:AI210702.PNT | 10XAC11CT006 | BFP TURBINE A SUPPORT PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 60.3015 | ok
332 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210603.PNT | 1QAI:AI210603.PNT | 10XAC11CT007 | BFP TURBINE A #2 BEARING PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 61.016 | ok
333 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI210703.PNT | 1QAI:AI210703.PNT | 10XAC11CT008 | BFP TURBINE A #2 BEARING PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 66.2383 | ok
334 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A | F296S-J0201-20 | OPC.AW1002.1QAI.AI212204.PNT | 1QAI:AI212204.PNT | 10XAC11CT009 | FRONT CYLINDER METAL WALL TEMP | TC | 0 | 600 | C | [6 empty] | 197.7877 | ok
335 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #1B - BOOSTER PUMP | F296S-J0201-08 | OPC.AW1002.1PAI.AI202102.PNT | 1PAI:AI202102.PNT | 10LAC12AP001XB13 | BOOSTER PUMP FOR T-BFP B CURRENT | AI | 0 | 400 | A |  |  |  | 237 |  |  | 159.2031 | ok
336 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #1B - BOOSTER PUMP | F296S-J0201-32 | OPC.AW1002.1PAI.AI202601.PNT | 1PAI:AI202601.PNT | 10LAC12CT001 | BOOSTER PUMP FOR T-BFP B DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 49.0905 | ok
337 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 3 | T-BFP #1B - BOOSTER PUMP | F296S-J0201-32 | OPC.AW1002.1PAI.AI202602.PNT | 1PAI:AI202602.PNT | 10LAC12CT002 | BOOSTER PUMP FOR T-BFP B FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 47.8303 | ok
338 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-08 | OPC.AW1002.1M_TFPBREC.AO162701.OUT | 1M_TFPBREC:AO162701.OUT | 10LAB12AA101XB11 | T-BFP B MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok | REVISI TAG
339 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-08 | OPC.AW1002.1MAI.AI161701.PNT | 1MAI:AI161701.PNT | 10LAB12AA101XB12 | T-BFP B MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.19336 | ok
340 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-08 | OPC.AW1002.1M_FLOW.BFPBAIN.PNT | 1M_FLOW:BFPBAIN.PNT | 10LAB12CF201 | T-BFP B INLET WATER FLOW | AI | 0 | 800 | t/h |  | 120 | 140 |  |  |  | 323.002 | ok
341 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-08 | OPC.AW1002.1PAI.AI203601.PNT | 1PAI:AI203601.PNT | 10LAB12CP201 | T-BFP B INLET WATER PRESS | AI | 0 | 2 | MPa |  | 1.25 | 1.4 |  |  |  | 1.0412 | ok
342 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-08 | OPC.AW1002.1QAI.AI213104.PNT | 1QAI:AI213104.PNT | 10LAB12CP202 | T-BFP B OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 13.4448 | ok
343 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202603.PNT | 1PAI:AI202603.PNT | 10LAC12CT003 | T-BFP B INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 51.2729 | ok
344 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202604.PNT | 1PAI:AI202604.PNT | 10LAC12CT004 | T-BFP B OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 51.6367 | ok
345 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202605.PNT | 1PAI:AI202605.PNT | 10LAC12CT005 | T-BFP B THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 43.1796 | ok
346 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202606.PNT | 1PAI:AI202606.PNT | 10LAC12CT006 | T-BFP B THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 44.3099 | ok
347 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202607.PNT | 1PAI:AI202607.PNT | 10LAC12CT007 | T-BFP B INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 34.9435 | ok
348 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202701.PNT | 1PAI:AI202701.PNT | 10LAC12CT008 | T-BFP B OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 49.0125 | ok
349 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202702.PNT | 1PAI:AI202702.PNT | 10LAC12CT009 | T-BFP B WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 131.5308 | ok
350 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202703.PNT | 1PAI:AI202703.PNT | 10LAC12CT010 | T-BFP B WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 130.529 | ok
351 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202704.PNT | 1PAI:AI202704.PNT | 10LAC12CT011 | T-BFP B WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 129.2734 | ok
352 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-32 | OPC.AW1002.1PAI.AI202705.PNT | 1PAI:AI202705.PNT | 10LAC12CT012 | T-BFP B WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 133.6679 | ok
353 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1RAI.AI231603.PNT | 1RAI:AI231603.PNT | 10LAC12CY201X | T-BFP B WATER INLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
354 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1RAI.AI231703.PNT | 1RAI:AI231703.PNT | 10LAC12CY202Y | T-BFP B WATER INLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
355 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1RAI.AI231604.PNT | 1RAI:AI231604.PNT | 10LAC12CY203X | T-BFP B WATER OUTLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
356 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1RAI.AI231704.PNT | 1RAI:AI231704.PNT | 10LAC12CY204Y | T-BFP B WATER OUTLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
357 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1Q_FLOW.BFPSTMBAIN.PNT | 1Q_FLOW:BFPSTMBAIN.PNT | 10LBR22CF201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30 | t/h | [6 empty] | 10.6005 | ok
358 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI212501.PNT | 1QAI:AI212501.PNT | 10LBR22CP201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.49078 | ok
359 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI211502.PNT | 1QAI:AI211502.PNT | 10LBR22CT001 | BFP TURBINE B INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 600 | C | [6 empty] | 331.5627 | ok
360 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI212502.PNT | 1QAI:AI212502.PNT | 10LBR32CP201 | BFP TURBINE B EXHAUST STEAM PRESS | AI | -100 | 100 | KPa |  |  |  | -67.71 | -47.45 |  | -88.8164 | ok
361 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1NAI.AI172505.PNT | 1NAI:AI172505.PNT | 10LBR32CT001 | BFP TURBINE B EXHAUST STEAM TEMP | RTD | 0 | 200 | C | [6 empty] | 39.7631 | ok
362 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1NAI.AI172506.PNT | 1NAI:AI172506.PNT | 10LBR32CT002 | BFP TURBINE B EXHAUST STEAM TEMP 1 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 39.5942 | ok
363 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1NAI.AI172602.PNT | 1NAI:AI172602.PNT | 10LBR32CT003 | BFP TURBINE B EXHAUST STEAM TEMP 2 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 40.5685 | ok
364 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202103.PNT | 1PAI:AI202103.PNT | 10MAV60AP101XB13 | BFP TURBINE B LUBE-OIL SYSTEM MAIN OIL PUMP A CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | 0.0082031 | ok
365 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202104.PNT | 1PAI:AI202104.PNT | 10MAV60AP102XB13 | BFP TURBINE B LUBE-OIL SYSTEM MAIN OIL PUMP B CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | 20.7797 | ok
366 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202105.PNT | 1PAI:AI202105.PNT | 10MAV60AP103XB13 | BFP TURBINE B LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 40.8 |  |  | -0.09668 | no
367 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI213306.PNT | 1QAI:AI213306.PNT | 10MAV60CL201 | BFP TURBINE B LUBE-OIL TANK LEVEL | AI | 0 | 1050 | mm |  | 195 | 322 | 525 | 1050 |  | 466.9102 | ok
368 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210604.PNT | 1QAI:AI210604.PNT | 10MAV60CT001 | BFP TURBINE B LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 42.8419 | ok
369 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210705.PNT | 1QAI:AI210705.PNT | 10MAV60CT002 | BFP TURBINE B LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 32.1895 | ok
370 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202505.PNT | 1PAI:AI202505.PNT | 10MAV60CT003 | BFP TURBINE B LUBE-OIL TANK TEMP. | RTD | 0 | 100 | C | [6 empty] | 42.738 | ok
371 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202506.PNT | 1PAI:AI202506.PNT | 10MAV60CT009 | BFP TURBINE B SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 42.1144 | ok
372 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202503.PNT | 1PAI:AI202503.PNT | 10MAV60CT010 | BFP TURBINE B THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 43.6473 | ok
373 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202504.PNT | 1PAI:AI202504.PNT | 10MAV60CT011 | BFP TURBINE B #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | C | [6 empty] | 44.6216 | ok
374 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1PAI.AI202804.PNT | 1PAI:AI202804.PNT | 10MAV60GC001AI01 | BFP TURBINE B TURNING GEAR CURRENT | AI | 0 | 50 | A | [6 empty] | -0.28125 | no
375 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1MAI.AI162305.PNT | 1MAI:AI162305.PNT | 10MEHBDCS01 | BFP TURBINE B SPEED SET POINT SIGNAL | AI | 0 | 100 | % | [6 empty] | 37.5215 | ok
376 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1MEHB.BSPDLOG1.RO01 | 1MEHB:BSPDLOG1.RO01 | 10MTSIBDCS01 | BFP TURBINE B SPEED (4~20mA) | AI | 0 | 10000 | rpm | [6 empty] | 4004.0039 | ok
377 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI231806.PNT | 1RAI:AI231806.PNT | 10MTSIBDCS02 | BFP TURBINE B NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 22.3389 | ok
378 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232106.PNT | 1RAI:AI232106.PNT | 10MTSIBDCS03 | BFP TURBINE B NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 21.0352 | ok
379 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI231807.PNT | 1RAI:AI231807.PNT | 10MTSIBDCS04 | BFP TURBINE B NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 13.3242 | ok
380 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232107.PNT | 1RAI:AI232107.PNT | 10MTSIBDCS05 | BFP TURBINE B NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 12.5684 | ok
381 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232201.PNT | 1RAI:AI232201.PNT | 10MTSIBDCS06 | BFP TURBINE B NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 19.9512 | ok
382 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232301.PNT | 1RAI:AI232301.PNT | 10MTSIBDCS07 | BFP TURBINE B NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 19.4502 | ok
383 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232202.PNT | 1RAI:AI232202.PNT | 10MTSIBDCS08 | BFP TURBINE B NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 13.5791 | ok
384 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232302.PNT | 1RAI:AI232302.PNT | 10MTSIBDCS09 | BFP TURBINE B NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 35.3965 | ok
385 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232203.PNT | 1RAI:AI232203.PNT | 10MTSIBDCS10 | BFP TURBINE B AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | -0.027375 | ok
386 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232303.PNT | 1RAI:AI232303.PNT | 10MTSIBDCS11 | BFP TURBINE B AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | -0.0355 | ok
387 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-K0611-03 | OPC.AW1002.1RAI.AI232204.PNT | 1RAI:AI232204.PNT | 10MTSIBDCS12 | BFP TURBINE B ECCENTRICTIY (4~20mA) | AI | 0 | 100 | um |  |  |  | 30 |  |  | 0.056641 | ok
388 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210605.PNT | 1QAI:AI210605.PNT | 10XAC12CT001 | BFP TURBINE B POSITION THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 41.9455 | ok
389 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210706.PNT | 1QAI:AI210706.PNT | 10XAC12CT002 | BFP TURBINE B POSITION THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 42.4911 | ok
390 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210606.PNT | 1QAI:AI210606.PNT | 10XAC12CT003 | BFP TURBINE B WORK THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 43.8292 | ok
391 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210801.PNT | 1QAI:AI210801.PNT | 10XAC12CT004 | BFP TURBINE B WORK THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 43.9336 | ok
392 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210607.PNT | 1QAI:AI210607.PNT | 10XAC12CT005 | BFP TURBINE B SUPPORT PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 64.9002 | ok
393 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210802.PNT | 1QAI:AI210802.PNT | 10XAC12CT006 | BFP TURBINE B SUPPORT PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 56.833 | ok
394 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210707.PNT | 1QAI:AI210707.PNT | 10XAC12CT007 | BFP TURBINE B #2 BEARING PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 58.9504 | ok
395 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI210803.PNT | 1QAI:AI210803.PNT | 10XAC12CT008 | BFP TURBINE B #2 BEARING PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 64.2377 | ok
396 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-20 | OPC.AW1002.1QAI.AI212107.PNT | 1QAI:AI212107.PNT | 10XAC12CT009 | FRONT CYLINDER METAL WALL TEMP | TC | 0 | 600 | C | [6 empty] | 316.4155 | ok
397 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1M_BFPREC.AO162602.OUT | 1M_BFPREC:AO162602.OUT | 10LAH10AA101XB11 | M-BFP MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
398 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1MAI.AI161606.PNT | 1MAI:AI161606.PNT | 10LAH10AA101XB12 | M-BFP MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 100.0098 | no
399 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1M_FLOW.MBFPAIN.PNT | 1M_FLOW:MBFPAIN.PNT | 10LAH10CF201 | M-BFP INLET WATER FLOW | AI | 0 | 410 | t/h | [6 empty] | 0 | ok
400 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1OAI.AI193501.PNT | 1OAI:AI193501.PNT | 10LAH10CP201 | M-BFP INLET PRESS | AI | 0 | 2 | MPa |  | 0.95 | 1.1 |  |  |  | 0.53465 | ok
401 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI213103.PNT | 1QAI:AI213103.PNT | 10LAH10CP202 | M-BFP OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 0.54102 | ok
402 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1M_FWCNTL.AOUTC.OUT | 1M_FWCNTL:AOUTC.OUT | 10LAJ10AA101XB11 | M-BFP HYDRAULIC CUOPLE ACTUATOR CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
403 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1MAI.AI161702.PNT | 1MAI:AI161702.PNT | 10LAJ10AA101XB12 | M-BFP HYDRAULIC CUOPLE ACTUATOR POSITION | AI | 0 | 100 | % | [6 empty] | 56.1543 | ok
404 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-08 | OPC.AW1002.1OAI.AI191302.PNT | 1OAI:AI191302.PNT | 10LAJ10AP001XB13 | M-BFP GROUP CURRENT | AI | 0 | 600 | A |  |  |  | 363 |  |  | 0.12891 | ok
405 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI191405.PNT | 1OAI:AI191405.PNT | 10LAJ10AP003XB13 | M-BFP HYDRAULIC CUOPLE OIL PUMP CURRENT | AI | 0 | 25 | A | [6 empty] | 14.2266 | ok
406 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI191404.PNT | 1OAI:AI191404.PNT | 10LAJ10CS002 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min | [8 empty] | TIDAK DIPAKAI
407 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1QAI.AI213406.PNT | 1QAI:AI213406.PNT | 10LAJ10CS201 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min | [6 empty] | 3.5547 | ok
408 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192603.PNT | 1OAI:AI192603.PNT | 10LAJ10CT003 | M-BFP INLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 28.4221 | ok
409 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192604.PNT | 1OAI:AI192604.PNT | 10LAJ10CT004 | M-BFP OUTET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 28.2922 | ok
410 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192605.PNT | 1OAI:AI192605.PNT | 10LAJ10CT005 | M-BFP THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 28.2533 | ok
411 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192606.PNT | 1OAI:AI192606.PNT | 10LAJ10CT006 | M-BFP THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 28.4481 | ok
412 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192607.PNT | 1OAI:AI192607.PNT | 10LAJ10CT007 | M-BFP INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 28.4611 | ok
413 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192701.PNT | 1OAI:AI192701.PNT | 10LAJ10CT008 | M-BFP OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 27.3179 | ok
414 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192702.PNT | 1OAI:AI192702.PNT | 10LAJ10CT009 | M-BFP HYDRAULIC COUPLER B1 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.7469 | ok
415 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192703.PNT | 1OAI:AI192703.PNT | 10LAJ10CT010 | M-BFP HYDRAULIC COUPLER B2 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 24.8757 | ok
416 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192704.PNT | 1OAI:AI192704.PNT | 10LAJ10CT011 | M-BFP HYDRAULIC COUPLER B3 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 27.8635 | ok
417 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192705.PNT | 1OAI:AI192705.PNT | 10LAJ10CT012 | M-BFP HYDRAULIC COUPLER B4 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.6819 | ok
418 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192706.PNT | 1OAI:AI192706.PNT | 10LAJ10CT013 | M-BFP HYDRAULIC COUPLER B5 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.4221 | ok
419 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192707.PNT | 1OAI:AI192707.PNT | 10LAJ10CT014 | M-BFP HYDRAULIC COUPLER B6 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.3962 | ok
420 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192801.PNT | 1OAI:AI192801.PNT | 10LAJ10CT015 | M-BFP HYDRAULIC COUPLER B7 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.669 | ok
421 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192802.PNT | 1OAI:AI192802.PNT | 10LAJ10CT016 | M-BFP HYDRAULIC COUPLER B8 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.669 | ok
422 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192803.PNT | 1OAI:AI192803.PNT | 10LAJ10CT017 | M-BFP HYDRAULIC COUPLER B9 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 28.4481 | ok
423 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192804.PNT | 1OAI:AI192804.PNT | 10LAJ10CT018 | M-BFP HYDRAULIC COUPLER B10 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 29.3185 | ok
424 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192805.PNT | 1OAI:AI192805.PNT | 10LAJ10CT019 | M-BFP LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 180 | C |  |  |  | 55 | 60 |  | 28.2922 | ok
425 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192806.PNT | 1OAI:AI192806.PNT | 10LAJ10CT020 | M-BFP WORKING OIL COOLER INLET TEMP | RTD | 0 | 180 | C |  |  |  | 110 | 130 |  | 30.007 | ok
426 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192807.PNT | 1OAI:AI192807.PNT | 10LAJ10CT021 | M-BFP WORKING OIL COOLER OUTLET TEMP | RTD | 0 | 180 | C |  |  |  | 75 | 85 |  | 29.2016 | ok
427 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193101.PNT | 1OAI:AI193101.PNT | 10LAJ10CT022 | M-BFP HYDRAULIC COUPLER MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | C |  |  |  | 85 | 90 |  | 28.5001 | ok
428 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193103.PNT | 1OAI:AI193103.PNT | 10LAJ10CT024 | M-BFP MOTOR STATOR WINDING TEMP 1 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 26.9412 | ok
429 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193104.PNT | 1OAI:AI193104.PNT | 10LAJ10CT025 | M-BFP MOTOR STATOR WINDING TEMP 2 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 28.2013 | ok
430 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193105.PNT | 1OAI:AI193105.PNT | 10LAJ10CT026 | M-BFP MOTOR STATOR WINDING TEMP 3 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 28.578 | ok
431 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193201.PNT | 1OAI:AI193201.PNT | 10LAJ10CT027 | M-BFP MOTOR STATOR WINDING TEMP 4 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 28.9808 | ok
432 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193202.PNT | 1OAI:AI193202.PNT | 10LAJ10CT028 | M-BFP MOTOR STATOR WINDING TEMP 5 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 28.4351 | ok
433 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193203.PNT | 1OAI:AI193203.PNT | 10LAJ10CT029 | M-BFP MOTOR STATOR WINDING TEMP 6 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 28.9028 | ok
434 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI191402.PNT | 1OAI:AI191402.PNT | 10LAJ10CY201X | M-BFP FREE END BEARING VIBRATION (X DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.0066406 | ok
435 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI191401.PNT | 1OAI:AI191401.PNT | 10LAJ10CY202Y | M-BFP FREE END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.058984 | ok
436 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1QAI.AI213501.PNT | 1QAI:AI213501.PNT | 10LAJ10CY203X | M-BFP DRIVE END BEARING VIBRATION (X DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.044531 | ok
437 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1QAI.AI213502.PNT | 1QAI:AI213502.PNT | 10LAJ10CY204Y | M-BFP DRIVE END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.0078125 | ok
438 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192601.PNT | 1OAI:AI192601.PNT | 10LAJ10CT001 | BOOSTER PUMP FOR M-BFP FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 28.0454 | ok
439 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI192602.PNT | 1OAI:AI192602.PNT | 10LAJ10CT002 | BOOSTER PUMP FOR M-BFP DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 27.5518 | ok
440 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 5 | M-BFP #1 | F296S-J0201-21 | OPC.AW1002.1OAI.AI193102.PNT | 1OAI:AI193102.PNT | 10LAJ10CT023 | BOOSTER PUMP FOR M-BFP MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | C |  |  |  | 85 | 90 |  | 28.5521 | ok
441 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI212705.PNT | 1QAI:AI212705.PNT | 10LAB30CP201 | HP HEATER MAIN PIPE INLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 13.2739 | ok
442 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI211702.PNT | 1QAI:AI211702.PNT | 10LAB30CT001 | HP HEATER INLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 146.3884 | ok
443 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI212102.PNT | 1QAI:AI212102.PNT | 10LAB30CT002 | #3 HP HEATER OUTLET MAIN PIPE WATER TEMP | TC | 0 | 500 | C | [6 empty] | 187.1156 | ok
444 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.234.RO01 | 1PMS:234.RO01 | 10LAB30CT002C1 | #3 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | -6.5318 | ok
445 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.233.RO01 | 1PMS:233.RO01 | 10LAB30CT002C2 | #3 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 40.7324 | ok
446 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI160702.PNT | 1MAI:AI160702.PNT | 10LAD30CL201 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -1.9238 | ok
447 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP3LVL_1.SIGSEL1OUT.PNT | 1M_HP3LVL_1:SIGSEL1OUT.PNT | 10LAD30CL201C1 | #3 HP HEATER LEVEL AVG | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -4.3145 | ok
448 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161102.PNT | 1MAI:AI161102.PNT | 10LAD30CL202 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -5.1279 | ok
449 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161202.PNT | 1MAI:AI161202.PNT | 10LAD30CL203 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -6.9541 | ok
450 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI172101.PNT | 1NAI:AI172101.PNT | 10LBQ30AA001XB12 | #3 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.5098 | ok | REVISI TAG
451 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212306.PNT | 1QAI:AI212306.PNT | 10LBQ30CP201 | #3 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 1.9 | MPa | [6 empty] | 1.0436 | ok
452 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212406.PNT | 1QAI:AI212406.PNT | 10LBQ30CP202 | #3 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 1.9 | MPa | [6 empty] | 1.0159 | ok
453 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211303.PNT | 1QAI:AI211303.PNT | 10LBQ30CT001 | #3 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 452.0354 | ok
454 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211304.PNT | 1QAI:AI211304.PNT | 10LBQ30CT002 | #3 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 400.4524 | ok
455 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211404.PNT | 1QAI:AI211404.PNT | 10LBQ30CT003 | #3 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 417.2599 | ok
456 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211403.PNT | 1QAI:AI211403.PNT | 10LBQ30CT004 | #3 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 456.1406 | ok
457 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP3LVL.AO162704.OUT | 1M_HP3LVL:AO162704.OUT | 10LCH30AA101XB11 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 48.8984 | ok
458 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161706.PNT | 1MAI:AI161706.PNT | 10LCH30AA101XB12 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 48.7559 | ok
459 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP3LVL.AO163102.OUT | 1M_HP3LVL:AO163102.OUT | 10LCH30AA102XB11 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
460 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI162104.PNT | 1MAI:AI162104.PNT | 10LCH30AA102XB12 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.20312 | ok
461 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1QAI.AI211705.PNT | 1QAI:AI211705.PNT | 10LCH30CT001 | #3 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 155.7701 | ok
462 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI211703.PNT | 1QAI:AI211703.PNT | 10LAB30CT003 | #2 HP HEATER OUTLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 215.1046 | ok
463 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.236.RO01 | 1PMS:236.RO01 | 10LAB30CT003C1 | #2 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | 3.0706 | ok
464 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.235.RO01 | 1PMS:235.RO01 | 10LAB30CT003C2 | #2 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 27.9891 | ok
465 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI160701.PNT | 1MAI:AI160701.PNT | 10LAD20CL201 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -9.0459 | ok
466 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP2LVL_1.SIGSEL1OUT.PNT | 1M_HP2LVL_1:SIGSEL1OUT.PNT | 10LAD20CL201C1 | #2 HP HEATER LEVEL SIGSEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -12.582 | ok
467 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161101.PNT | 1MAI:AI161101.PNT | 10LAD20CL202 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -12.9473 | ok
468 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161201.PNT | 1MAI:AI161201.PNT | 10LAD20CL203 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -12.5156 | ok
469 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI172103.PNT | 1NAI:AI172103.PNT | 10LBQ20AA001XB12 | #2 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 100.1582 | no
470 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212305.PNT | 1QAI:AI212305.PNT | 10LBQ20CP201 | #2 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 4 | MPa | [6 empty] | 2.2495 | ok
471 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212405.PNT | 1QAI:AI212405.PNT | 10LBQ20CP202 | #2 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 4 | MPa | [6 empty] | 2.2687 | ok
472 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211301.PNT | 1QAI:AI211301.PNT | 10LBQ20CT001 | #2 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 331.2535 | ok
473 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211302.PNT | 1QAI:AI211302.PNT | 10LBQ20CT002 | #2 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 244.6529 | ok
474 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211402.PNT | 1QAI:AI211402.PNT | 10LBQ20CT003 | #2 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 261.4228 | ok
475 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211401.PNT | 1QAI:AI211401.PNT | 10LBQ20CT004 | #2 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | C | [6 empty] | 331.4668 | ok
476 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP2LVL.AO163101.OUT | 1M_HP2LVL:AO163101.OUT | 10LCH20AA101XB11 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 49.504 | ok
477 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI162102.PNT | 1MAI:AI162102.PNT | 10LCH20AA101XB12 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 49.2949 | ok
478 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP2LVL.AO162607.OUT | 1M_HP2LVL:AO162607.OUT | 10LCH20AA102XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
479 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161705.PNT | 1MAI:AI161705.PNT | 10LCH20AA102XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | -0.50195 | no
480 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP2LVL.AO162703.OUT | 1M_HP2LVL:AO162703.OUT | 10LCH20AA103XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
481 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI162103.PNT | 1MAI:AI162103.PNT | 10LCH20AA103XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | -0.55859 | no
482 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1QAI.AI212104.PNT | 1QAI:AI212104.PNT | 10LCH20CT001 | #2 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 190.2274 | ok
483 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI212103.PNT | 1QAI:AI212103.PNT | 10LAB30CT004 | #1 HP HEATER OUTLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 246.8903 | ok
484 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.238.RO01 | 1PMS:238.RO01 | 10LAB30CT004C1 | #1 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | -1.8359 | ok
485 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-08 | OPC.AW1002.1PMS.237.RO01 | 1PMS:237.RO01 | 10LAB30CT004C2 | #1 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 31.7857 | ok
486 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-08 | OPC.AW1002.1QAI.AI213105.PNT | 1QAI:AI213105.PNT | 10LAB40CP201 | HP HEATER OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 13.2397 | ok
487 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI160407.PNT | 1MAI:AI160407.PNT | 10LAD10CL201 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | 5.7793 | ok
488 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP1LVL_1.SIGSEL1OUT.PNT | 1M_HP1LVL_1:SIGSEL1OUT.PNT | 10LAD10CL201C1 | #1 HP HEATER LEVEL SIGSEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -9.5273 | ok
489 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI160507.PNT | 1MAI:AI160507.PNT | 10LAD10CL202 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -10.3242 | ok
490 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI160607.PNT | 1MAI:AI160607.PNT | 10LAD10CL203 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -9.5938 | ok
491 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1NAI.AI172102.PNT | 1NAI:AI172102.PNT | 10LBQ10AA001XB12 | #1 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 100.2578 | no
492 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212304.PNT | 1QAI:AI212304.PNT | 10LBQ10CP201 | #1 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 6.6 | MPa | [6 empty] | 3.6871 | ok
493 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI212404.PNT | 1QAI:AI212404.PNT | 10LBQ10CP202 | #1 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 6.6 | MPa | [6 empty] | 3.6899 | ok
494 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211106.PNT | 1QAI:AI211106.PNT | 10LBQ10CT001 | #1 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 395.5012 | ok
495 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211107.PNT | 1QAI:AI211107.PNT | 10LBQ10CT002 | #1 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 341.6871 | ok
496 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211207.PNT | 1QAI:AI211207.PNT | 10LBQ10CT003 | #1 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 371.7826 | ok
497 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-05 | OPC.AW1002.1QAI.AI211206.PNT | 1QAI:AI211206.PNT | 10LBQ10CT004 | #1 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | C | [6 empty] | 396.2876 | ok
498 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP1LVL.AO162605.OUT | 1M_HP1LVL:AO162605.OUT | 10LCH10AA101XB11 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 71.9882 | ok
499 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161703.PNT | 1MAI:AI161703.PNT | 10LCH10AA101XB12 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 71.541 | ok
500 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP1LVL.AO162606.OUT | 1M_HP1LVL:AO162606.OUT | 10LCH10AA102XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
501 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI161704.PNT | 1MAI:AI161704.PNT | 10LCH10AA102XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | -1.998 | no
502 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1M_HP1LVL.AO162702.OUT | 1M_HP1LVL:AO162702.OUT | 10LCH10AA103XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
503 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1MAI.AI162101.PNT | 1MAI:AI162101.PNT | 10LCH10AA103XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | -2.1309 | no
504 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 | F296S-J0201-09(1/2) | OPC.AW1002.1QAI.AI211704.PNT | 1QAI:AI211704.PNT | 10LCH10CT001 | #1 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 213.7067 | ok
505 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FWCNTL.AO163107.OUT | 1M_FWCNTL:AO163107.OUT | 10DCSMEHA01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | % | [6 empty] | 37.4943 | ok
506 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FWCNTL.AO163208.OUT | 1M_FWCNTL:AO163208.OUT | 10DCSMEHB01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | % | [6 empty] | 37.4943 | ok
507 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1JAI.AI125601.PNT | 1JAI:AI125601.PNT | 10LAB40AA002XB12 | BOILER FEED WATER MOTORIZED ORIFICE VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.03125 | ok
508 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FLOW.FW1AIN.PNT | 1M_FLOW:FW1AIN.PNT | 10LAB40CF201 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 566.9237 | ok
509 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FLOW.FW2AIN.PNT | 1M_FLOW:FW2AIN.PNT | 10LAB40CF202 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 590.0635 | ok
510 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FLOW.FW3AIN.PNT | 1M_FLOW:FW3AIN.PNT | 10LAB40CF203 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 587.1685 | ok
511 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI140605.PNT | 1LAI:AI140605.PNT | 10LAB40CP201C1 | FEED WATER OPERATE STATION FRONT PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 13.2861 | ok
512 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI140606.PNT | 1LAI:AI140606.PNT | 10LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 13.2197 | ok
513 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1MAI.AI163307.PNT | 1MAI:AI163307.PNT | 10LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | ℃ | [6 empty] | 248.3404 | ok
514 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1M_FWCNTL.AO162801.OUT | 1M_FWCNTL:AO162801.OUT | 10LAB41AA101XB11 | BOILER FEED WATER BYPASS CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
515 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 12 | FEEDWATER PIPE#1 | 50-F296S-J0201-08 | OPC.AW1002.1MAI.AI162306.PNT | 1MAI:AI162306.PNT | 10LAB41AA101XB12 | BOILER FEED WATER BYPASS CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.59766 | ok
516 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051603.PNT | 1EAI:AI051603.PNT | 10HFW11AA101XB12 | SAF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | -0.38086 | no
517 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1IAI.AI100507.PNT | 1IAI:AI100507.PNT | 10HFW11AN001XB13 | SAF A CURRENT | AI | 0 | 300 | A | [6 empty] | -1.0488 | no
518 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 1 | SAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_SAF.AO052503.OUT | 1E_SAF:AO052503.OUT | 10HFW11AA101XB11 | SAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
519 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051703.PNT | 1EAI:AI051703.PNT | 10HFW12AA101XB12 | SAF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 66.9316 | ok
520 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1IAI.AI100605.PNT | 1IAI:AI100605.PNT | 10HFW12AN001XB13 | SAF B CURRENT | AI | 0 | 300 | A | [6 empty] | 126.5684 | ok
521 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 2 | SAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_SAF.AO052603.OUT | 1E_SAF:AO052603.OUT | 10HFW12AA101XB11 | SAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 67 | ok
522 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051103.PNT | 1EAI:AI051103.PNT | 10HFW10CP201 | SAF OUTLET AIR PRESSURE | AI | 0 | 25 | KPa | [6 empty] | 12.542 | ok
523 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140306.PNT | 1LAI:AI140306.PNT | 10HFW10DP201 | DIFFERENTIAL PRESSURE BETWEEN SAF OUTLET AND PRIMARY HOT AIR MAIN PIPE | AI | 0 | 1.37 | KPa | [6 empty] | 3.2834 | ok
524 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141607.PNT | 1LAI:AI141607.PNT | 10HFW10CT001 | SAF OUTLET AIR TEMP. | TC | 0 | 100 | °C | [6 empty] | 48.1242 | ok
525 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051604.PNT | 1EAI:AI051604.PNT | 10HFW13AA101XB12 | SAF EXHAUST ASH VAVLE POSITION | AI | 0 | 100 | % | [6 empty] | 7.2793 | ok
526 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051104.PNT | 1EAI:AI051104.PNT | 10HFW13DP201 | SAF DIFFERENTIAL PRESSURE BETWEEN FILTER AND DISCHARGE ASH INLET | AI | 0 | 1.37 | KPa | [6 empty] | 0.030691 | ok
527 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 3 | DUCTING SAF #1 | 50-F296S-J0201-02 | OPC.AW1002.1E_SAFASH.AO052504.OUT | 1E_SAFASH:AO052504.OUT | 10HFW13AA101XB11 | SAF EXHAUST ASH VAVLE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 8 | ok
528 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 4 | COAL FEEDER #1A | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELC.LLAG1.OUT | 1E_FUELC.LLAG1.OUT | 10HFB10GC001AI01 | ECF A INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 0 | ok
529 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 4 | COAL FEEDER #1A | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELF.AOUT1.OUT | 1E_FUELF:AOUT1.OUT | 10HFB10GC001AO01 | ECF A FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
530 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI071105.PNT | 1GAI:AI071105.PNT | 10HFC10AJ001XB13 | MSM A CURRENT | AI | 0 | 200 | A | [6 empty] | 0.011719 | ok
531 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070101.PNT | 1GAI:AI070101.PNT | 10HFC10CT001 | MSM A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 28.656 | ok
532 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070201.PNT | 1GAI:AI070201.PNT | 10HFC10CT002 | MSM A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 27.4348 | ok
533 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070102.PNT | 1GAI:AI070102.PNT | 10HFC10CT003 | MSM A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 30.3058 | ok
534 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070202.PNT | 1GAI:AI070202.PNT | 10HFC10CT004 | MSM A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 30.046 | ok
535 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070103.PNT | 1GAI:AI070103.PNT | 10HFC10CT005 | MSM A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 30.2409 | ok
536 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070203.PNT | 1GAI:AI070203.PNT | 10HFC10CT006 | MSM A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 30.072 | ok
537 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070104.PNT | 1GAI:AI070104.PNT | 10HFC10CT007 | MSM A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 29.9421 | ok
538 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070204.PNT | 1GAI:AI070204.PNT | 10HFC10CT008 | MSM A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 30.072 | ok
539 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070105.PNT | 1GAI:AI070105.PNT | 10HFC10CT009 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 32.5272 | ok
540 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070205.PNT | 1GAI:AI070205.PNT | 10HFC10CT010 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 32.1765 | ok
541 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070501.PNT | 1GAI:AI070501.PNT | 10HFC10CT011 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 32.0725 | ok
542 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070502.PNT | 1GAI:AI070502.PNT | 10HFC10CT012 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 32.4103 | ok
543 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070106.PNT | 1GAI:AI070106.PNT | 10HFC10CT013 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 29.7342 | ok
544 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070206.PNT | 1GAI:AI070206.PNT | 10HFC10CT014 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 29.8381 | ok
545 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070107.PNT | 1GAI:AI070107.PNT | 10HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 49.1814 | ok
546 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050501.PNT | 1EAI:AI050501.PNT | 10HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 49.675 | ok
547 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050601.PNT | 1EAI:AI050601.PNT | 10HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 51.2989 | ok
548 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070207.PNT | 1GAI:AI070207.PNT | 10HFC10CT018 | MSM A LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 38.8018 | ok
549 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070503.PNT | 1GAI:AI070503.PNT | 10HFC10CT019 | MSM A LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 27.9285 | ok
550 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141301.PNT | 1LAI:AI141301.PNT | 10HFC10CY001X | MSM A BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.055859 | ok
551 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141302.PNT | 1LAI:AI141302.PNT | 10HFC10CY001Y | MSM A BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.10352 | ok
552 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070603.PNT | 1GAI:AI070603.PNT | 10HFC10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 0.077344 | ok
553 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI071106.PNT | 1GAI:AI071106.PNT | 10HFC10GC003AI01 | MSM A OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -0.43359 | no
554 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1GAI.AI070601.PNT | 1GAI:AI070601.PNT | 10HFE10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | -0.071289 | no
555 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_MAHCAD.AO052606.OUT | 1E_MAHCAD:AO052606.OUT | 10HFE41AA101XB11 | MSM A INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75 | ok
556 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052102.PNT | 1EAI:AI052102.PNT | 10HFE41AA101XB12 | MSM A INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 75.2324 | ok
557 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_MAHCAD.AO052505.OUT | 1E_MAHCAD:AO052505.OUT | 10HFE51AA101XB11 | MSM A INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
558 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051605.PNT | 1EAI:AI051605.PNT | 10HFE51AA101XB12 | MSM A INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.32422 | ok
559 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_MAPAD.AO052704.OUT | 1E_MAPAD:AO052704.OUT | 10HFE51AA102XB11 | MSM A INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 6 | ok
560 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052204.PNT | 1EAI:AI052204.PNT | 10HFE51AA102XB12 | MSM A INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 5.8613 | ok
561 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMA1AIN.PNT | 1E_AIRFLOW:MSMA1AIN.PNT | 10HFE51CF201 | MSM A INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 62.48 | ok
562 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMA2AIN.PNT | 1E_AIRFLOW:MSMA2AIN.PNT | 10HFE51CF202 | MSM A INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 62.334 | ok
563 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050703.PNT | 1EAI:AI050703.PNT | 10HFE51CP201 | MSM A INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 1.3332 | ok
564 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 5 | MEDIUM SPEED MILL #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050107.PNT | 1EAI:AI050107.PNT | 10HFE51CT001 | MSM A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 50.3349 | ok
565 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140501.PNT | 1LAI:AI140501.PNT | 10HFF11CF201 | 1# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
566 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI071101.PNT | 1GAI:AI071101.PNT | 10HHA51CB201B | 1# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.22852 | ok
567 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCE.AO062504.OUT | 1F_CYCE:AO062504.OUT | 10HLA11AA011XB11 | 1# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
568 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061104.PNT | 1FAI:AI061104.PNT | 10HLA11AA011XB12 | 1# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.24609 | ok
569 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXEF.AO062505.OUT | 1F_AUXEF:AO062505.OUT | 10HLA11AA012XB11 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 30 | ok
570 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061105.PNT | 1FAI:AI061105.PNT | 10HLA11AA012XB12 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 30.1348 | ok
571 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1F_BUTFF.AO062506.OUT | 1F_BUTFF:AO062506.OUT | 10HLA11AA013XB11 | 1# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20 | ok
572 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061106.PNT | 1FAI:AI061106.PNT | 10HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 21.0996 | ok
573 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140502.PNT | 1LAI:AI140502.PNT | 10HFF12CF201 | 2# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 19.7615 | ok
574 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI071102.PNT | 1GAI:AI071102.PNT | 10HHA52CB201B | 2# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.21875 | ok
575 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061303.PNT | 1FAI:AI061303.PNT | 10HLA21AA011XB12 | 2# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.40625 | ok
576 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061304.PNT | 1FAI:AI061304.PNT | 10HLA21AA012XB12 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 29.5684 | ok
577 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061305.PNT | 1FAI:AI061305.PNT | 10HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.7168 | ok
578 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCE.AO062703.OUT | 1F_CYCE:AO062703.OUT | 10HLA21AA011XB11 | 2# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
579 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXEF.AO062704.OUT | 1F_AUXEF:AO062704.OUT | 10HLA21AA012XB11 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 30 | ok
580 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW1002.1F_BUTFF.AO062705.OUT | 1F_BUTFF:AO062705.OUT | 10HLA21AA013XB11 | 2# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20 | ok
581 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140503.PNT | 1LAI:AI140503.PNT | 10HFF13CF201 | 3# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
582 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI071103.PNT | 1GAI:AI071103.PNT | 10HHA53CB201B | 3# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.28125 | ok
583 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCE.AO063202.OUT | 1F_CYCE:AO063202.OUT | 10HLA31AA011XB11 | 3# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
584 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061502.PNT | 1FAI:AI061502.PNT | 10HLA31AA011XB12 | 3# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.63281 | ok
585 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXEF.AO063203.OUT | 1F_AUXEF:AO063203.OUT | 10HLA31AA012XB11 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 30 | ok
586 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061503.PNT | 1FAI:AI061503.PNT | 10HLA31AA012XB12 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 29.2754 | ok
587 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1F_BUTFF.AO063204.OUT | 1F_BUTFF:AO063204.OUT | 10HLA31AA013XB11 | 3# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20 | ok
588 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061504.PNT | 1FAI:AI061504.PNT | 10HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.8125 | ok
589 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140504.PNT | 1LAI:AI140504.PNT | 10HFF14CF201 | 4# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
590 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI071104.PNT | 1GAI:AI071104.PNT | 10HHA54CB201B | 4# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.28906 | ok
591 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCE.AO063401.OUT | 1F_CYCE:AO063401.OUT | 10HLA41AA011XB11 | 4# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
592 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061701.PNT | 1FAI:AI061701.PNT | 10HLA41AA011XB12 | 4# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.51367 | ok
593 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXEF.AO063402.OUT | 1F_AUXEF:AO063402.OUT | 10HLA41AA012XB11 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 30 | ok
594 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061702.PNT | 1FAI:AI061702.PNT | 10HLA41AA012XB12 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 30.084 | ok
595 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1F_BUTFF.AO063403.OUT | 1F_BUTFF:AO063403.OUT | 10HLA41AA013XB11 | 4# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20 | ok
596 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061703.PNT | 1FAI:AI061703.PNT | 10HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.7578 | ok
597 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 11 | COAL FEEDER #1B | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELC.LLAG2.OUT | 1E_FUELC.LLAG2.OUT | 10HFB20GC001AI01 | ECF B INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 0 | ok
598 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 11 | COAL FEEDER #1B | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELF.AOUT2.OUT | 1E_FUELF:AOUT2.OUT | 10HFB20GC001AO01 | ECF B FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
599 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070705.PNT | 1GAI:AI070705.PNT | 10HFC20AJ001XB13 | MSM B CURRENT | AI | 0 | 200 | A | [6 empty] | 0.023438 | ok
600 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070301.PNT | 1GAI:AI070301.PNT | 10HFC20CT001 | MSM B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 38.1782 | ok
601 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070401.PNT | 1GAI:AI070401.PNT | 10HFC20CT002 | MSM B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 31.7348 | ok
602 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070302.PNT | 1GAI:AI070302.PNT | 10HFC20CT003 | MSM B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 52.6889 | ok
603 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070402.PNT | 1GAI:AI070402.PNT | 10HFC20CT004 | MSM B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 50.5194 | ok
604 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070303.PNT | 1GAI:AI070303.PNT | 10HFC20CT005 | MSM B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 49.714 | ok
605 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070403.PNT | 1GAI:AI070403.PNT | 10HFC20CT006 | MSM B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 49.662 | ok
606 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070304.PNT | 1GAI:AI070304.PNT | 10HFC20CT007 | MSM B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 48.7007 | ok
607 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070404.PNT | 1GAI:AI070404.PNT | 10HFC20CT008 | MSM B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 49.714 | ok
608 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070305.PNT | 1GAI:AI070305.PNT | 10HFC20CT009 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 34.242 | ok
609 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070405.PNT | 1GAI:AI070405.PNT | 10HFC20CT010 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 34.216 | ok
610 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070504.PNT | 1GAI:AI070504.PNT | 10HFC20CT011 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 35.2163 | ok
611 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070505.PNT | 1GAI:AI070505.PNT | 10HFC20CT012 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 34.7876 | ok
612 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070306.PNT | 1GAI:AI070306.PNT | 10HFC20CT013 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 33.0079 | ok
613 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070406.PNT | 1GAI:AI070406.PNT | 10HFC20CT014 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 36.2166 | ok
614 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070307.PNT | 1GAI:AI070307.PNT | 10HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 52.3122 | ok
615 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050502.PNT | 1EAI:AI050502.PNT | 10HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 51.9354 | ok
616 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050602.PNT | 1EAI:AI050602.PNT | 10HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 52.4031 | ok
617 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070407.PNT | 1GAI:AI070407.PNT | 10HFC20CT018 | MSM B LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 29.1106 | ok
618 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070506.PNT | 1GAI:AI070506.PNT | 10HFC20CT019 | MSM B LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 27.0581 | ok
619 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141303.PNT | 1LAI:AI141303.PNT | 10HFC20CY001X | MSM B BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.021484 | ok
620 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141304.PNT | 1LAI:AI141304.PNT | 10HFC20CY001Y | MSM B BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.036328 | ok
621 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070604.PNT | 1GAI:AI070604.PNT | 10HFC20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 0.22373 | ok
622 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-34 | OPC.AW1002.1GAI.AI070706.PNT | 1GAI:AI070706.PNT | 10HFC20GC003AI01 | MSM B OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -0.26953 | no
623 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1GAI.AI070602.PNT | 1GAI:AI070602.PNT | 10HFE20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 3 | ok
624 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_MBHCAD.AO052607.OUT | 1E_MBHCAD:AO052607.OUT | 10HFE42AA101XB11 | MSM B INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 63.1118 | ok
625 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052103.PNT | 1EAI:AI052103.PNT | 10HFE42AA101XB12 | MSM B INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 62.4648 | ok
626 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_MBHCAD.AO052506.OUT | 1E_MBHCAD:AO052506.OUT | 10HFE52AA101XB11 | MSM B INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
627 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051606.PNT | 1EAI:AI051606.PNT | 10HFE52AA101XB12 | MSM B INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | -0.21953 | no
628 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_MBPAD.AO053102.OUT | 1E_MBPAD:AO053102.OUT | 10HFE52AA102XB11 | MSM B INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
629 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052205.PNT | 1EAI:AI052205.PNT | 10HFE52AA102XB12 | MSM B INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.42578 | ok
630 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMB1AIN.PNT | 1E_AIRFLOW:MSMB1AIN.PNT | 10HFE52CF201 | MSM B INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 0 | ok
631 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMB2AIN.PNT | 1E_AIRFLOW:MSMB2AIN.PNT | 10HFE52CF202 | MSM B INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 0 | ok
632 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050704.PNT | 1EAI:AI050704.PNT | 10HFE52CP201 | MSM B INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 1.1777 | ok
633 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 12 | MEDIUM SPEED MILL #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050205.PNT | 1EAI:AI050205.PNT | 10HFE52CT001 | MSM B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 51.1472 | ok
634 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140601.PNT | 1LAI:AI140601.PNT | 10HFF21CF201 | 1# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
635 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI070701.PNT | 1GAI:AI070701.PNT | 10HHA41CB201B | 1# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.2793 | ok
636 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDD.AO062501.OUT | 1F_AUXDD:AO062501.OUT | 10HLA11AA008XB11 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
637 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061101.PNT | 1FAI:AI061101.PNT | 10HLA11AA008XB12 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.0234 | ok
638 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCD.AO062502.OUT | 1F_CYCD:AO062502.OUT | 10HLA11AA009XB11 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.0057089 | ok
639 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061102.PNT | 1FAI:AI061102.PNT | 10HLA11AA009XB12 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | 0.011719 | ok
640 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDE.AO062503.OUT | 1F_AUXDE:AO062503.OUT | 10HLA11AA010XB11 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
641 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061103.PNT | 1FAI:AI061103.PNT | 10HLA11AA010XB12 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 55.0703 | ok
642 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140602.PNT | 1LAI:AI140602.PNT | 10HFF22CF201 | 2# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
643 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI070702.PNT | 1GAI:AI070702.PNT | 10HHA42CB201B | 2# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.22461 | ok
644 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDD.AO062607.OUT | 1F_AUXDD:AO062607.OUT | 10HLA21AA008XB11 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
645 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061207.PNT | 1FAI:AI061207.PNT | 10HLA21AA008XB12 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.7949 | ok
646 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCD.AO062701.OUT | 1F_CYCD:AO062701.OUT | 10HLA21AA009XB11 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.0057089 | ok
647 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061301.PNT | 1FAI:AI061301.PNT | 10HLA21AA009XB12 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | -0.11719 | no
648 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDE.AO062702.OUT | 1F_AUXDE:AO062702.OUT | 10HLA21AA010XB11 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
649 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061302.PNT | 1FAI:AI061302.PNT | 10HLA21AA010XB12 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 54.3379 | ok
650 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140603.PNT | 1LAI:AI140603.PNT | 10HFF23CF201 | 3# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 16.707 | ok
651 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI070703.PNT | 1GAI:AI070703.PNT | 10HHA43CB201B | 3# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.31836 | ok
652 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDD.AO063106.OUT | 1F_AUXDD:AO063106.OUT | 10HLA31AA008XB11 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
653 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061406.PNT | 1FAI:AI061406.PNT | 10HLA31AA008XB12 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.4668 | ok
654 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCD.AO063107.OUT | 1F_CYCD:AO063107.OUT | 10HLA31AA009XB11 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.0057089 | ok
655 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061407.PNT | 1FAI:AI061407.PNT | 10HLA31AA009XB12 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | -0.13086 | no
656 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDE.AO063201.OUT | 1F_AUXDE:AO063201.OUT | 10HLA31AA010XB11 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
657 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061501.PNT | 1FAI:AI061501.PNT | 10HLA31AA010XB12 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 55.1484 | ok
658 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140604.PNT | 1LAI:AI140604.PNT | 10HFF24CF201 | 4# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 14.8128 | ok
659 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-39 | OPC.AW1002.1GAI.AI070704.PNT | 1GAI:AI070704.PNT | 10HHA44CB201B | 4# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.23828 | ok
660 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDD.AO063305.OUT | 1F_AUXDD:AO063305.OUT | 10HLA41AA008XB11 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
661 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061605.PNT | 1FAI:AI061605.PNT | 10HLA41AA008XB12 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.6328 | ok
662 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCD.AO063306.OUT | 1F_CYCD:AO063306.OUT | 10HLA41AA009XB11 | 4# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.0057089 | ok
663 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061606.PNT | 1FAI:AI061606.PNT | 10HLA41AA009XB12 | 4# CORNER D LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.060547 | ok
664 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXDE.AO063307.OUT | 1F_AUXDE:AO063307.OUT | 10HLA41AA010XB11 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
665 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061607.PNT | 1FAI:AI061607.PNT | 10HLA41AA010XB12 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 54.457 | ok
666 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 18 | COAL FEEDER #1C | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELC.LLAG3.OUT | 1E_FUELC.LLAG3.OUT | 10HFB30GC001AI01 | ECF C INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 40.3924 | ok
667 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 18 | COAL FEEDER #1C | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELF.AOUT3.OUT | 1E_FUELF:AOUT3.OUT | 10HFB30GC001AO01 | ECF C FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 74.1816 | ok
668 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI091105.PNT | 1HAI:AI091105.PNT | 10HFC30AJ001XB13 | MSM C CURRENT | AI | 0 | 200 | A | [6 empty] | 46.6836 | ok
669 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090101.PNT | 1HAI:AI090101.PNT | 10HFC30CT001 | MSM C MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 52.2082 | ok
670 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090201.PNT | 1HAI:AI090201.PNT | 10HFC30CT002 | MSM C MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 49.3892 | ok
671 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090102.PNT | 1HAI:AI090102.PNT | 10HFC30CT003 | MSM C MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 68.2648 | ok
672 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090202.PNT | 1HAI:AI090202.PNT | 10HFC30CT004 | MSM C MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.4721 | ok
673 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090103.PNT | 1HAI:AI090103.PNT | 10HFC30CT005 | MSM C MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 67.0697 | ok
674 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090203.PNT | 1HAI:AI090203.PNT | 10HFC30CT006 | MSM C MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.0304 | ok
675 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090104.PNT | 1HAI:AI090104.PNT | 10HFC30CT007 | MSM C MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.563 | ok
676 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090204.PNT | 1HAI:AI090204.PNT | 10HFC30CT008 | MSM C MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.9917 | ok
677 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090105.PNT | 1HAI:AI090105.PNT | 10HFC30CT009 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.0356 | ok
678 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090205.PNT | 1HAI:AI090205.PNT | 10HFC30CT010 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.1395 | ok
679 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090501.PNT | 1HAI:AI090501.PNT | 10HFC30CT011 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 38.2691 | ok
680 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090502.PNT | 1HAI:AI090502.PNT | 10HFC30CT012 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.2694 | ok
681 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090106.PNT | 1HAI:AI090106.PNT | 10HFC30CT013 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 47.7394 | ok
682 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090206.PNT | 1HAI:AI090206.PNT | 10HFC30CT014 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 50.8702 | ok
683 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090107.PNT | 1HAI:AI090107.PNT | 10HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.5731 | ok
684 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050503.PNT | 1EAI:AI050503.PNT | 10HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.0925 | ok
685 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050603.PNT | 1EAI:AI050603.PNT | 10HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.8327 | ok
686 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090207.PNT | 1HAI:AI090207.PNT | 10HFC30CT018 | MSM C LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 34.5668 | ok
687 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090503.PNT | 1HAI:AI090503.PNT | 10HFC30CT019 | MSM C LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 29.3445 | ok
688 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141305.PNT | 1LAI:AI141305.PNT | 10HFC30CY001X | MSM C BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.22617 | ok
689 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141306.PNT | 1LAI:AI141306.PNT | 10HFC30CY001Y | MSM C BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 1.777 | ok
690 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090603.PNT | 1HAI:AI090603.PNT | 10HFC30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 5.0862 | ok
691 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI091106.PNT | 1HAI:AI091106.PNT | 10HFC30GC003AI01 | MSM C OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | 0.58594 | ok
692 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1HAI.AI090601.PNT | 1HAI:AI090601.PNT | 10HFE30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 4.7953 | ok
693 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1E_MCHCAD.AO052701.OUT | 1E_MCHCAD:AO052701.OUT | 10HFE43AA101XB11 | MSM C INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 35.0387 | ok
694 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052201.PNT | 1EAI:AI052201.PNT | 10HFE43AA101XB12 | MSM C INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 35.9922 | ok
695 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1E_MCHCAD.AO052507.OUT | 1E_MCHCAD:AO052507.OUT | 10HFE53AA101XB11 | MSM C INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
696 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051607.PNT | 1EAI:AI051607.PNT | 10HFE53AA101XB12 | MSM C INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 54.3223 | ok
697 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1E_MCPAD.AO053103.OUT | 1E_MCPAD:AO053103.OUT | 10HFE53AA102XB11 | MSM C INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
698 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052206.PNT | 1EAI:AI052206.PNT | 10HFE53AA102XB12 | MSM C INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.582 | ok
699 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMC1AIN.PNT | 1E_AIRFLOW:MSMC1AIN.PNT | 10HFE53CF201 | MSM C INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 92.7162 | ok
700 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMC2AIN.PNT | 1E_AIRFLOW:MSMC2AIN.PNT | 10HFE53CF202 | MSM C INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 92.742 | ok
701 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050705.PNT | 1EAI:AI050705.PNT | 10HFE53CP201 | MSM C INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 5.748 | ok
702 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 19 | MEDIUM SPEED MILL #1C | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050305.PNT | 1EAI:AI050305.PNT | 10HFE53CT001 | MSM C INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 257.0519 | ok
703 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140701.PNT | 1LAI:AI140701.PNT | 10HFF31CF201 | 1# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 18.5662 | ok
704 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI091101.PNT | 1HAI:AI091101.PNT | 10HHA31CB201B | 1# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.1738 | ok
705 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCC.AO062406.OUT | 1F_CYCC:AO062406.OUT | 10HLA11AA006XB11 | 1# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75.7687 | ok
706 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060706.PNT | 1FAI:AI060706.PNT | 10HLA11AA006XB12 | 1# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 75.0254 | ok
707 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXCC.AO062407.OUT | 1F_AUXCC:AO062407.OUT | 10HLA11AA007XB11 | 1#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
708 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060707.PNT | 1FAI:AI060707.PNT | 10HLA11AA007XB12 | 1# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.4863 | ok
709 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140702.PNT | 1LAI:AI140702.PNT | 10HFF32CF201 | 2# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 19.4079 | ok
710 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI091102.PNT | 1HAI:AI091102.PNT | 10HHA32CB201B | 2# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 100.5215 | ok
711 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCC.AO062605.OUT | 1F_CYCC:AO062605.OUT | 10HLA21AA006XB11 | 2# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75.7687 | ok
712 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061205.PNT | 1FAI:AI061205.PNT | 10HLA21AA006XB12 | 2# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 75.5215 | ok
713 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXCC.AO062606.OUT | 1F_AUXCC:AO062606.OUT | 10HLA21AA007XB11 | 2#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
714 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061206.PNT | 1FAI:AI061206.PNT | 10HLA21AA007XB12 | 2# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.5078 | ok
715 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140703.PNT | 1LAI:AI140703.PNT | 10HFF33CF201 | 3# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 11.2875 | ok
716 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI091103.PNT | 1HAI:AI091103.PNT | 10HHA33CB201B | 3# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 100.3223 | ok
717 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCC.AO063104.OUT | 1F_CYCC:AO063104.OUT | 10HLA31AA006XB11 | 3# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75.7687 | ok
718 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061404.PNT | 1FAI:AI061404.PNT | 10HLA31AA006XB12 | 3# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 75.1152 | ok
719 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXCC.AO063105.OUT | 1F_AUXCC:AO063105.OUT | 10HLA31AA007XB11 | 3#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
720 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061405.PNT | 1FAI:AI061405.PNT | 10HLA31AA007XB12 | 3# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 65.1055 | ok
721 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI140704.PNT | 1LAI:AI140704.PNT | 10HFF34CF201 | 4# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 11.4431 | ok
722 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI091104.PNT | 1HAI:AI091104.PNT | 10HHA34CB201B | 4# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.5 | ok
723 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCC.AO063303.OUT | 1F_CYCC:AO063303.OUT | 10HLA41AA006XB11 | 4# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75.7687 | ok
724 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061603.PNT | 1FAI:AI061603.PNT | 10HLA41AA006XB12 | 4# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 75.1191 | ok
725 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXCC.AO063304.OUT | 1F_AUXCC:AO063304.OUT | 10HLA41AA007XB11 | 4#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
726 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061604.PNT | 1FAI:AI061604.PNT | 10HLA41AA007XB12 | 4# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.416 | ok
727 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 25 | COAL FEEDER #1D | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELC.LLAG4.OUT | 1E_FUELC.LLAG4.OUT | 10HFB40GC001AI01 | ECF D INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 41.2048 | ok
728 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 25 | COAL FEEDER #1D | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELF.AOUT4.OUT | 1E_FUELF:AOUT4.OUT | 10HFB40GC001AO01 | ECF D FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 75.8208 | ok
729 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090705.PNT | 1HAI:AI090705.PNT | 10HFC40AJ001XB13 | MSM D CURRENT | AI | 0 | 200 | A | [6 empty] | 50.2852 | ok
730 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090301.PNT | 1HAI:AI090301.PNT | 10HFC40CT001 | MSM D MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 48.9865 | ok
731 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090401.PNT | 1HAI:AI090401.PNT | 10HFC40CT002 | MSM D MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 34.229 | ok
732 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090302.PNT | 1HAI:AI090302.PNT | 10HFC40CT003 | MSM D MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 59.561 | ok
733 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090402.PNT | 1HAI:AI090402.PNT | 10HFC40CT004 | MSM D MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 70.759 | ok
734 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090303.PNT | 1HAI:AI090303.PNT | 10HFC40CT005 | MSM D MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 60.2625 | ok
735 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090403.PNT | 1HAI:AI090403.PNT | 10HFC40CT006 | MSM D MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 60.3015 | ok
736 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090304.PNT | 1HAI:AI090304.PNT | 10HFC40CT007 | MSM D MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 46.986 | ok
737 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090404.PNT | 1HAI:AI090404.PNT | 10HFC40CT008 | MSM D MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 60.5353 | ok
738 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090305.PNT | 1HAI:AI090305.PNT | 10HFC40CT009 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.3739 | ok
739 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090405.PNT | 1HAI:AI090405.PNT | 10HFC40CT010 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.5033 | ok
740 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090504.PNT | 1HAI:AI090504.PNT | 10HFC40CT011 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.8021 | ok
741 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090505.PNT | 1HAI:AI090505.PNT | 10HFC40CT012 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.2694 | ok
742 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090306.PNT | 1HAI:AI090306.PNT | 10HFC40CT013 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 47.7914 | ok
743 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090406.PNT | 1HAI:AI090406.PNT | 10HFC40CT014 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 50.8572 | ok
744 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090307.PNT | 1HAI:AI090307.PNT | 10HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.0925 | ok
745 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050504.PNT | 1EAI:AI050504.PNT | 10HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.3263 | ok
746 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050604.PNT | 1EAI:AI050604.PNT | 10HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.3003 | ok
747 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090407.PNT | 1HAI:AI090407.PNT | 10HFC40CT018 | MSM D LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 36.9441 | ok
748 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090506.PNT | 1HAI:AI090506.PNT | 10HFC40CT019 | MSM D LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 29.1237 | ok
749 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141401.PNT | 1LAI:AI141401.PNT | 10HFC40CY001X | MSM D BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.29297 | ok
750 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141402.PNT | 1LAI:AI141402.PNT | 10HFC40CY001Y | MSM D BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.42734 | ok
751 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090604.PNT | 1HAI:AI090604.PNT | 10HFC40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 5.0909 | ok
752 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-34 | OPC.AW1002.1HAI.AI090706.PNT | 1HAI:AI090706.PNT | 10HFC40GC003AI01 | MSM D OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -2.1328 | no
753 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1HAI.AI090602.PNT | 1HAI:AI090602.PNT | 10HFE40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 4.5958 | ok
754 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1E_MDHCAD.AO052702.OUT | 1E_MDHCAD:AO052702.OUT | 10HFE44AA101XB11 | MSM D INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 47.6585 | ok
755 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052202.PNT | 1EAI:AI052202.PNT | 10HFE44AA101XB12 | MSM D INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 47.4141 | ok
756 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1E_MDHCAD.AO052604.OUT | 1E_MDHCAD:AO052604.OUT | 10HFE54AA101XB11 | MSM D INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
757 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051704.PNT | 1EAI:AI051704.PNT | 10HFE54AA101XB12 | MSM D INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.7246 | ok
758 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1E_MDPAD.AO053104.OUT | 1E_MDPAD:AO053104.OUT | 10HFE54AA102XB11 | MSM D INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
759 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052207.PNT | 1EAI:AI052207.PNT | 10HFE54AA102XB12 | MSM D INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.043 | ok
760 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMD1AIN.PNT | 1E_AIRFLOW:MSMD1AIN.PNT | 10HFE54CF201 | MSM D INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 90.7512 | ok
761 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSMD2AIN.PNT | 1E_AIRFLOW:MSMD2AIN.PNT | 10HFE54CF202 | MSM D INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 90.6816 | ok
762 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050706.PNT | 1EAI:AI050706.PNT | 10HFE54CP201 | MSM D INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 5.8453 | ok
763 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 26 | MEDIUM SPEED MILL #1D | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050401.PNT | 1EAI:AI050401.PNT | 10HFE54CT001 | MSM D INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 244.4735 | ok
764 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141101.PNT | 1LAI:AI141101.PNT | 10HFF41CF201 | 1# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 21.1078 | ok
765 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI090701.PNT | 1HAI:AI090701.PNT | 10HHA21CB201B | 1# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 94.498 | ok
766 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCB.AO062404.OUT | 1F_CYCB:AO062404.OUT | 10HLA11AA004XB11 | 1# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 76.998 | ok
767 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060704.PNT | 1FAI:AI060704.PNT | 10HLA11AA004XB12 | 1# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 77.7246 | ok
768 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXBC.AO062405.OUT | 1F_AUXBC:AO062405.OUT | 10HLA11AA005XB11 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
769 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060705.PNT | 1FAI:AI060705.PNT | 10HLA11AA005XB12 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 65.5605 | ok
770 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141102.PNT | 1LAI:AI141102.PNT | 10HFF42CF201 | 2# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
771 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI090702.PNT | 1HAI:AI090702.PNT | 10HHA22CB201B | 2# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 34.4121 | ok
772 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCB.AO062603.OUT | 1F_CYCB:AO062603.OUT | 10HLA21AA004XB11 | 2# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 76.998 | ok
773 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061203.PNT | 1FAI:AI061203.PNT | 10HLA21AA004XB12 | 2# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 76.0879 | ok
774 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXBC.AO062604.OUT | 1F_AUXBC:AO062604.OUT | 10HLA21AA005XB11 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
775 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061204.PNT | 1FAI:AI061204.PNT | 10HLA21AA005XB12 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.7598 | ok
776 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141103.PNT | 1LAI:AI141103.PNT | 10HFF43CF201 | 3# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 21.0355 | ok
777 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI090703.PNT | 1HAI:AI090703.PNT | 10HHA23CB201B | 3# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 74.8633 | ok
778 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCB.AO063102.OUT | 1F_CYCB:AO063102.OUT | 10HLA31AA004XB11 | 3# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 76.998 | ok
779 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061402.PNT | 1FAI:AI061402.PNT | 10HLA31AA004XB12 | 3# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 77.0801 | ok
780 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXBC.AO063103.OUT | 1F_AUXBC:AO063103.OUT | 10HLA31AA005XB11 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
781 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061403.PNT | 1FAI:AI061403.PNT | 10HLA31AA005XB12 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.5664 | ok
782 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141104.PNT | 1LAI:AI141104.PNT | 10HFF44CF201 | 4# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
783 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-39 | OPC.AW1002.1HAI.AI090704.PNT | 1HAI:AI090704.PNT | 10HHA24CB201B | 4# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.4824 | ok
784 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCB.AO063301.OUT | 1F_CYCB:AO063301.OUT | 10HLA41AA004XB11 | 4# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 76.998 | ok
785 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061601.PNT | 1FAI:AI061601.PNT | 10HLA41AA004XB12 | 4# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 72.8887 | ok
786 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXBC.AO063302.OUT | 1F_AUXBC:AO063302.OUT | 10HLA41AA005XB11 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
787 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061602.PNT | 1FAI:AI061602.PNT | 10HLA41AA005XB12 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.3145 | ok
788 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 32 | COAL FEEDER #1E | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELC.LLAG5.OUT | 1E_FUELC.LLAG5.OUT | 10HFB50GC001AI01 | ECF E INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 41.6095 | ok
789 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 32 | COAL FEEDER #1E | 50-F296S-J0201-03 | OPC.AW1002.1E_FUELF.AOUT5.OUT | 1E_FUELF:AOUT5.OUT | 10HFB50GC001AO01 | ECF E FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 76.2962 | ok
790 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100505.PNT | 1IAI:AI100505.PNT | 10HFC50AJ001XB13 | MSM E CURRENT | AI | 0 | 200 | A | [6 empty] | 47.2969 | ok
791 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100101.PNT | 1IAI:AI100101.PNT | 10HFC50CT001 | MSM E MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 53.5723 | ok
792 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100201.PNT | 1IAI:AI100201.PNT | 10HFC50CT002 | MSM E MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 53.8191 | ok
793 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100102.PNT | 1IAI:AI100102.PNT | 10HFC50CT003 | MSM E MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 67.7842 | ok
794 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100202.PNT | 1IAI:AI100202.PNT | 10HFC50CT004 | MSM E MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.9138 | ok
795 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100103.PNT | 1IAI:AI100103.PNT | 10HFC50CT005 | MSM E MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.8618 | ok
796 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100203.PNT | 1IAI:AI100203.PNT | 10HFC50CT006 | MSM E MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 68.3298 | ok
797 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100104.PNT | 1IAI:AI100104.PNT | 10HFC50CT007 | MSM E MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 67.2905 | ok
798 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100204.PNT | 1IAI:AI100204.PNT | 10HFC50CT008 | MSM E MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 68.4857 | ok
799 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100105.PNT | 1IAI:AI100105.PNT | 10HFC50CT009 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 44.9594 | ok
800 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100205.PNT | 1IAI:AI100205.PNT | 10HFC50CT010 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 44.8814 | ok
801 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100301.PNT | 1IAI:AI100301.PNT | 10HFC50CT011 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 45.9337 | ok
802 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100302.PNT | 1IAI:AI100302.PNT | 10HFC50CT012 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 46.0116 | ok
803 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100106.PNT | 1IAI:AI100106.PNT | 10HFC50CT013 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 46.4663 | ok
804 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100206.PNT | 1IAI:AI100206.PNT | 10HFC50CT014 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 56.5342 | ok
805 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100107.PNT | 1IAI:AI100107.PNT | 10HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.3653 | ok
806 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050505.PNT | 1EAI:AI050505.PNT | 10HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.6251 | ok
807 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1EAI.AI050605.PNT | 1EAI:AI050605.PNT | 10HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.2224 | ok
808 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100207.PNT | 1IAI:AI100207.PNT | 10HFC50CT018 | MSM E LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 35.8009 | ok
809 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100303.PNT | 1IAI:AI100303.PNT | 10HFC50CT019 | MSM E LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 31.9946 | ok
810 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141403.PNT | 1LAI:AI141403.PNT | 10HFC50CY001X | MSM E BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.24531 | ok
811 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1LAI.AI141404.PNT | 1LAI:AI141404.PNT | 10HFC50CY001Y | MSM E BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.14486 | ok
812 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100402.PNT | 1IAI:AI100402.PNT | 10HFC50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 5.0932 | ok
813 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-34 | OPC.AW1002.1IAI.AI100506.PNT | 1IAI:AI100506.PNT | 10HFC50GC003AI01 | MSM E OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | 0.082031 | ok
814 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1E_MEHCAD.AO052703.OUT | 1E_MEHCAD:AO052703.OUT | 10HFE45AA101XB11 | MSM E INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 42.4016 | ok
815 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052203.PNT | 1EAI:AI052203.PNT | 10HFE45AA101XB12 | MSM E INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 43.2871 | ok
816 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1IAI.AI100401.PNT | 1IAI:AI100401.PNT | 10HFE50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 4.2386 | ok
817 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1E_MEHCAD.AO052605.OUT | 1E_MEHCAD:AO052605.OUT | 10HFE55AA101XB11 | MSM E INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 57 | ok
818 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052101.PNT | 1EAI:AI052101.PNT | 10HFE55AA101XB12 | MSM E INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 56.7812 | ok
819 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1E_MEPAD.AO053105.OUT | 1E_MEPAD:AO053105.OUT | 10HFE55AA102XB11 | MSM E INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
820 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052301.PNT | 1EAI:AI052301.PNT | 10HFE55AA102XB12 | MSM E INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.3613 | ok
821 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSME1AIN.PNT | 1E_AIRFLOW:MSME1AIN.PNT | 10HFE55CF201 | MSM E INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 92.2188 | ok
822 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1E_AIRFLOW.MSME2AIN.PNT | 1E_AIRFLOW:MSME2AIN.PNT | 10HFE55CF202 | MSM E INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 92.0889 | ok
823 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050707.PNT | 1EAI:AI050707.PNT | 10HFE55CP201 | MSM E INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 5.866 | ok
824 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 33 | MEDIUM SPEED MILL #1E | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050402.PNT | 1EAI:AI050402.PNT | 10HFE55CT001 | MSM E INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 251.5874 | ok
825 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141201.PNT | 1LAI:AI141201.PNT | 10HFF51CF201 | 1# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 17.1702 | ok
826 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063601.OUT | 1F_RHTEM:AO063601.OUT | 10HHA10KV001XB11 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
827 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW1002.1FAI.AI062202.PNT | 1FAI:AI062202.PNT | 10HHA10KV001XB12 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 58.1523 | ok
828 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063602.OUT | 1F_RHTEM:AO063602.OUT | 10HHA10KV002XB11 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
829 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW1002.1FAI.AI062203.PNT | 1FAI:AI062203.PNT | 10HHA10KV002XB12 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 50 | ok
830 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-39 | OPC.AW1002.1IAI.AI100501.PNT | 1IAI:AI100501.PNT | 10HHA11CB201B | 1# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.3828 | ok
831 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAA.AO062401.OUT | 1F_AUXAA:AO062401.OUT | 10HLA11AA001XB11 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
832 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060701.PNT | 1FAI:AI060701.PNT | 10HLA11AA001XB12 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 59.6133 | ok
833 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCA.AO062402.OUT | 1F_CYCA:AO062402.OUT | 10HLA11AA002XB11 | 1# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 77.3546 | ok
834 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060702.PNT | 1FAI:AI060702.PNT | 10HLA11AA002XB12 | 1# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 76.5645 | ok
835 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAB.AO062403.OUT | 1F_AUXAB:AO062403.OUT | 10HLA11AA003XB11 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
836 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI060703.PNT | 1FAI:AI060703.PNT | 10HLA11AA003XB12 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 65.0723 | ok
837 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141202.PNT | 1LAI:AI141202.PNT | 10HFF52CF201 | 2# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 18.5998 | ok
838 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW1002.1IAI.AI100502.PNT | 1IAI:AI100502.PNT | 10HHA12CB201B | 2# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0 | ok
839 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063603.OUT | 1F_RHTEM:AO063603.OUT | 10HHA20KV001XB11 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
840 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW1002.1FAI.AI062204.PNT | 1FAI:AI062204.PNT | 10HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 57.8887 | ok
841 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063604.OUT | 1F_RHTEM:AO063604.OUT | 10HHA20KV002XB11 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
842 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-39 | OPC.AW1002.1FAI.AI062205.PNT | 1FAI:AI062205.PNT | 10HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 57.9941 | ok
843 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAA.AO062507.OUT | 1F_AUXAA:AO062507.OUT | 10HLA21AA001XB11 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
844 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061107.PNT | 1FAI:AI061107.PNT | 10HLA21AA001XB12 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 1.6816 | ok
845 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCA.AO062601.OUT | 1F_CYCA:AO062601.OUT | 10HLA21AA002XB11 | 2# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 77.3546 | ok
846 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061201.PNT | 1FAI:AI061201.PNT | 10HLA21AA002XB12 | 2# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 76.5781 | ok
847 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAB.AO062602.OUT | 1F_AUXAB:AO062602.OUT | 10HLA21AA003XB11 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
848 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061202.PNT | 1FAI:AI061202.PNT | 10HLA21AA003XB12 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.1934 | ok
849 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141203.PNT | 1LAI:AI141203.PNT | 10HFF53CF201 | 3# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 21.4343 | ok
850 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW1002.1IAI.AI100503.PNT | 1IAI:AI100503.PNT | 10HHA13CB201B | 3# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 1.1992 | ok
851 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063605.OUT | 1F_RHTEM:AO063605.OUT | 10HHA30KV001XB11 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
852 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW1002.1FAI.AI062301.PNT | 1FAI:AI062301.PNT | 10HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 58.1504 | ok
853 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063701.OUT | 1F_RHTEM:AO063701.OUT | 10HHA30KV002XB11 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
854 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-39 | OPC.AW1002.1FAI.AI062302.PNT | 1FAI:AI062302.PNT | 10HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 57.9746 | ok
855 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAA.AO062706.OUT | 1F_AUXAA:AO062706.OUT | 10HLA31AA001XB11 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
856 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061306.PNT | 1FAI:AI061306.PNT | 10HLA31AA001XB12 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.2188 | ok
857 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCA.AO062707.OUT | 1F_CYCA:AO062707.OUT | 10HLA31AA002XB11 | 3# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 77.3546 | ok
858 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061307.PNT | 1FAI:AI061307.PNT | 10HLA31AA002XB12 | 3# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 76.9941 | ok
859 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAB.AO063101.OUT | 1F_AUXAB:AO063101.OUT | 10HLA31AA003XB11 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
860 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061401.PNT | 1FAI:AI061401.PNT | 10HLA31AA003XB12 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.2402 | ok
861 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1LAI.AI141204.PNT | 1LAI:AI141204.PNT | 10HFF54CF201 | 4# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
862 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW1002.1IAI.AI100504.PNT | 1IAI:AI100504.PNT | 10HHA14CB201B | 4# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.4707 | ok
863 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063702.OUT | 1F_RHTEM:AO063702.OUT | 10HHA40KV001XB11 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
864 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW1002.1FAI.AI062303.PNT | 1FAI:AI062303.PNT | 10HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 57.6797 | ok
865 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW1002.1F_RHTEM.AO063703.OUT | 1F_RHTEM:AO063703.OUT | 10HHA40KV002XB11 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 58 | ok
866 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-39 | OPC.AW1002.1FAI.AI062304.PNT | 1FAI:AI062304.PNT | 10HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 58.0879 | ok
867 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAA.AO063205.OUT | 1F_AUXAA:AO063205.OUT | 10HLA41AA001XB11 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
868 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061505.PNT | 1FAI:AI061505.PNT | 10HLA41AA001XB12 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.418 | ok
869 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1F_CYCA.AO063206.OUT | 1F_CYCA:AO063206.OUT | 10HLA41AA002XB11 | 4# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 77.3546 | ok
870 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061506.PNT | 1FAI:AI061506.PNT | 10HLA41AA002XB12 | 4# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 76.6797 | ok
871 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1F_AUXAB.AO063207.OUT | 1F_AUXAB:AO063207.OUT | 10HLA41AA003XB11 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 65 | ok
872 | 1 | UJPCT #1 | 5 | PULVERIZER SYSTEM#1 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW1002.1FAI.AI061507.PNT | 1FAI:AI061507.PNT | 10HLA41AA003XB12 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 64.1914 | ok
873 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140106.PNT | 1LAI:AI140106.PNT | 10HNA10CP201 | A SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa | [6 empty] | -402.2461 | ok
874 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140206.PNT | 1LAI:AI140206.PNT | 10HNA20CP201 | B SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa | [6 empty] | -394.5703 | ok
875 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141504.PNT | 1LAI:AI141504.PNT | 10HNA10CT001 | A SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 349.8422 | ok
876 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 1 | ECONOMIZER #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141604.PNT | 1LAI:AI141604.PNT | 10HNA20CT001 | B SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 356.563 | ok
877 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1M_DRUMLVL.LT160708.PNT | 1M_DRUMLVL:LT160708.PNT | 10HAG10CL201 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | -85.5834 | ok
878 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1M_DRUMLVL.LT161108.PNT | 1M_DRUMLVL:LT161108.PNT | 10HAG10CL202 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | -2.5713 | ok
879 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1M_DRUMLVL.LT161208.PNT | 1M_DRUMLVL:LT161208.PNT | 10HAG10CL203 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | -0.6011 | ok
880 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1MAI.AI160707.PNT | 1MAI:AI160707.PNT | 10HAG10CP201 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 12.7886 | ok
881 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1MAI.AI161107.PNT | 1MAI:AI161107.PNT | 10HAG10CP202 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 12.7925 | ok
882 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 2 | STEAM DRUM #1 | 50-F296S-J0201-04 | OPC.AW1002.1MAI.AI161207.PNT | 1MAI:AI161207.PNT | 10HAG10CP203 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 12.7988 | ok
883 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154101.PNT | 1LAI:AI154101.PNT | 10HAG10CT001 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 329.7744 | ok
884 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154102.PNT | 1LAI:AI154102.PNT | 10HAG10CT002 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 329.6554 | ok
885 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154103.PNT | 1LAI:AI154103.PNT | 10HAG10CT003 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 329.1199 | ok
886 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154104.PNT | 1LAI:AI154104.PNT | 10HAG10CT004 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 331.1725 | ok
887 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154105.PNT | 1LAI:AI154105.PNT | 10HAG10CT005 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 328.9117 | ok
888 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154106.PNT | 1LAI:AI154106.PNT | 10HAG10CT006 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 328.1978 | ok
889 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154107.PNT | 1LAI:AI154107.PNT | 10HAG10CT007 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 329.3282 | ok
890 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154201.PNT | 1LAI:AI154201.PNT | 10HAG10CT008 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 328.6316 | ok
891 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154202.PNT | 1LAI:AI154202.PNT | 10HAG10CT009 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 328.8152 | ok
892 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154203.PNT | 1LAI:AI154203.PNT | 10HAG10CT010 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 327.7094 | ok
893 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154204.PNT | 1LAI:AI154204.PNT | 10HAG10CT011 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 328.4532 | ok
894 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154205.PNT | 1LAI:AI154205.PNT | 10HAG10CT012 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 5th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 328.8747 | ok
895 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 3 | WALL TUBE #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154206.PNT | 1LAI:AI154206.PNT | 10HAG10CT013 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 12th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 330.0943 | ok
896 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140305.PNT | 1LAI:AI140305.PNT | 10H10CP205 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -341.6445 | no
897 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051707.PNT | 1EAI:AI051707.PNT | 10H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 4.7656 | ok
898 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI052105.PNT | 1EAI:AI052105.PNT | 10H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 5.9425 | ok
899 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142208.PNT | 1LAI:AI142208.PNT | 10H10CT009 | A SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 371.7854 | ok
900 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140405.PNT | 1LAI:AI140405.PNT | 10H20CP205 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -349.25 | no
901 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI052304.PNT | 1EAI:AI052304.PNT | 10H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 6.5005 | ok
902 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI052401.PNT | 1EAI:AI052401.PNT | 10H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 4.9543 | ok
903 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154207.PNT | 1LAI:AI154207.PNT | 10HAH10CT001 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 493.4421 | ok
904 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154301.PNT | 1LAI:AI154301.PNT | 10HAH10CT002 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 501.2047 | ok
905 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154302.PNT | 1LAI:AI154302.PNT | 10HAH10CT003 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 470.2497 | ok
906 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154303.PNT | 1LAI:AI154303.PNT | 10HAH10CT004 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 469.9555 | ok
907 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154304.PNT | 1LAI:AI154304.PNT | 10HAH10CT005 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 4th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 520.97 | ok
908 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154305.PNT | 1LAI:AI154305.PNT | 10HAH10CT006 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 7th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 523.559 | ok
909 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154306.PNT | 1LAI:AI154306.PNT | 10HAH10CT007 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 10th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 519.6461 | ok
910 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154307.PNT | 1LAI:AI154307.PNT | 10HAH10CT008 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 12th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 524.118 | ok
911 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154401.PNT | 1LAI:AI154401.PNT | 10HAH10CT009 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FEOM LEFT 15th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 523.0573 | ok
912 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154402.PNT | 1LAI:AI154402.PNT | 10HAH10CT010 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 18th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 517.7617 | ok
913 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154403.PNT | 1LAI:AI154403.PNT | 10HAH10CT011 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 5th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 527.029 | ok
914 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154404.PNT | 1LAI:AI154404.PNT | 10HAH10CT012 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 20th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 538.238 | ok
915 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154405.PNT | 1LAI:AI154405.PNT | 10HAH10CT013 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 35th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 536.2964 | ok
916 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154406.PNT | 1LAI:AI154406.PNT | 10HAH10CT014 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 50th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 548.7117 | ok
917 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154407.PNT | 1LAI:AI154407.PNT | 10HAH10CT015 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 65th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 550.1532 | ok
918 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154501.PNT | 1LAI:AI154501.PNT | 10HAH10CT016 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 80th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 545.3271 | ok
919 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154502.PNT | 1LAI:AI154502.PNT | 10HAH10CT017 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 4th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 461.1763 | ok
920 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154503.PNT | 1LAI:AI154503.PNT | 10HAH10CT018 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 46th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 449.0986 | ok
921 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154504.PNT | 1LAI:AI154504.PNT | 10HAH10CT019 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 67th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 432.6183 | ok
922 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154505.PNT | 1LAI:AI154505.PNT | 10HAH10CT020 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 109th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 494.5185 | ok
923 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141701.PNT | 1LAI:AI141701.PNT | 10HAH11CT001 | SUPERHEATER 1st STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 467.7693 | ok
924 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060201.PNT | 1FAI:AI060201.PNT | 10HAH11CT002 | SUPERHEATER 1st STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 419.6299 | ok
925 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060301.PNT | 1FAI:AI060301.PNT | 10HAH11CT003 | SUPERHEATER 1st STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 422.1143 | ok
926 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141702.PNT | 1LAI:AI141702.PNT | 10HAH21CT001 | SUPERHEATER 2nd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 459.385 | ok
927 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060202.PNT | 1FAI:AI060202.PNT | 10HAH21CT002 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 435.5749 | ok
928 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060302.PNT | 1FAI:AI060302.PNT | 10HAH21CT003 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 433.7406 | ok
929 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141704.PNT | 1LAI:AI141704.PNT | 10HAH21CT004 | SUPERHEATER 3rd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 517.4893 | ok
930 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060204.PNT | 1FAI:AI060204.PNT | 10HAH21CT005 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 505.2389 | ok
931 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060303.PNT | 1FAI:AI060303.PNT | 10HAH21CT006 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 505.0774 | ok
932 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141703.PNT | 1LAI:AI141703.PNT | 10HAH22CT001 | SUPERHEATER 2nd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 450.4904 | ok
933 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060401.PNT | 1FAI:AI060401.PNT | 10HAH22CT002 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 448.8801 | ok
934 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060203.PNT | 1FAI:AI060203.PNT | 10HAH22CT003 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 451.6685 | ok
935 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141705.PNT | 1LAI:AI141705.PNT | 10HAH22CT004 | SUPERHEATER 3rd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 516.7244 | ok
936 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060402.PNT | 1FAI:AI060402.PNT | 10HAH22CT005 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 497.2444 | ok
937 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060205.PNT | 1FAI:AI060205.PNT | 10HAH22CT006 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 498.3251 | ok
938 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI140507.PNT | 1LAI:AI140507.PNT | 10LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 13.3525 | ok
939 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI142104.PNT | 1LAI:AI142104.PNT | 10LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃ | [6 empty] | 145.2754 | ok
940 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_SH1.AO063502.OUT | 1F_SH1:AO063502.OUT | 10LAE41AA101XB11 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 34.3226 | ok
941 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI061706.PNT | 1FAI:AI061706.PNT | 10LAE41AA101XB12 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 34.4219 | ok
942 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.1SHCALCA.RO01 | 1F_FLOW:1SHCALCA.RO01 | 10LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 33.144 | ok
943 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_SH2A.AO063406.OUT | 1F_SH2A:AO063406.OUT | 10LAE42AA101XB11 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 47.3581 | ok
944 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI062102.PNT | 1FAI:AI062102.PNT | 10LAE42AA101XB12 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 47.7324 | ok
945 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.2SHACALCA.RO01 | 1F_FLOW:2SHACALCA.RO01 | 10LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 15.8301 | ok
946 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_SH2B.AO063503.OUT | 1F_SH2B:AO063503.OUT | 10LAE43AA101XB11 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0.75212 | ok
947 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI061707.PNT | 1FAI:AI061707.PNT | 10LAE43AA101XB12 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.15039 | ok
948 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.2SHBCALCA.RO01 | 1F_FLOW:2SHBCALCA.RO01 | 10LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 0 | ok
949 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_SH3A.AO063407.OUT | 1F_SH3A:AO063407.OUT | 10LAE44AA101XB11 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 18.1819 | ok
950 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI062103.PNT | 1FAI:AI062103.PNT | 10LAE44AA101XB12 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 18.7227 | ok
951 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.3SHACALCA.RO01 | 1F_FLOW:3SHACALCA.RO01 | 10LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 12.0463 | ok
952 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_SH3B.AO063504.OUT | 1F_SH3B:AO063504.OUT | 10LAE45AA101XB11 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 19.0558 | ok
953 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI062104.PNT | 1FAI:AI062104.PNT | 10LAE45AA101XB12 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 19.4258 | ok
954 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.3SHBCALCA.RO01 | 1F_FLOW:3SHBCALCA.RO01 | 10LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 0 | ok
955 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI140307.PNT | 1LAI:AI140307.PNT | 10LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa |  |  | 0 | 17.41 |  |  | 12.0869 | ok
956 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160401.PNT | 1MAI:AI160401.PNT | 10LBA10CP202 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.9338 | ok
957 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160501.PNT | 1MAI:AI160501.PNT | 10LBA10CP203 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.9416 | ok
958 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160601.PNT | 1MAI:AI160601.PNT | 10LBA10CP204 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.9175 | ok
959 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060206.PNT | 1FAI:AI060206.PNT | 10LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 536.6596 | ok
960 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060304.PNT | 1FAI:AI060304.PNT | 10LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 536.6158 | ok
961 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1M_MSTFLOW_1.SIGSEL1OUT.PNT | 1M_MSTFLOW_1:SIGSEL1OUT.PNT | 10LBA10CP101C1 | MAIN STEAM PRESSURE SIGSEL | AI | 0 | 20 | MPa | [6 empty] | 11.9377 | ok
962 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1M_MSTFLOW.SWCH2OUT.PNT | 1M_MSTFLOW:SWCH2OUT.PNT | 10LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h | [6 empty] | 608.4485 | ok
963 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1F_SH3A_2.SIGSEL1OUT.PNT | 1F_SH3A_2:SIGSEL1OUT.PNT | 10LBA10CT001C1 | MAIN STEAM TEMPERATURE SIGSEL | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 536.6352 | ok
964 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154605.PNT | 1LAI:AI154605.PNT | 10HAJ10CT001 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 3th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 491.354 | ok
965 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154606.PNT | 1LAI:AI154606.PNT | 10HAJ10CT002 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 9th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 510.8839 | ok
966 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154607.PNT | 1LAI:AI154607.PNT | 10HAJ10CT003 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 16th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 533.2188 | ok
967 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154701.PNT | 1LAI:AI154701.PNT | 10HAJ10CT004 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 22th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 542.6884 | ok
968 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154702.PNT | 1LAI:AI154702.PNT | 10HAJ10CT005 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 28th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 544.8949 | ok
969 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154703.PNT | 1LAI:AI154703.PNT | 10HAJ10CT006 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 37th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 545.6599 | ok
970 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154704.PNT | 1LAI:AI154704.PNT | 10HAJ10CT007 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 43th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 550.5142 | ok
971 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154705.PNT | 1LAI:AI154705.PNT | 10HAJ10CT008 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 49th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 538.9226 | ok
972 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154706.PNT | 1LAI:AI154706.PNT | 10HAJ10CT009 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 56th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 557.3102 | ok
973 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154707.PNT | 1LAI:AI154707.PNT | 10HAJ10CT010 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 62th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 527.6547 | ok
974 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141708.PNT | 1LAI:AI141708.PNT | 10HAJ21CT001 | REHEATER DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 386.4132 | ok
975 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060307.PNT | 1FAI:AI060307.PNT | 10HAJ21CT002 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 229.9957 | ok
976 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060404.PNT | 1FAI:AI060404.PNT | 10HAJ21CT003 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 231.3861 | ok
977 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI142101.PNT | 1LAI:AI142101.PNT | 10HAJ22CT001 | REHEATER DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 380.4319 | ok
978 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060405.PNT | 1FAI:AI060405.PNT | 10HAJ22CT002 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 271.8951 | ok
979 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060406.PNT | 1FAI:AI060406.PNT | 10HAJ22CT003 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 278.1703 | ok
980 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154506.PNT | 1LAI:AI154506.PNT | 10HAK10CT001 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 3th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 459.8377 | ok
981 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154507.PNT | 1LAI:AI154507.PNT | 10HAK10CT002 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 8th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 478.7199 | ok
982 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154601.PNT | 1LAI:AI154601.PNT | 10HAK10CT003 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 13th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 490.7361 | ok
983 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154602.PNT | 1LAI:AI154602.PNT | 10HAK10CT004 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 17th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 482.5867 | ok
984 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154603.PNT | 1LAI:AI154603.PNT | 10HAK10CT005 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 22th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 494.7079 | ok
985 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-16 | OPC.AW1002.1LAI.AI154604.PNT | 1LAI:AI154604.PNT | 10HAK10CT006 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 28th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 489.677 | ok
986 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI140506.PNT | 1LAI:AI140506.PNT | 10LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa | [6 empty] | 7.0657 | ok
987 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1LAI.AI142103.PNT | 1LAI:AI142103.PNT | 10LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃ | [6 empty] | 144.2813 | ok
988 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_RHEMG.AO063404.OUT | 1F_RHEMG:AO063404.OUT | 10LAF61AA101XB11 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
989 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI061704.PNT | 1FAI:AI061704.PNT | 10LAF61AA101XB12 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.56055 | ok
990 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.RHCALCA.RO01 | 1F_FLOW:RHCALCA.RO01 | 10LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 0 | ok
991 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_RHA.AO063405.OUT | 1F_RHA:AO063405.OUT | 10LAF62AA101XB11 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0.0088242 | ok
992 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI061705.PNT | 1FAI:AI061705.PNT | 10LAF62AA101XB12 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.14648 | no
993 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.RHACALCA.RO01 | 1F_FLOW:RHACALCA.RO01 | 10LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 13.0821 | ok
994 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_RHB.AO063501.OUT | 1F_RHB:AO063501.OUT | 10LAF63AA101XB11 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 8.1689 | ok
995 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1FAI.AI062101.PNT | 1FAI:AI062101.PNT | 10LAF63AA101XB12 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 5.666 | ok
996 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-08 | OPC.AW1002.1F_FLOW.RHBCALCA.RO01 | 1F_FLOW:RHBCALCA.RO01 | 10LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 5.403 | ok
997 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI140505.PNT | 1LAI:AI140505.PNT | 10LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa |  |  | 0 |  |  |  | 2.1593 | ok
998 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI142102.PNT | 1LAI:AI142102.PNT | 10LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 540.5527 | ok
999 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI140406.PNT | 1LAI:AI140406.PNT | 10LBC21CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa | [6 empty] | 2.2614 | ok
1000 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141706.PNT | 1LAI:AI141706.PNT | 10LBC21CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 333.6273 | ok
1001 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060207.PNT | 1FAI:AI060207.PNT | 10LBC21CT002 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 332.3791 | ok
1002 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060305.PNT | 1FAI:AI060305.PNT | 10LBC21CT003 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 332.3348 | ok
1003 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI140407.PNT | 1LAI:AI140407.PNT | 10LBC22CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa | [6 empty] | 2.2532 | ok
1004 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1LAI.AI141707.PNT | 1LAI:AI141707.PNT | 10LBC22CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 333.3428 | ok
1005 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060403.PNT | 1FAI:AI060403.PNT | 10LBC22CT002 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 332.4168 | ok
1006 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1FAI.AI060306.PNT | 1FAI:AI060306.PNT | 10LBC22CT003 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 332.3943 | ok
1007 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1PMS.RSFLOW.RO01 | 1PMS:RSFLOW.RO01 | 10LBB10CF101C1 | RH STEAM OUTLET FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | 561.2693 | ok
1008 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 5 | REHEATER #1 | 50-F296S-J0201-04 | OPC.AW1002.1PMS.RSFLOW.RO02 | 1PMS:RSFLOW.RO02 | 10LBB10CF101C2 | RH STM FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | 542.7842 | ok
1009 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOT BLOWER #1 | K0601-02 | OPC.AW1002.1EAI.AI052106.PNT | 1EAI:AI052106.PNT | 10HCB10AA101XB12 | BOILER SOOTBLOWER STEAM PRESSURE POSITION | AI | 0 | 100 | % | [6 empty] | -1.1309 | no
1010 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOT BLOWER #1 | K0601-02 | OPC.AW1002.1EAI.AI051405.PNT | 1EAI:AI051405.PNT | 10HCB10CP201 | BOILER SOOTBLOWER STEAM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 0.012891 | ok
1011 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 6 | SOOT BLOWER #1 | K0601-02 | OPC.AW1002.1E_BLCV.AO053106.OUT | 1E_BLCV:AO053106.OUT | 10HCB10AA101XB11 | BOILER SOOTBLOWER STEAM PRESSURE CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1012 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051402.PNT | 1EAI:AI051402.PNT | 10H10CP201 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -11.8125 | ok
1013 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051306.PNT | 1EAI:AI051306.PNT | 10H10CP202 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -91.1602 | ok
1014 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140303.PNT | 1LAI:AI140303.PNT | 10H10CP203 | A SIDE FURNACE PRESSURE | AI | -2000 | 2000 | Pa | [6 empty] | 4.8438 | ok
1015 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140304.PNT | 1LAI:AI140304.PNT | 10H10CP204 | A SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -50.5859 | ok
1016 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142201.PNT | 1LAI:AI142201.PNT | 10H10CT002 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 815.6884 | ok
1017 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142202.PNT | 1LAI:AI142202.PNT | 10H10CT003 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 687.3987 | ok
1018 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142203.PNT | 1LAI:AI142203.PNT | 10H10CT004 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 625.2928 | ok
1019 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142204.PNT | 1LAI:AI142204.PNT | 10H10CT005 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 576.5142 | ok
1020 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142205.PNT | 1LAI:AI142205.PNT | 10H10CT006 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 562.0983 | ok
1021 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142206.PNT | 1LAI:AI142206.PNT | 10H10CT007 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 512.0841 | ok
1022 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142207.PNT | 1LAI:AI142207.PNT | 10H10CT008 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 511.2309 | ok
1023 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051307.PNT | 1EAI:AI051307.PNT | 10H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 465.2188 | ok
1024 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051401.PNT | 1EAI:AI051401.PNT | 10H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 469.9375 | ok
1025 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1JAI.AI112703.PNT | 1JAI:AI112703.PNT | 10H10GC001AI01 | A SIDE PROBE POSITION SIGNAL | AI | 0 | 100 | % | [6 empty] | 34.1699 | ok
1026 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1JAI.AI112704.PNT | 1JAI:AI112704.PNT | 10H10GC001AI02 | A SIDE PROBE TEMPERATURE SIGNAL | AI | 0 | 800 | C |  |  |  | 540 | 560 |  | 209.9062 | ok
1027 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051207.PNT | 1EAI:AI051207.PNT | 10H20CP201 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -7.5234 | ok
1028 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051502.PNT | 1EAI:AI051502.PNT | 10H20CP202 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -8.1914 | ok
1029 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140403.PNT | 1LAI:AI140403.PNT | 10H20CP203 | B SIDE FURNACE PRESSURE | AI | -2000 | 2000 | Pa | [6 empty] | -8.3594 | ok
1030 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI140404.PNT | 1LAI:AI140404.PNT | 10H20CP204 | B SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -55.625 | ok
1031 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142301.PNT | 1LAI:AI142301.PNT | 10H20CT002 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 805.6078 | ok
1032 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142302.PNT | 1LAI:AI142302.PNT | 10H20CT003 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 767.9602 | ok
1033 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142303.PNT | 1LAI:AI142303.PNT | 10H20CT004 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 647.726 | ok
1034 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142304.PNT | 1LAI:AI142304.PNT | 10H20CT005 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 610.5095 | ok
1035 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142305.PNT | 1LAI:AI142305.PNT | 10H20CT006 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 584.149 | ok
1036 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142306.PNT | 1LAI:AI142306.PNT | 10H20CT007 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 538.2537 | ok
1037 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142307.PNT | 1LAI:AI142307.PNT | 10H20CT008 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 531.1927 | ok
1038 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1LAI.AI142308.PNT | 1LAI:AI142308.PNT | 10H20CT009 | B SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 386.1689 | ok
1039 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051403.PNT | 1EAI:AI051403.PNT | 10H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 522.5625 | ok
1040 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1EAI.AI051501.PNT | 1EAI:AI051501.PNT | 10H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 535.8438 | ok
1041 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1JAI.AI112705.PNT | 1JAI:AI112705.PNT | 10H20GC001AI01 | B SIDE PROBE POSITION SIGNAL | AI | 0 | 100 | % | [6 empty] | 0.16406 | ok
1042 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1JAI.AI112706.PNT | 1JAI:AI112706.PNT | 10H20GC001AI02 | B SIDE PROBE TEMPERATURE SIGNAL | AI | 0 | 800 | C |  |  |  | 540 | 560 |  | -8.0781 | no
1043 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051105.PNT | 1EAI:AI051105.PNT | 10HLA10CF201 | FURNACE A-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | 77.3282 | ok
1044 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051202.PNT | 1EAI:AI051202.PNT | 10HLA10CF202 | FURNACE A-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h | [6 empty] | 76.4138 | ok
1045 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051106.PNT | 1EAI:AI051106.PNT | 10HLA20CF201 | FURNACE B-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | 89.045 | ok
1046 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051203.PNT | 1EAI:AI051203.PNT | 10HLA20CF202 | FURNACE B-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h | [6 empty] | 85.3004 | ok
1047 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_PAF.AO052502.OUT | 1E_PAF:AO052502.OUT | 10HFE10AA101XB11 | PAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 44.233 | ok
1048 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051602.PNT | 1EAI:AI051602.PNT | 10HFE10AA101XB12 | PAF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 44.6328 | ok
1049 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1JAI.AI111102.PNT | 1JAI:AI111102.PNT | 10HFE10AN001XB13 | PAF A CURRENT | AI | 0 | 300 | A | [6 empty] | 145.0957 | ok
1050 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140103.PNT | 1LAI:AI140103.PNT | 10HFE10CP201 | PAF A OUTLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.1613 | ok
1051 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141502.PNT | 1LAI:AI141502.PNT | 10HFE10CT001 | PAF A INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 23.3254 | ok
1052 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111407.PNT | 1JAI:AI111407.PNT | 10HFE10CT006 | PAF A MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 72.201 | ok
1053 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111507.PNT | 1JAI:AI111507.PNT | 10HFE10CT007 | PAF A MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 71.8373 | ok
1054 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111603.PNT | 1JAI:AI111603.PNT | 10HFE10CT008 | PAF A MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 73.2533 | ok
1055 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111701.PNT | 1JAI:AI111701.PNT | 10HFE10CT009 | PAF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 55.7677 | ok
1056 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI112101.PNT | 1JAI:AI112101.PNT | 10HFE10CT010 | PAF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 47.7394 | ok
1057 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111702.PNT | 1JAI:AI111702.PNT | 10HFE10CT011 | PAF A NON DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 49.9608 | ok
1058 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI112102.PNT | 1JAI:AI112102.PNT | 10HFE10CT012 | PAF A DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 43.4914 | ok
1059 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111205.PNT | 1JAI:AI111205.PNT | 10HFE10CY001X | PAF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.92421 | ok
1060 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111301.PNT | 1JAI:AI111301.PNT | 10HFE10CY001Y | PAF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.73125 | ok
1061 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111206.PNT | 1JAI:AI111206.PNT | 10HFE10CY002X | PAF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.0187 | ok
1062 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 1 | PAF #1A | 50-F296S-J0201-36 | OPC.AW1002.1JAI.AI111302.PNT | 1JAI:AI111302.PNT | 10HFE10CY002Y | PAF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.8707 | ok
1063 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140101.PNT | 1LAI:AI140101.PNT | 10HLA10CP201 | FDF A OUTLET AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 1.052 | ok
1064 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141501.PNT | 1LAI:AI141501.PNT | 10HLA10CT001 | FDF A INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 23.0383 | ok
1065 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_FDF.AO052501.OUT | 1E_FDF:AO052501.OUT | 10HLB10AA101XB11 | FDF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 7 | ok
1066 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051601.PNT | 1EAI:AI051601.PNT | 10HLB10AA101XB12 | FDF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 6.9297 | ok
1067 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1JAI.AI111101.PNT | 1JAI:AI111101.PNT | 10HLB10AN001XB13 | FDF A CURRENT | AI | 0 | 200 | A | [6 empty] | 23.9102 | ok
1068 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111401.PNT | 1JAI:AI111401.PNT | 10HLB10CT001 | FDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 52.7668 | ok
1069 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111501.PNT | 1JAI:AI111501.PNT | 10HLB10CT002 | FDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 53.4034 | ok
1070 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111402.PNT | 1JAI:AI111402.PNT | 10HLB10CT003 | FDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 52.8188 | ok
1071 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111502.PNT | 1JAI:AI111502.PNT | 10HLB10CT004 | FDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 52.1693 | ok
1072 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111403.PNT | 1JAI:AI111403.PNT | 10HLB10CT005 | FDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 52.7668 | ok
1073 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111503.PNT | 1JAI:AI111503.PNT | 10HLB10CT006 | FDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 53.1955 | ok
1074 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111404.PNT | 1JAI:AI111404.PNT | 10HLB10CT007 | FDF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 43.3615 | ok
1075 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111504.PNT | 1JAI:AI111504.PNT | 10HLB10CT008 | FDF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 30.3708 | ok
1076 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111405.PNT | 1JAI:AI111405.PNT | 10HLB10CT009 | FDF A NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 38.0613 | ok
1077 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111505.PNT | 1JAI:AI111505.PNT | 10HLB10CT010 | FDF A NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 37.5806 | ok
1078 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111601.PNT | 1JAI:AI111601.PNT | 10HLB10CT011 | FDF A NON DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 38.0223 | ok
1079 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111406.PNT | 1JAI:AI111406.PNT | 10HLB10CT012 | FDF A DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 35.4891 | ok
1080 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111506.PNT | 1JAI:AI111506.PNT | 10HLB10CT013 | FDF A DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 35.3592 | ok
1081 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111602.PNT | 1JAI:AI111602.PNT | 10HLB10CT014 | FDF A DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 35.5281 | ok
1082 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111106.PNT | 1JAI:AI111106.PNT | 10HLB10CY001X | FDF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.93437 | ok
1083 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111203.PNT | 1JAI:AI111203.PNT | 10HLB10CY001Y | FDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.50977 | ok
1084 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111107.PNT | 1JAI:AI111107.PNT | 10HLB10CY002X | FDF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.38224 | ok
1085 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 2 | FDF #1A | 50-F296S-J0201-35 | OPC.AW1002.1JAI.AI111204.PNT | 1JAI:AI111204.PNT | 10HLB10CY002Y | FDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.27374 | ok
1086 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140104.PNT | 1LAI:AI140104.PNT | 10HFE10CP202 | APH A INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.6199 | ok
1087 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140105.PNT | 1LAI:AI140105.PNT | 10HFE10CP203 | APH A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 9.4711 | ok
1088 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050105.PNT | 1EAI:AI050105.PNT | 10HFE10CT002 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.8355 | ok
1089 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050203.PNT | 1EAI:AI050203.PNT | 10HFE10CT003 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.4378 | ok
1090 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050303.PNT | 1EAI:AI050303.PNT | 10HFE10CT004 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 0 | ok
1091 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141503.PNT | 1LAI:AI141503.PNT | 10HFE10CT005 | APH A OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 322.4145 | ok
1092 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140102.PNT | 1LAI:AI140102.PNT | 10HLA10CP202 | APH A INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.96211 | ok
1093 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050701.PNT | 1EAI:AI050701.PNT | 10HLA10CP203 | APH A OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | -0.00039063 | no
1094 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050101.PNT | 1EAI:AI050101.PNT | 10HLA10CT002 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 27.1156 | ok
1095 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050201.PNT | 1EAI:AI050201.PNT | 10HLA10CT003 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 25.2008 | ok
1096 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050301.PNT | 1EAI:AI050301.PNT | 10HLA10CT004 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 24.9043 | ok
1097 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050102.PNT | 1EAI:AI050102.PNT | 10HLA10CT005 | APH A OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 317.3586 | ok
1098 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAI.AI111104.PNT | 1JAI:AI111104.PNT | 10HLD11GC001AI01 | AIR PREHEATER A MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 14.3301 | ok
1099 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAI.AI111201.PNT | 1JAI:AI111201.PNT | 10HLD11GC001AI02 | AIR PREHEATER A AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 0.14746 | ok
1100 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAI.AI111105.PNT | 1JAI:AI111105.PNT | 10HLD11GC001AI03 | AIR PREHEATER A MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 986.6908 | ok
1101 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAI.AI111202.PNT | 1JAI:AI111202.PNT | 10HLD11GC001AI04 | AIR PREHEATER A AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 10.7609 | ok
1102 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAH.AO112601.OUT | 1JAH:AO112601.OUT | 10HLD11GC001AO01 | AIR PREHEATER A MAIN MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | -1 | no
1103 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-38 | OPC.AW1002.1JAH.AO112602.OUT | 1JAH:AO112602.OUT | 10HLD11GC001AO02 | AIR PREHEATER A AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | -1 | no
1104 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140107.PNT | 1LAI:AI140107.PNT | 10HNA10CP202 | APH A OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa | [6 empty] | -1746.1035 | ok
1105 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050206.PNT | 1EAI:AI050206.PNT | 10HNA10CT002 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 149.3323 | ok
1106 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050306.PNT | 1EAI:AI050306.PNT | 10HNA10CT003 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 143.695 | ok
1107 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050403.PNT | 1EAI:AI050403.PNT | 10HNA10CT004 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 138.0219 | ok
1108 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141507.PNT | 1LAI:AI141507.PNT | 10LCN10CT001 | STEAM AIR HEATER DRAIN WATER TEMP. | TC | 0 | 400 | ℃ | [6 empty] | 59.3792 | ok
1109 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | F296S-J0201-06 | OPC.AW1002.1M_GLDSED.AO162403.OUT | 1M_GLDSED:AO162403.OUT | 10LBG41AA101XB11 | AUXILIARY STEAM TO SECONDARY AIR HEATER CONTRL VALVE CONTROL SIGNAL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1110 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | F296S-J0201-06 | OPC.AW1002.1MAI.AI161403.PNT | 1MAI:AI161403.PNT | 10LBG41AA101XB12 | AUXILIARY STEAM TO SECONDARY AIR HEATER CONTRL VALVE POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0 | ok | TIDAK DIOPERASIKAN
1111 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | F296S-J0201-06 | OPC.AW1002.1M_GLDPRI.AO162404.OUT | 1M_GLDPRI:AO162404.OUT | 10LBG42AA101XB11 | AUXILIARY STEAM TO PRIMARY AIR HEATER CONTRL VALVE CONTROL SIGNAL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1112 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 4 | AIR HEATER #1A | F296S-J0201-06 | OPC.AW1002.1MAI.AI161404.PNT | 1MAI:AI161404.PNT | 10LBG42AA101XB12 | AUXILIARY STEAM TO PRIMARY AIR HEATER CONTRL VALVE POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0 | ok | TIDAK DIOPERASIKAN
1113 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050702.PNT | 1EAI:AI050702.PNT | 10HFE50CP201 | PRIMARY HOT AIR HEADER PRESSURE 1 | AI | 0 | 20 | KPa | [6 empty] | 9.2445 | ok
1114 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051102.PNT | 1EAI:AI051102.PNT | 10HFE50CP202 | PRIMARY HOT AIR HEADER PRESSURE 2 | AI | 0 | 20 | KPa | [6 empty] | 9.2262 | ok
1115 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 5 | DUCTING HOT AIR #1 | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051201.PNT | 1EAI:AI051201.PNT | 10HFE50CP203 | PRIMARY HOT AIR HEADER PRESSURE 3 | AI | 0 | 20 | KPa | [6 empty] | 9.2383 | ok
1116 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1E_PAF.AO053205.OUT | 1E_PAF:AO053205.OUT | 10HFE20AA101XB11 | PAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 44.2209 | ok
1117 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051702.PNT | 1EAI:AI051702.PNT | 10HFE20AA101XB12 | PAF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 44.4062 | ok
1118 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1KAI.AI131102.PNT | 1KAI:AI131102.PNT | 10HFE20AN001XB13 | PAF B CURRENT | AI | 0 | 300 | A | [6 empty] | 140.5488 | ok
1119 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140203.PNT | 1LAI:AI140203.PNT | 10HFE20CP201 | PAF B OUTLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.4969 | ok
1120 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141602.PNT | 1LAI:AI141602.PNT | 10HFE20CT001 | PAF B INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 25.4524 | ok
1121 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1KAI.AI131407.PNT | 1KAI:AI131407.PNT | 10HFE20CT006 | PAF B MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 69.6029 | ok
1122 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1KAI.AI131507.PNT | 1KAI:AI131507.PNT | 10HFE20CT007 | PAF B MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 69.369 | ok
1123 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1KAI.AI131603.PNT | 1KAI:AI131603.PNT | 10HFE20CT008 | PAF B MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 70.5772 | ok
1124 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-03 | OPC.AW1002.1KAI.AI131701.PNT | 1KAI:AI131701.PNT | 10HFE20CT009 | PAF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 61.1329 | ok
1125 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-08 | OPC.AW1002.1KAI.AI132101.PNT | 1KAI:AI132101.PNT | 10HFE20CT010 | PAF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 55.339 | ok
1126 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-08 | OPC.AW1002.1KAI.AI131702.PNT | 1KAI:AI131702.PNT | 10HFE20CT011 | PAF B NON DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 49.2074 | ok
1127 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-K1003-02 | OPC.AW1002.1KAI.AI132102.PNT | 1KAI:AI132102.PNT | 10HFE20CT012 | PAF B DRIVED END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 85 |  | 49.2463 | ok
1128 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1KAI.AI131205.PNT | 1KAI:AI131205.PNT | 10HFE20CY001X | PAF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.9102 | ok
1129 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1KAI.AI131301.PNT | 1KAI:AI131301.PNT | 10HFE20CY001Y | PAF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.034 | ok
1130 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1KAI.AI131206.PNT | 1KAI:AI131206.PNT | 10HFE20CY002X | PAF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.2582 | ok
1131 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 6 | PAF #1B | 50-F296S-J0201-02 | OPC.AW1002.1KAI.AI131302.PNT | 1KAI:AI131302.PNT | 10HFE20CY002Y | PAF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.0387 | ok
1132 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140201.PNT | 1LAI:AI140201.PNT | 10HLA20CP201 | FDF B OUTLET AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.95752 | ok
1133 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141601.PNT | 1LAI:AI141601.PNT | 10HLA20CT001 | FDF B INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 23.6675 | ok
1134 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_FDF.AO052601.OUT | 1E_FDF:AO052601.OUT | 10HLB20AA101XB11 | FDF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 6 | ok
1135 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051701.PNT | 1EAI:AI051701.PNT | 10HLB20AA101XB12 | FDF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 5.8496 | ok
1136 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1KAI.AI131101.PNT | 1KAI:AI131101.PNT | 10HLB20AN001XB13 | FDF B CURRENT | AI | 0 | 200 | A | [6 empty] | 22.8984 | ok
1137 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131401.PNT | 1KAI:AI131401.PNT | 10HLB20CT001 | FDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 55.1701 | ok
1138 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131501.PNT | 1KAI:AI131501.PNT | 10HLB20CT002 | FDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 54.4686 | ok
1139 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131402.PNT | 1KAI:AI131402.PNT | 10HLB20CT003 | FDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 52.9617 | ok
1140 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131502.PNT | 1KAI:AI131502.PNT | 10HLB20CT004 | FDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 54.4297 | ok
1141 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131403.PNT | 1KAI:AI131403.PNT | 10HLB20CT005 | FDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 53.8061 | ok
1142 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131503.PNT | 1KAI:AI131503.PNT | 10HLB20CT006 | FDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 54.0269 | ok
1143 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131404.PNT | 1KAI:AI131404.PNT | 10HLB20CT007 | FDF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 45.8687 | ok
1144 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131504.PNT | 1KAI:AI131504.PNT | 10HLB20CT008 | FDF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 34.19 | ok
1145 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131405.PNT | 1KAI:AI131405.PNT | 10HLB20CT009 | FDF B NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 42.2573 | ok
1146 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131505.PNT | 1KAI:AI131505.PNT | 10HLB20CT010 | FDF B NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 41.9195 | ok
1147 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131601.PNT | 1KAI:AI131601.PNT | 10HLB20CT011 | FDF B NON DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 43.0108 | ok
1148 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131406.PNT | 1KAI:AI131406.PNT | 10HLB20CT012 | FDF B DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 49.5321 | ok
1149 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131506.PNT | 1KAI:AI131506.PNT | 10HLB20CT013 | FDF B DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 52.559 | ok
1150 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131602.PNT | 1KAI:AI131602.PNT | 10HLB20CT014 | FDF B DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 50.3246 | ok
1151 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131106.PNT | 1KAI:AI131106.PNT | 10HLB20CY001X | FDF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.5191 | ok
1152 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131203.PNT | 1KAI:AI131203.PNT | 10HLB20CY001Y | FDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.96641 | ok
1153 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131107.PNT | 1KAI:AI131107.PNT | 10HLB20CY002X | FDF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.1883 | ok
1154 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 7 | FDF #1B | 50-F296S-J0201-35 | OPC.AW1002.1KAI.AI131204.PNT | 1KAI:AI131204.PNT | 10HLB20CY002Y | FDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.1215 | ok
1155 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140204.PNT | 1LAI:AI140204.PNT | 10HFE20CP202 | APH B INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.2941 | ok
1156 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140205.PNT | 1LAI:AI140205.PNT | 10HFE20CP203 | APH B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 9.3938 | ok
1157 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050106.PNT | 1EAI:AI050106.PNT | 10HFE20CT002 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.9566 | ok
1158 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050204.PNT | 1EAI:AI050204.PNT | 10HFE20CT003 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.6193 | ok
1159 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050304.PNT | 1EAI:AI050304.PNT | 10HFE20CT004 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 15.6982 | ok
1160 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141603.PNT | 1LAI:AI141603.PNT | 10HFE20CT005 | APH B OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 327.9752 | ok
1161 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140202.PNT | 1LAI:AI140202.PNT | 10HLA20CP202 | APH B INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.90488 | ok
1162 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051101.PNT | 1EAI:AI051101.PNT | 10HLA20CP203 | APH B OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.54111 | ok
1163 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050103.PNT | 1EAI:AI050103.PNT | 10HLA20CT002 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 26.0823 | ok
1164 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050202.PNT | 1EAI:AI050202.PNT | 10HLA20CT003 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 26.5473 | ok
1165 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050302.PNT | 1EAI:AI050302.PNT | 10HLA20CT004 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 25.5306 | ok
1166 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050104.PNT | 1EAI:AI050104.PNT | 10HLA20CT005 | APH B OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 324.3791 | ok
1167 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1KAI.AI131104.PNT | 1KAI:AI131104.PNT | 10HLD12GC001AI01 | AIR PREHEATER B MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 14.5367 | ok
1168 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1KAI.AI131201.PNT | 1KAI:AI131201.PNT | 10HLD12GC001AI02 | AIR PREHEATER B AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 0.002539 | ok
1169 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1KAI.AI131105.PNT | 1KAI:AI131105.PNT | 10HLD12GC001AI03 | AIR PREHEATER B MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 989.381 | ok
1170 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1KAI.AI131202.PNT | 1KAI:AI131202.PNT | 10HLD12GC001AI04 | AIR PREHEATER B AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 12.9018 | ok
1171 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1JAH.AO112603.OUT | 1JAH:AO112603.OUT | 10HLD12GC001AO01 | AIR PREHEATER B MAIN MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | -1 | no
1172 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-38 | OPC.AW1002.1JAH.AO112604.OUT | 1JAH:AO112604.OUT | 10HLD12GC001AO02 | AIR PREHEATER B AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | -1 | no
1173 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140207.PNT | 1LAI:AI140207.PNT | 10HNA20CP202 | APH B OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa | [6 empty] | -1706.7969 | ok
1174 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050207.PNT | 1EAI:AI050207.PNT | 10HNA20CT002 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 158.1238 | ok
1175 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050307.PNT | 1EAI:AI050307.PNT | 10HNA20CT003 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 150.0944 | ok
1176 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 8 | AIR HEATER #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI050404.PNT | 1EAI:AI050404.PNT | 10HNA20CT004 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 143.5116 | ok
1177 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140301.PNT | 1LAI:AI140301.PNT | 10HNA11CP201 | ESP A OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa | [6 empty] | -2344.2383 | ok
1178 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141505.PNT | 1LAI:AI141505.PNT | 10HNA11CT001 | ESP A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 138.3994 | ok
1179 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140302.PNT | 1LAI:AI140302.PNT | 10HNA12CP201 | IDF A OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa | [6 empty] | 293.3789 | ok
1180 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141506.PNT | 1LAI:AI141506.PNT | 10HNA12CT001 | IDF A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 140.4821 | ok
1181 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1E_IDF.AO052705.OUT | 1E_IDF:AO052705.OUT | 10HNC11AA101XB11 | IDF A INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 49.0917 | ok
1182 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI051705.PNT | 1EAI:AI051705.PNT | 10HNC11AA101XB12 | IDF A INLET STATIONARY BLADE POSITION | AI | 0 | 100 | % | [6 empty] | 49.5254 | ok
1183 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111103.PNT | 1JAI:AI111103.PNT | 10HNC11AN001XB13 | IDF A CURRENT | AI | 0 | 400 | A | [6 empty] | 124.5078 | ok
1184 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111305.PNT | 1JAI:AI111305.PNT | 10HNC11AN002XB13 | IDF A #1 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | -0.072656 | no
1185 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111306.PNT | 1JAI:AI111306.PNT | 10HNC11AN003XB13 | IDF A #2 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | 9.8461 | ok
1186 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111703.PNT | 1JAI:AI111703.PNT | 10HNC11CT001 | IDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.7143 | ok
1187 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI112103.PNT | 1JAI:AI112103.PNT | 10HNC11CT002 | IDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.0258 | ok
1188 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111704.PNT | 1JAI:AI111704.PNT | 10HNC11CT003 | IDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 51.4288 | ok
1189 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI112104.PNT | 1JAI:AI112104.PNT | 10HNC11CT004 | IDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 51.4158 | ok
1190 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111705.PNT | 1JAI:AI111705.PNT | 10HNC11CT005 | IDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.5974 | ok
1191 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI112105.PNT | 1JAI:AI112105.PNT | 10HNC11CT006 | IDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.1037 | ok
1192 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111706.PNT | 1JAI:AI111706.PNT | 10HNC11CT007 | IDF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 44.089 | ok
1193 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI112106.PNT | 1JAI:AI112106.PNT | 10HNC11CT008 | IDF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 36.1257 | ok
1194 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111707.PNT | 1JAI:AI111707.PNT | 10HNC11CT009 | IDF A DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 45.9727 | ok
1195 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI112107.PNT | 1JAI:AI112107.PNT | 10HNC11CT010 | IDF A DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 47.5186 | ok
1196 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111604.PNT | 1JAI:AI111604.PNT | 10HNC11CT011 | IDF A MIDDLE BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 54.2868 | ok
1197 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111605.PNT | 1JAI:AI111605.PNT | 10HNC11CT012 | IDF A MIDDLE BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 52.7019 | ok
1198 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111606.PNT | 1JAI:AI111606.PNT | 10HNC11CT013 | IDF A NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 49.2853 | ok
1199 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111607.PNT | 1JAI:AI111607.PNT | 10HNC11CT014 | IDF A NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 49.1294 | ok
1200 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111207.PNT | 1JAI:AI111207.PNT | 10HNC11CY001X | IDF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.641 | ok
1201 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111303.PNT | 1JAI:AI111303.PNT | 10HNC11CY001Y | IDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.1598 | ok
1202 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111208.PNT | 1JAI:AI111208.PNT | 10HNC11CY002X | IDF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.21613 | ok
1203 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 10 | IDF #1A | 50-F296S-J0201-37 | OPC.AW1002.1JAI.AI111304.PNT | 1JAI:AI111304.PNT | 10HNC11CY002Y | IDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.0423 | ok
1204 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140401.PNT | 1LAI:AI140401.PNT | 10HNA21CP201 | ESP B OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa | [6 empty] | 0 | ok
1205 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141605.PNT | 1LAI:AI141605.PNT | 10HNA21CT001 | ESP B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 147.4695 | ok
1206 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI140402.PNT | 1LAI:AI140402.PNT | 10HNA22CP201 | IDF B OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa | [6 empty] | 411.5977 | ok
1207 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI141606.PNT | 1LAI:AI141606.PNT | 10HNA22CT001 | IDFB OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 152.3778 | ok
1208 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1E_IDF.AO053101.OUT | 1E_IDF:AO053101.OUT | 10HNC21AA101XB11 | IDF B INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 49.0917 | ok
1209 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-02 | OPC.AW1002.1EAI.AI052302.PNT | 1EAI:AI052302.PNT | 10HNC21AA101XB12 | IDF B INLET STATIONARY BLADE POSITION | AI | 0 | 100 | % | [6 empty] | 49.7617 | ok
1210 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131103.PNT | 1KAI:AI131103.PNT | 10HNC21AN001XB13 | IDF B CURRENT | AI | 0 | 400 | A | [6 empty] | 129.2188 | ok
1211 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131305.PNT | 1KAI:AI131305.PNT | 10HNC21AN002XB13 | IDF B #1 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | -0.12266 | no
1212 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131306.PNT | 1KAI:AI131306.PNT | 10HNC21AN003XB13 | IDF B #2 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | 14.8867 | ok
1213 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131703.PNT | 1KAI:AI131703.PNT | 10HNC21CT001 | IDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.5445 | ok
1214 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI132103.PNT | 1KAI:AI132103.PNT | 10HNC21CT002 | IDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 46.7131 | ok
1215 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131704.PNT | 1KAI:AI131704.PNT | 10HNC21CT003 | IDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 46.6092 | ok
1216 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI132104.PNT | 1KAI:AI132104.PNT | 10HNC21CT004 | IDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.0509 | ok
1217 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131705.PNT | 1KAI:AI131705.PNT | 10HNC21CT005 | IDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 46.7651 | ok
1218 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI132105.PNT | 1KAI:AI132105.PNT | 10HNC21CT006 | IDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 46.6352 | ok
1219 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131706.PNT | 1KAI:AI131706.PNT | 10HNC21CT007 | IDF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 38.7628 | ok
1220 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI132106.PNT | 1KAI:AI132106.PNT | 10HNC21CT008 | IDF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 35.4631 | ok
1221 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131707.PNT | 1KAI:AI131707.PNT | 10HNC21CT009 | IDF B DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 51.0391 | ok
1222 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI132107.PNT | 1KAI:AI132107.PNT | 10HNC21CT010 | IDF B DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 52.1303 | ok
1223 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131604.PNT | 1KAI:AI131604.PNT | 10HNC21CT011 | IDF B MIDDLE BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 50.3116 | ok
1224 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131605.PNT | 1KAI:AI131605.PNT | 10HNC21CT012 | IDF B MIDDLE BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 48.6877 | ok
1225 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131606.PNT | 1KAI:AI131606.PNT | 10HNC21CT013 | IDF B NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 46.3884 | ok
1226 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131607.PNT | 1KAI:AI131607.PNT | 10HNC21CT014 | IDF B NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 48.5319 | ok
1227 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131207.PNT | 1KAI:AI131207.PNT | 10HNC21CY001X | IDF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.23242 | ok
1228 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131303.PNT | 1KAI:AI131303.PNT | 10HNC21CY001Y | IDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.613 | ok
1229 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131208.PNT | 1KAI:AI131208.PNT | 10HNC21CY002X | IDF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.0045 | ok
1230 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 12 | IDF #1B | 50-F296S-J0201-37 | OPC.AW1002.1KAI.AI131304.PNT | 1KAI:AI131304.PNT | 10HNC21CY002Y | IDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.61699 | ok
1231 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142701.PNT | 1LAI:AI142701.PNT | 10HNEAI001 | DUST CONCENTRATION | AI | 10 | 1000 | mg/m3 | [6 empty] | 0 | no
1232 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142702.PNT | 1LAI:AI142702.PNT | 10HNEAI002 | SO2 CONCENTRATION | AI | 0 | 1000 | mg/m3 | [6 empty] | 0 | ok
1233 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142703.PNT | 1LAI:AI142703.PNT | 10HNEAI003 | NOX CONCENTRATION | AI | 0 | 1000 | mg/m3 | [6 empty] | 0 | ok
1234 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142704.PNT | 1LAI:AI142704.PNT | 10HNEAI004 | O2 CONCENTRATION | AI | 0 | 25 | % | [6 empty] | 0 | ok
1235 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142705.PNT | 1LAI:AI142705.PNT | 10HNEAI005 | FLUE GAS FLOW | AI | 0 | 45 | m/s | [6 empty] | 0 | ok
1236 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142601.PNT | 1LAI:AI142601.PNT | 10HNEAI006 | FLUE GAS TEMPERATURE | RTD | 0 | 200 | ℃ | [6 empty] | 0 | ok
1237 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142706.PNT | 1LAI:AI142706.PNT | 10HNEAI007 | FLUE GAS PRESSURE | AI | -5 | 5 | kPa | [6 empty] | 0 | ok
1238 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142707.PNT | 1LAI:AI142707.PNT | 10HNEAI008 | FLUE GAS HUMIDITY | AI | 0 | 100 | % | [6 empty] | 0 | ok
1239 | 1 | UJPCT #1 | 7 | AIR & FLUE GAS SYSTEM #1 | 13 | CEMS #1 | 50-F296S-J0201-02 | OPC.AW1002.1LAI.AI142708.PNT | 1LAI:AI142708.PNT | 10HNEAI009 | CO CONCENTRATION | AI | 0 | 500 | mg/m3 | [8 empty] | TIDAK DIPAKAI
1240 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-19 | OPC.AW1002.1QAI.AI213404.PNT | 1QAI:AI213404.PNT | 10MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.019043 | ok
1241 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1PAI.AI203602.PNT | 1PAI:AI203602.PNT | 10MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 1000 | mm |  |  | 300 | 600 |  |  | 596.1797 | ok
1242 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1RAI.AI231204.PNT | 1RAI:AI231204.PNT | 10MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 2 | MPa | [6 empty] | 0.35266 | ok
1243 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230305.PNT | 1RAI:AI230305.PNT | 10MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C | [6 empty] | 63.5102 | ok
1244 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230405.PNT | 1RAI:AI230405.PNT | 10MKW10CT003 | GENERATOR H2 SIDE RETURN OIL TEMP(EXCITER SIDE) | RTD | 0 | 100 | C | [6 empty] | 60.5223 | ok
1245 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1PAI.AI202205.PNT | 1PAI:AI202205.PNT | 10MKW20AP101XB13 | GENERATOR H2 SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 15 | A |  |  |  | 8.8 |  |  | -0.036035 | no
1246 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 1 | GENERATOR SEAL OIL - H2 SIDE #1A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230307.PNT | 1RAI:AI230307.PNT | 10MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 30.1239 | ok
1247 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1PAI.AI202801.PNT | 1PAI:AI202801.PNT | 10MKW20AP102XB13 | GENERATOR H2 SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 15 | A |  |  |  | 8.8 |  |  | 5.966 | ok
1248 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 3 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW1002.1PAI.AI202107.PNT | 1PAI:AI202107.PNT | 10MKW10AP101XB13 | GENERATOR AIR SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 25 | A |  |  |  | 15.4 |  |  | -0.011719 | no
1249 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 3 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230404.PNT | 1RAI:AI230404.PNT | 10MKW10CT001 | GENERATOR AIR SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 48.8047 | ok
1250 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 3 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230306.PNT | 1RAI:AI230306.PNT | 10MKW10CT004 | GENERATOR TURBINE SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 60.3924 | ok
1251 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 3 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW1002.1RAI.AI230406.PNT | 1RAI:AI230406.PNT | 10MKW10CT005 | GENERATOR EXCITER SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 57.1187 | ok
1252 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 4 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW1002.1PAI.AI202203.PNT | 1PAI:AI202203.PNT | 10MKW10AP102XB13 | GENERATOR AIR SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 25 | A |  |  |  | 15.4 |  |  | 10.0215 | ok
1253 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 5 | GENERATOR SEAL OIL #1 - AIR SIDE DC EMERGENCY PUMP | F296S-J0201-25 | OPC.AW1002.1PAI.AI202204.PNT | 1PAI:AI202204.PNT | 10MKW10AP103XB13 | GENERATOR AIR SIDE DC EMERGENCY SEAL OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 41.1 |  |  | -0.083008 | no
1254 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1M_GESTAT.AO162608.OUT | 1M_GESTAT:AO162608.OUT | 10MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 12.2438 | ok
1255 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1MAI.AI162304.PNT | 1MAI:AI162304.PNT | 10MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 11.0605 | ok
1256 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1PAI.AI202201.PNT | 1PAI:AI202201.PNT | 10MKF10AP001XB13 | GENERATOR STATOR COOLING WATER PUMP A CURRENT | AI | 0 | 75 | A |  |  |  | 42.2 |  |  | -0.13037 | no
1257 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1R_FLOW.GENAIN.PNT | 1R_FLOW:GENAIN.PNT | 10MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 50 | t/h |  |  | 5 | 45 |  |  | 44.0852 | ok
1258 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1RAI.AI231501.PNT | 1RAI:AI231501.PNT | 10MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2 |  |  | 0.19023 | ok
1259 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1RAI.AI231402.PNT | 1RAI:AI231402.PNT | 10MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5 |  |  | 0.3668 | ok
1260 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1MAI.AI160101.PNT | 1MAI:AI160101.PNT | 10MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | C |  |  |  | 48 |  |  | 45.6349 | ok
1262 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1RAI.AI231103.PNT | 1RAI:AI231103.PNT | 10MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.22724 | ok
1263 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1RAI.AI231203.PNT | 1RAI:AI231203.PNT | 10MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.051431 | ok
1264 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-24 | OPC.AW1002.1RAI.AI230304.PNT | 1RAI:AI230304.PNT | 10MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | C |  |  |  | 80 |  |  | 47.1938 | ok
1265 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 6 | GENERATOR STATOR COOLING #1A | F296S-J0201-14 | OPC.AW1002.1RAI.AI230206.PNT | 1RAI:AI230206.PNT | 10PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 41.5688 | ok
1266 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1PAI.AI202202.PNT | 1PAI:AI202202.PNT | 10MKF10AP002XB13 | GENERATOR STATOR COOLING WATER PUMP B CURRENT | AI | 0 | 75 | A |  |  |  | 42.2 |  |  | 36.3794 | ok
1267 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_6 | 1ATC:1BD117AIN.PNT_6 | 10MKA00CT0143 | GENERATOR TURBINE SIDE BABBIT TEMP | RTD | 0 | 120 | C | [6 empty] | 79.7097 | ok
1268 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_5 | 1ATC:1BD115AIN.PNT_5 | 10MKA00CT0144 | GENERATOR TURBINE SIDE BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 61.8344 | ok
1269 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_7 | 1ATC:1BD104AIN.PNT_7 | 10TSIDEH16 | SHAFT NO.5 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 43.7891 | ok
1270 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_8 | 1ATC:1BD104AIN.PNT_8 | 10TSIDEH17 | SHAFT NO.5 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 31.3281 | ok
1271 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 8 | BEARING GENERATOR NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_7 | 1ATC:1BD105AIN.PNT_7 | 10TSIDEH24 | BEARING COVER NO.5 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 29.0015 | ok
1272 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_7 | 1ATC:1BD117AIN.PNT_7 | 10MKA00CT0146 | GENERATOR COLECTOR SIDE BABBIT TEMP | RTD | 0 | 120 | C | [6 empty] | 80.7749 | ok
1273 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_6 | 1ATC:1BD115AIN.PNT_6 | 10MKA00CT0147 | GENERATOR COLECTOR SIDE BEARING RETURN OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 59.522 | ok
1274 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_1 | 1ATC:1BD105AIN.PNT_1 | 10TSIDEH18 | SHAFT NO.6 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 21.2422 | ok
1275 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_2 | 1ATC:1BD105AIN.PNT_2 | 10TSIDEH19 | SHAFT NO.6 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 30.7812 | ok
1276 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 9 | BEARING GENERATOR NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_8 | 1ATC:1BD105AIN.PNT_8 | 10TSIDEH25 | BEARING COVER NO.6 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 26.4331 | ok
1277 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224601.PNT | 1QAI:AI224601.PNT | 10MKA00CT001 | GENERATOR STATOR COIL OUTLET WATER TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.3739 | ok
1278 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224602.PNT | 1QAI:AI224602.PNT | 10MKA00CT002 | GENERATOR STATOR COIL OUTLET WATER TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.7637 | ok
1279 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224603.PNT | 1QAI:AI224603.PNT | 10MKA00CT003 | GENERATOR STATOR COIL OUTLET WATER TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.9585 | ok
1280 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224604.PNT | 1QAI:AI224604.PNT | 10MKA00CT004 | GENERATOR STATOR COIL OUTLET WATER TEMP 4 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.7637 | ok
1281 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224605.PNT | 1QAI:AI224605.PNT | 10MKA00CT005 | GENERATOR STATOR COIL OUTLET WATER TEMP 5 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.8933 | ok
1282 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224606.PNT | 1QAI:AI224606.PNT | 10MKA00CT006 | GENERATOR STATOR COIL OUTLET WATER TEMP 6 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1147 | ok
1283 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224607.PNT | 1QAI:AI224607.PNT | 10MKA00CT007 | GENERATOR STATOR COIL OUTLET WATER TEMP 7 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.5558 | ok
1284 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224608.PNT | 1QAI:AI224608.PNT | 10MKA00CT008 | GENERATOR STATOR COIL OUTLET WATER TEMP 8 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.2573 | ok
1285 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224701.PNT | 1QAI:AI224701.PNT | 10MKA00CT009 | GENERATOR STATOR COIL OUTLET WATER TEMP 9 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.9069 | ok
1286 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224702.PNT | 1QAI:AI224702.PNT | 10MKA00CT010 | GENERATOR STATOR COIL OUTLET WATER TEMP 10 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.4646 | ok
1287 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224703.PNT | 1QAI:AI224703.PNT | 10MKA00CT011 | GENERATOR STATOR COIL OUTLET WATER TEMP 11 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.5298 | ok
1288 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224704.PNT | 1QAI:AI224704.PNT | 10MKA00CT012 | GENERATOR STATOR COIL OUTLET WATER TEMP 12 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.0619 | ok
1289 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224705.PNT | 1QAI:AI224705.PNT | 10MKA00CT013 | GENERATOR STATOR COIL OUTLET WATER TEMP 13 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.2567 | ok
1290 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224706.PNT | 1QAI:AI224706.PNT | 10MKA00CT014 | GENERATOR STATOR COIL OUTLET WATER TEMP 14 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 38.3861 | ok
1291 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224707.PNT | 1QAI:AI224707.PNT | 10MKA00CT015 | GENERATOR STATOR COIL OUTLET WATER TEMP 15 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 38.9187 | ok
1292 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224708.PNT | 1QAI:AI224708.PNT | 10MKA00CT016 | GENERATOR STATOR COIL OUTLET WATER TEMP 16 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.0489 | ok
1293 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225101.PNT | 1QAI:AI225101.PNT | 10MKA00CT017 | GENERATOR STATOR COIL OUTLET WATER TEMP 17 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.0096 | ok
1294 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225102.PNT | 1QAI:AI225102.PNT | 10MKA00CT018 | GENERATOR STATOR COIL OUTLET WATER TEMP 18 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.2051 | ok
1295 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225103.PNT | 1QAI:AI225103.PNT | 10MKA00CT019 | GENERATOR STATOR COIL OUTLET WATER TEMP 19 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 37.4637 | ok
1296 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225104.PNT | 1QAI:AI225104.PNT | 10MKA00CT020 | GENERATOR STATOR COIL OUTLET WATER TEMP 20 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.1531 | ok
1297 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225105.PNT | 1QAI:AI225105.PNT | 10MKA00CT021 | GENERATOR STATOR COIL OUTLET WATER TEMP 21 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.0226 | ok
1298 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225106.PNT | 1QAI:AI225106.PNT | 10MKA00CT022 | GENERATOR STATOR COIL OUTLET WATER TEMP 22 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 38.7498 | ok
1299 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225107.PNT | 1QAI:AI225107.PNT | 10MKA00CT023 | GENERATOR STATOR COIL OUTLET WATER TEMP 23 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.3087 | ok
1300 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225108.PNT | 1QAI:AI225108.PNT | 10MKA00CT024 | GENERATOR STATOR COIL OUTLET WATER TEMP 24 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.6332 | ok
1301 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225201.PNT | 1QAI:AI225201.PNT | 10MKA00CT025 | GENERATOR STATOR COIL OUTLET WATER TEMP 25 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.9455 | ok
1302 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225202.PNT | 1QAI:AI225202.PNT | 10MKA00CT026 | GENERATOR STATOR COIL OUTLET WATER TEMP 26 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.335 | ok
1303 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225203.PNT | 1QAI:AI225203.PNT | 10MKA00CT027 | GENERATOR STATOR COIL OUTLET WATER TEMP 27 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.867 | ok
1304 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225204.PNT | 1QAI:AI225204.PNT | 10MKA00CT028 | GENERATOR STATOR COIL OUTLET WATER TEMP 28 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.9323 | ok
1305 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225205.PNT | 1QAI:AI225205.PNT | 10MKA00CT029 | GENERATOR STATOR COIL OUTLET WATER TEMP 29 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.5295 | ok
1306 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225206.PNT | 1QAI:AI225206.PNT | 10MKA00CT030 | GENERATOR STATOR COIL OUTLET WATER TEMP 30 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.6854 | ok
1307 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225207.PNT | 1QAI:AI225207.PNT | 10MKA00CT031 | GENERATOR STATOR COIL OUTLET WATER TEMP 31 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.9452 | ok
1308 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225208.PNT | 1QAI:AI225208.PNT | 10MKA00CT032 | GENERATOR STATOR COIL OUTLET WATER TEMP 32 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.9323 | ok
1309 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225301.PNT | 1QAI:AI225301.PNT | 10MKA00CT033 | GENERATOR STATOR COIL OUTLET WATER TEMP 33 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.4773 | ok
1310 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225302.PNT | 1QAI:AI225302.PNT | 10MKA00CT034 | GENERATOR STATOR COIL OUTLET WATER TEMP 34 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.2963 | ok
1311 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225303.PNT | 1QAI:AI225303.PNT | 10MKA00CT035 | GENERATOR STATOR COIL OUTLET WATER TEMP 35 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.322 | ok
1312 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225304.PNT | 1QAI:AI225304.PNT | 10MKA00CT036 | GENERATOR STATOR COIL OUTLET WATER TEMP 36 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.4259 | ok
1313 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225305.PNT | 1QAI:AI225305.PNT | 10MKA00CT037 | GENERATOR STATOR COIL OUTLET WATER TEMP 37 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.2443 | ok
1314 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225306.PNT | 1QAI:AI225306.PNT | 10MKA00CT038 | GENERATOR STATOR COIL OUTLET WATER TEMP 38 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.1528 | ok
1315 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225307.PNT | 1QAI:AI225307.PNT | 10MKA00CT039 | GENERATOR STATOR COIL OUTLET WATER TEMP 39 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.1534 | ok
1316 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225308.PNT | 1QAI:AI225308.PNT | 10MKA00CT040 | GENERATOR STATOR COIL OUTLET WATER TEMP 40 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.4389 | ok
1317 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225401.PNT | 1QAI:AI225401.PNT | 10MKA00CT041 | GENERATOR STATOR COIL OUTLET WATER TEMP 41 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.6854 | ok
1318 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225402.PNT | 1QAI:AI225402.PNT | 10MKA00CT042 | GENERATOR STATOR COIL OUTLET WATER TEMP 42 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 39.2694 | ok
1319 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225403.PNT | 1QAI:AI225403.PNT | 10MKA00CT043 | GENERATOR STATOR COIL OUTLET WATER TEMP 43 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.5818 | ok
1320 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225404.PNT | 1QAI:AI225404.PNT | 10MKA00CT044 | GENERATOR STATOR COIL OUTLET WATER TEMP 44 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.2957 | ok
1321 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225405.PNT | 1QAI:AI225405.PNT | 10MKA00CT045 | GENERATOR STATOR COIL OUTLET WATER TEMP 45 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 47.7524 | ok
1322 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225406.PNT | 1QAI:AI225406.PNT | 10MKA00CT046 | GENERATOR STATOR COIL OUTLET WATER TEMP 46 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.9066 | ok
1323 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225407.PNT | 1QAI:AI225407.PNT | 10MKA00CT047 | GENERATOR STATOR COIL OUTLET WATER TEMP 47 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.8026 | ok
1324 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225408.PNT | 1QAI:AI225408.PNT | 10MKA00CT048 | GENERATOR STATOR COIL OUTLET WATER TEMP 48 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 40.9842 | ok
1325 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225501.PNT | 1QAI:AI225501.PNT | 10MKA00CT049 | GENERATOR STATOR COIL OUTLET WATER TEMP 49 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.5558 | ok
1326 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225502.PNT | 1QAI:AI225502.PNT | 10MKA00CT050 | GENERATOR STATOR COIL OUTLET WATER TEMP 50 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.9715 | ok
1327 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225503.PNT | 1QAI:AI225503.PNT | 10MKA00CT051 | GENERATOR STATOR COIL OUTLET WATER TEMP 51 | RTD | 0 | 100 | C | [6 empty] | 42.5431 | ok
1328 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225504.PNT | 1QAI:AI225504.PNT | 10MKA00CT052 | GENERATOR STATOR COIL OUTLET WATER TEMP 52 | RTD | 0 | 100 | C | [6 empty] | 40.9972 | ok
1329 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225505.PNT | 1QAI:AI225505.PNT | 10MKA00CT053 | GENERATOR STATOR COIL OUTLET WATER TEMP 53 | RTD | 0 | 100 | C | [6 empty] | 42.3093 | ok
1330 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225506.PNT | 1QAI:AI225506.PNT | 10MKA00CT054 | GENERATOR STATOR COIL OUTLET WATER TEMP 54 | RTD | 0 | 100 | C | [6 empty] | 41.6337 | ok
1331 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225601.PNT | 1QAI:AI225601.PNT | 10MKA00CT055 | GENERATOR STATOR BARS TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.3358 | ok
1332 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225602.PNT | 1QAI:AI225602.PNT | 10MKA00CT056 | GENERATOR STATOR BARS TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.3875 | ok
1333 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225603.PNT | 1QAI:AI225603.PNT | 10MKA00CT057 | GENERATOR STATOR BARS TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9201 | ok
1334 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225604.PNT | 1QAI:AI225604.PNT | 10MKA00CT058 | GENERATOR STATOR BARS TEMP 4 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4787 | ok
1335 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225605.PNT | 1QAI:AI225605.PNT | 10MKA00CT059 | GENERATOR STATOR BARS TEMP 5 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6083 | ok
1336 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225606.PNT | 1QAI:AI225606.PNT | 10MKA00CT060 | GENERATOR STATOR BARS TEMP 6 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8812 | ok
1337 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225607.PNT | 1QAI:AI225607.PNT | 10MKA00CT061 | GENERATOR STATOR BARS TEMP 7 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7383 | ok
1338 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225608.PNT | 1QAI:AI225608.PNT | 10MKA00CT062 | GENERATOR STATOR BARS TEMP 8 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.1799 | ok
1339 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225701.PNT | 1QAI:AI225701.PNT | 10MKA00CT063 | GENERATOR STATOR BARS TEMP 9 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1667 | ok
1340 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225702.PNT | 1QAI:AI225702.PNT | 10MKA00CT064 | GENERATOR STATOR BARS TEMP 10 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.3615 | ok
1341 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225703.PNT | 1QAI:AI225703.PNT | 10MKA00CT065 | GENERATOR STATOR BARS TEMP 11 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8422 | ok
1342 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225704.PNT | 1QAI:AI225704.PNT | 10MKA00CT066 | GENERATOR STATOR BARS TEMP 12 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5564 | ok
1343 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225705.PNT | 1QAI:AI225705.PNT | 10MKA00CT067 | GENERATOR STATOR BARS TEMP 13 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 15.8471 | ok
1344 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225706.PNT | 1QAI:AI225706.PNT | 10MKA00CT068 | GENERATOR STATOR BARS TEMP 14 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.9588 | ok
1345 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225707.PNT | 1QAI:AI225707.PNT | 10MKA00CT069 | GENERATOR STATOR BARS TEMP 15 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5694 | ok
1346 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI225708.PNT | 1QAI:AI225708.PNT | 10MKA00CT070 | GENERATOR STATOR BARS TEMP 16 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.3875 | ok
1347 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226101.PNT | 1QAI:AI226101.PNT | 10MKA00CT071 | GENERATOR STATOR BARS TEMP 17 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6343 | ok
1348 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226102.PNT | 1QAI:AI226102.PNT | 10MKA00CT072 | GENERATOR STATOR BARS TEMP 18 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7642 | ok
1349 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226103.PNT | 1QAI:AI226103.PNT | 10MKA00CT073 | GENERATOR STATOR BARS TEMP 19 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8552 | ok
1350 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226104.PNT | 1QAI:AI226104.PNT | 10MKA00CT074 | GENERATOR STATOR BARS TEMP 20 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.2839 | ok
1351 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226105.PNT | 1QAI:AI226105.PNT | 10MKA00CT075 | GENERATOR STATOR BARS TEMP 21 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.3878 | ok
1352 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226106.PNT | 1QAI:AI226106.PNT | 10MKA00CT076 | GENERATOR STATOR BARS TEMP 22 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6343 | ok
1353 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226107.PNT | 1QAI:AI226107.PNT | 10MKA00CT077 | GENERATOR STATOR BARS TEMP 23 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8422 | ok
1354 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226108.PNT | 1QAI:AI226108.PNT | 10MKA00CT078 | GENERATOR STATOR BARS TEMP 24 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8812 | ok
1355 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226201.PNT | 1QAI:AI226201.PNT | 10MKA00CT079 | GENERATOR STATOR BARS TEMP 25 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.3488 | ok
1356 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226202.PNT | 1QAI:AI226202.PNT | 10MKA00CT080 | GENERATOR STATOR BARS TEMP 26 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.128 | ok
1357 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226203.PNT | 1QAI:AI226203.PNT | 10MKA00CT081 | GENERATOR STATOR BARS TEMP 27 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8422 | ok
1358 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226204.PNT | 1QAI:AI226204.PNT | 10MKA00CT082 | GENERATOR STATOR BARS TEMP 28 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4917 | ok
1359 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226205.PNT | 1QAI:AI226205.PNT | 10MKA00CT083 | GENERATOR STATOR BARS TEMP 29 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9071 | ok
1360 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226206.PNT | 1QAI:AI226206.PNT | 10MKA00CT084 | GENERATOR STATOR BARS TEMP 30 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.6219 | ok
1361 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226207.PNT | 1QAI:AI226207.PNT | 10MKA00CT085 | GENERATOR STATOR BARS TEMP 31 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9461 | ok
1362 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226208.PNT | 1QAI:AI226208.PNT | 10MKA00CT086 | GENERATOR STATOR BARS TEMP 32 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.4135 | ok
1363 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226301.PNT | 1QAI:AI226301.PNT | 10MKA00CT087 | GENERATOR STATOR BARS TEMP 33 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8162 | ok
1364 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226302.PNT | 1QAI:AI226302.PNT | 10MKA00CT088 | GENERATOR STATOR BARS TEMP 34 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.5177 | ok
1365 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226303.PNT | 1QAI:AI226303.PNT | 10MKA00CT089 | GENERATOR STATOR BARS TEMP 35 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9721 | ok
1366 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226304.PNT | 1QAI:AI226304.PNT | 10MKA00CT090 | GENERATOR STATOR BARS TEMP 36 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4398 | ok
1367 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226305.PNT | 1QAI:AI226305.PNT | 10MKA00CT091 | GENERATOR STATOR BARS TEMP 37 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6733 | ok
1368 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226306.PNT | 1QAI:AI226306.PNT | 10MKA00CT092 | GENERATOR STATOR BARS TEMP 38 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7512 | ok
1369 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226307.PNT | 1QAI:AI226307.PNT | 10MKA00CT093 | GENERATOR STATOR BARS TEMP 39 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1407 | ok
1370 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226308.PNT | 1QAI:AI226308.PNT | 10MKA00CT094 | GENERATOR STATOR BARS TEMP 40 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6083 | ok
1371 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226401.PNT | 1QAI:AI226401.PNT | 10MKA00CT095 | GENERATOR STATOR BARS TEMP 41 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5174 | ok
1372 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226402.PNT | 1QAI:AI226402.PNT | 10MKA00CT096 | GENERATOR STATOR BARS TEMP 42 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5564 | ok
1373 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226403.PNT | 1QAI:AI226403.PNT | 10MKA00CT097 | GENERATOR STATOR BARS TEMP 43 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4917 | ok
1374 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226404.PNT | 1QAI:AI226404.PNT | 10MKA00CT098 | GENERATOR STATOR BARS TEMP 44 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2842 | ok
1375 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226405.PNT | 1QAI:AI226405.PNT | 10MKA00CT099 | GENERATOR STATOR BARS TEMP 45 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.5437 | ok
1376 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226406.PNT | 1QAI:AI226406.PNT | 10MKA00CT100 | GENERATOR STATOR BARS TEMP 46 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.4005 | ok
1377 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226407.PNT | 1QAI:AI226407.PNT | 10MKA00CT101 | GENERATOR STATOR BARS TEMP 47 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.0111 | ok
1378 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226408.PNT | 1QAI:AI226408.PNT | 10MKA00CT102 | GENERATOR STATOR BARS TEMP 48 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.9074 | ok
1379 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226501.PNT | 1QAI:AI226501.PNT | 10MKA00CT103 | GENERATOR STATOR BARS TEMP 49 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8162 | ok
1380 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226502.PNT | 1QAI:AI226502.PNT | 10MKA00CT104 | GENERATOR STATOR BARS TEMP 50 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8422 | ok
1381 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226503.PNT | 1QAI:AI226503.PNT | 10MKA00CT105 | GENERATOR STATOR BARS TEMP 51 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.3225 | ok
1382 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226504.PNT | 1QAI:AI226504.PNT | 10MKA00CT106 | GENERATOR STATOR BARS TEMP 52 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9461 | ok
1383 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226505.PNT | 1QAI:AI226505.PNT | 10MKA00CT107 | GENERATOR STATOR BARS TEMP 53 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5044 | ok
1384 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226506.PNT | 1QAI:AI226506.PNT | 10MKA00CT108 | GENERATOR STATOR BARS TEMP 54 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.141 | ok
1385 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226601.PNT | 1QAI:AI226601.PNT | 10MKA00CT109 | GENERATOR STATOR CORE TEMP 1 | RTD | 0 | 100 | C | [6 empty] | 38.9057 | ok
1386 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226602.PNT | 1QAI:AI226602.PNT | 10MKA00CT110 | GENERATOR STATOR CORE TEMP 2 | RTD | 0 | 100 | C | [6 empty] | 39.945 | ok
1387 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226603.PNT | 1QAI:AI226603.PNT | 10MKA00CT111 | GENERATOR STATOR CORE TEMP 3 | RTD | 0 | 100 | C | [6 empty] | 39.6851 | ok
1388 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226604.PNT | 1QAI:AI226604.PNT | 10MKA00CT112 | GENERATOR STATOR CORE TEMP 4 | RTD | 0 | 100 | C | [6 empty] | 42.2443 | ok
1389 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226605.PNT | 1QAI:AI226605.PNT | 10MKA00CT113 | GENERATOR STATOR CORE TEMP 5 | RTD | 0 | 100 | C | [6 empty] | 52.3511 | ok
1390 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226606.PNT | 1QAI:AI226606.PNT | 10MKA00CT114 | GENERATOR STATOR CORE TEMP 6 | RTD | 0 | 100 | C | [6 empty] | 55.9366 | ok
1391 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226607.PNT | 1QAI:AI226607.PNT | 10MKA00CT115 | GENERATOR STATOR CORE TEMP 7 | RTD | 0 | 100 | C | [6 empty] | 54.0529 | ok
1392 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226608.PNT | 1QAI:AI226608.PNT | 10MKA00CT116 | GENERATOR STATOR CORE TEMP 8 | RTD | 0 | 100 | C | [6 empty] | 57.0668 | ok
1393 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226701.PNT | 1QAI:AI226701.PNT | 10MKA00CT117 | GENERATOR STATOR CORE TEMP 9 | RTD | 0 | 100 | C | [6 empty] | 54.0919 | ok
1394 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226702.PNT | 1QAI:AI226702.PNT | 10MKA00CT118 | GENERATOR STATOR CORE TEMP 10 | RTD | 0 | 100 | C | [6 empty] | 57.2097 | ok
1395 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226703.PNT | 1QAI:AI226703.PNT | 10MKA00CT119 | GENERATOR STATOR CORE TEMP 11 | RTD | 0 | 100 | C | [6 empty] | 57.6644 | ok
1396 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226704.PNT | 1QAI:AI226704.PNT | 10MKA00CT120 | GENERATOR STATOR CORE TEMP 12 | RTD | 0 | 100 | C | [6 empty] | 57.6124 | ok
1397 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226705.PNT | 1QAI:AI226705.PNT | 10MKA00CT121 | GENERATOR STATOR CORE TEMP 13 | RTD | 0 | 100 | C | [6 empty] | 37.4248 | ok
1398 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226706.PNT | 1QAI:AI226706.PNT | 10MKA00CT122 | GENERATOR STATOR CORE TEMP 14 | RTD | 0 | 100 | C | [6 empty] | 38.7498 | ok
1399 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226707.PNT | 1QAI:AI226707.PNT | 10MKA00CT123 | GENERATOR STATOR CORE TEMP 15 | RTD | 0 | 100 | C | [6 empty] | 37.2688 | ok
1400 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI226708.PNT | 1QAI:AI226708.PNT | 10MKA00CT124 | GENERATOR STATOR CORE TEMP 16 | RTD | 0 | 100 | C | [6 empty] | 38.8667 | ok
1401 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227101.PNT | 1QAI:AI227101.PNT | 10MKA00CT125 | GENERATOR STATOR CORE TEMP 17 | RTD | 0 | 100 | C | [6 empty] | 38.6459 | ok
1402 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227102.PNT | 1QAI:AI227102.PNT | 10MKA00CT126 | GENERATOR STATOR CORE TEMP 18 | RTD | 0 | 100 | C | [6 empty] | 39.4643 | ok
1403 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227105.PNT | 1QAI:AI227105.PNT | 10MKA00CT127 | GENERATOR COLD/HOT H2 TEMP 1 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 29.9551 | ok
1404 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227106.PNT | 1QAI:AI227106.PNT | 10MKA00CT128 | GENERATOR COLD/HOT H2 TEMP 2 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 30.3578 | ok
1405 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227107.PNT | 1QAI:AI227107.PNT | 10MKA00CT129 | GENERATOR COLD/HOT H2 TEMP 3 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 37.8534 | ok
1406 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227201.PNT | 1QAI:AI227201.PNT | 10MKA00CT130 | GENERATOR COLD/HOT H2 TEMP 4 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 31.8127 | ok
1407 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227202.PNT | 1QAI:AI227202.PNT | 10MKA00CT131 | GENERATOR COLD/HOT H2 TEMP 5 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 42.2443 | ok
1408 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227203.PNT | 1QAI:AI227203.PNT | 10MKA00CT132 | GENERATOR COLD/HOT H2 TEMP 6 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 33.3976 | ok
1409 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227204.PNT | 1QAI:AI227204.PNT | 10MKA00CT133 | GENERATOR COLD/HOT H2 TEMP 7 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 42.8419 | ok
1410 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227205.PNT | 1QAI:AI227205.PNT | 10MKA00CT134 | GENERATOR COLD/HOT H2 TEMP 8 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 32.6182 | ok
1411 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227206.PNT | 1QAI:AI227206.PNT | 10MKA00CT135 | GENERATOR COLD/HOT H2 TEMP 9 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 41.0232 | ok
1412 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227301.PNT | 1QAI:AI227301.PNT | 10MKA00CT136 | GENERATOR COLD/HOT H2 TEMP 10 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 32.5402 | ok
1413 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227302.PNT | 1QAI:AI227302.PNT | 10MKA00CT137 | GENERATOR COLD/HOT H2 TEMP 11 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 42.764 | ok
1414 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227303.PNT | 1QAI:AI227303.PNT | 10MKA00CT138 | GENERATOR COLD/HOT H2 TEMP 12 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 41.1141 | ok
1415 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227304.PNT | 1QAI:AI227304.PNT | 10MKA00CT139 | GENERATOR COLD/HOT H2 TEMP 13 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 30.2538 | ok
1416 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227305.PNT | 1QAI:AI227305.PNT | 10MKA00CT140 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.3353 | ok
1417 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227306.PNT | 1QAI:AI227306.PNT | 10MKA00CT141 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.8676 | ok
1418 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227307.PNT | 1QAI:AI227307.PNT | 10MKA00CT142 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.8936 | ok
1419 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224304.PNT | 1QAI:AI224304.PNT | 10MKA00CT160 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 100 | C | [6 empty] | 33.9173 | ok
1420 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224305.PNT | 1QAI:AI224305.PNT | 10MKA00CT161 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 100 | C | [6 empty] | 36.9697 | ok
1421 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224306.PNT | 1QAI:AI224306.PNT | 10MKA00CT162 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 100 | C | [6 empty] | 37.6352 | ok
1422 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224307.PNT | 1QAI:AI224307.PNT | 10MKA00CT163 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 4 | TC | 0 | 100 | C | [6 empty] | 34.1991 | ok
1423 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224308.PNT | 1QAI:AI224308.PNT | 10MKA00CT164 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 5 | TC | 0 | 100 | C | [6 empty] | 37.9075 | ok
1424 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224401.PNT | 1QAI:AI224401.PNT | 10MKA00CT165 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 6 | TC | 0 | 100 | C | [6 empty] | 36.1146 | ok
1425 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224402.PNT | 1QAI:AI224402.PNT | 10MKA00CT166 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 7 | TC | 0 | 600 | C | [6 empty] | 34.9873 | ok
1426 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224403.PNT | 1QAI:AI224403.PNT | 10MKA00CT167 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 8 | TC | 0 | 100 | C | [6 empty] | 34.361 | ok
1427 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224404.PNT | 1QAI:AI224404.PNT | 10MKA00CT168 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 9 | TC | 0 | 100 | C | [6 empty] | 36.9446 | ok
1428 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224405.PNT | 1QAI:AI224405.PNT | 10MKA00CT169 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 100 | C | [6 empty] | 32.3257 | ok
1429 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224406.PNT | 1QAI:AI224406.PNT | 10MKA00CT170 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 100 | C | [6 empty] | 37.0353 | ok
1430 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI224407.PNT | 1QAI:AI224407.PNT | 10MKA00CT171 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 100 | C | [6 empty] | 32.6075 | ok
1431 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1E_CSDMD.AO052608.OUT | 1E_CSDMD:AO052608.OUT | 10DCSDEHAO01 | CCS DEMAND 1 | AO | 0 | 100 | % | [6 empty] | 77.9776 | ok
1432 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1E_CSDMD.AO052707.OUT | 1E_CSDMD:AO052707.OUT | 10DCSDEHAO02 | CCS DEMAND 2 | AO | 0 | 100 | % | [6 empty] | 77.979 | ok
1433 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1EAI.AI052407.PNT | 1EAI:AI052407.PNT | 10DEHDCSAI02 | GENERATOR LOAD | AI | 0 | 519.6 | MW | [6 empty] | 197.7829 | ok
1434 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD106AIN.PNT_3 | 1VALVE:1AD106AIN.PNT_3 | 10DCSDEHAI01 | CCS DEMAND 1 | AI | 0 | 100 | % | [6 empty] | -93.6084 | no
1435 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD107AIN.PNT_3 | 1VALVE:1AD107AIN.PNT_3 | 10DCSDEHAI02 | CCS DEMAND 2 | AI | 0 | 100 | % | [6 empty] | 78.0332 | ok
1436 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD11206AOUT.OUT | 1VALVE:1AD11206AOUT.OUT | 10DEHDCSAO02 | GENERATOR LOAD | AO | 0 | 519.6 | MW | [6 empty] | 197.3125 | ok
1437 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD106AIN.PNT_1 | 1VALVE:1AD106AIN.PNT_1 | 10DQDEH01 | GENERATOR LOAD 1 | AI | 0 | 519.6 | MW | [6 empty] | 197.3203 | ok
1438 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD107AIN.PNT_1 | 1VALVE:1AD107AIN.PNT_1 | 10DQDEH02 | GENERATOR LOAD 2 | AI | 0 | 519.6 | MW | [6 empty] | 196.9453 | ok
1439 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 11 | GENERATOR #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD108AIN.PNT_1 | 1VALVE:1AD108AIN.PNT_1 | 10DQDEH03 | GENERATOR LOAD 3 | AI | 0 | 519.6 | MW | [6 empty] | 197.3359 | ok
1440 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242101.PNT | 1SAI:AI242101.PNT | 10MKA01-04 | GT HV SIDE CURRENT Ia | AI | 0 | 2500 | A | [6 empty] | 675.4883 | ok
1441 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242102.PNT | 1SAI:AI242102.PNT | 10MKA01-05 | GT HV SIDE CURRENT Ib | AI | 0 | 2500 | A | [6 empty] | 713.7695 | ok
1442 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242103.PNT | 1SAI:AI242103.PNT | 10MKA01-06 | GT HV SIDE CURRENT Ic | AI | 0 | 2500 | A | [6 empty] | 700.6348 | ok
1443 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242104.PNT | 1SAI:AI242104.PNT | 10MKA01-07 | GEN. CURRENT Ia | AI | 0 | 15000 | A | [6 empty] | 5487.0117 | ok
1444 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242105.PNT | 1SAI:AI242105.PNT | 10MKA01-08 | GEN. CURRENT Ib | AI | 0 | 15000 | A | [6 empty] | 5633.7891 | ok
1445 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242106.PNT | 1SAI:AI242106.PNT | 10MKA01-09 | GEN. CURRENT Ic | AI | 0 | 15000 | A | [6 empty] | 5804.8828 | ok
1446 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242107.PNT | 1SAI:AI242107.PNT | 10MKA01-10 | GEN. NEGATIVE-SEQUENCE CURRENT | AI | 0 | 15000 | A | [6 empty] | 164.6484 | ok
1447 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242201.PNT | 1SAI:AI242201.PNT | 10MKA01-11 | GEN. NEUTRAL POINT CURRENT | AI | 0 | 5 | A | [6 empty] | 0.059766 | ok
1448 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242202.PNT | 1SAI:AI242202.PNT | 10MKA01-12 | EXCITING TR. HV SIDE CURRENT Ia | AI | 0 | 300 | A | [6 empty] | 45.3047 | ok
1449 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242203.PNT | 1SAI:AI242203.PNT | 10MKA01-13 | EXCITING TR. HV SIDE CURRENT Ib | AI | 0 | 300 | A | [6 empty] | 44.3496 | ok
1450 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242204.PNT | 1SAI:AI242204.PNT | 10MKA01-14 | EXCITING TR. HV SIDE CURRENT Ic | AI | 0 | 300 | A | [6 empty] | 45.3457 | ok
1451 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242205.PNT | 1SAI:AI242205.PNT | 10MKA01-15 | GEN. A-C VOLTAGE | AI | 0 | 24 | kV | [6 empty] | 20.0437 | ok
1452 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242206.PNT | 1SAI:AI242206.PNT | 10MKA01-16 | GEN. OUTLET ZERO-SEQUENCE VOLTAGE | AI | 0 | 100 | V | [6 empty] | 4.9668 | ok
1453 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242301.PNT | 1SAI:AI242301.PNT | 10MKA01-17 | GT REACTIVE POWER | AI | -500 | 500 | MVAR | [6 empty] | -9.8242 | ok
1454 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242302.PNT | 1SAI:AI242302.PNT | 10MKA01-18 | GEN. REACTIVE POWER | AI | -400 | 400 | MVAR | [6 empty] | 10.7578 | ok
1455 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242303.PNT | 1SAI:AI242303.PNT | 10MKA01-19 | GT ACTIVE POWER | AI | 0 | 450 | MW | [6 empty] | 183.1113 | ok
1456 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242304.PNT | 1SAI:AI242304.PNT | 10MKA01-20 | GEN. ACTIVE POWER | AI | 0 | 450 | MW | [6 empty] | 197.6875 | ok
1457 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242305.PNT | 1SAI:AI242305.PNT | 10MKA01-21 | GEN. POWER FACTOR | AI | -1 | 1 | pF | [6 empty] | 12.035 | no
1458 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242306.PNT | 1SAI:AI242306.PNT | 10MKA01-22 | GEN. FREQUENCY | AI | 0 | 60 | Hz | [6 empty] | 49.9811 | ok
1459 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-05 | OPC.AW1002.1SAI.AI242307.PNT | 1SAI:AI242307.PNT | 10MKA01-23 | EXCITING TR. ACTIVE POWER | AI | 0 | 6 | MW | [6 empty] | 0.2667 | ok
1460 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-14 | OPC.AW1002.1SAI.AI242401.PNT | 1SAI:AI242401.PNT | 10MKA01-24 | FIELD CURRENT | AI | 0 | 3000 | A | [6 empty] | 1198.75 | ok
1461 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-14 | OPC.AW1002.1SAI.AI242402.PNT | 1SAI:AI242402.PNT | 10MKA01-25 | FIELD VOLTAGE | AI | 0 | 1000 | V | [6 empty] | 213.3984 | ok
1462 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242403.PNT | 1SAI:AI242403.PNT | 10MKA01-26 | GT OIL TEMPERATURE 1 | AI | 0 | 150 | C | [6 empty] | 38.1594 | ok
1463 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242404.PNT | 1SAI:AI242404.PNT | 10MKA01-27 | GT OIL TEMPERATURE 2 | AI | 0 | 150 | C | [6 empty] | 38.5844 | ok
1464 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242405.PNT | 1SAI:AI242405.PNT | 10MKA01-28 | GT HV WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 44.4562 | ok
1465 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242406.PNT | 1SAI:AI242406.PNT | 10MKA01-29 | GT LV WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 47.6375 | ok
1466 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-12 | OPC.AW1002.1SAI.AI242407.PNT | 1SAI:AI242407.PNT | 10MKA01-30 | GT OLTC CHANGING POSITION | AI | 0 | 150 | C | [6 empty] | 8.2575 | ok
1467 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242501.PNT | 1SAI:AI242501.PNT | 10MKA01-209 | ET A PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 59.2461 | ok
1468 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242502.PNT | 1SAI:AI242502.PNT | 10MKA01-210 | ET B PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 63.918 | ok
1469 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 12 | GENERATOR TRANSFORMER #1 | F296S-D0606-11 | OPC.AW1002.1SAI.AI242503.PNT | 1SAI:AI242503.PNT | 10MKA01-211 | ET C PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 56.918 | ok
1470 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231404.PNT | 1RAI:AI231404.PNT | 10MKG00GH001AI01 | GENERATOR H2 LEAKAGE RATE 1 | AI | 0.1 | 2 | % | [6 empty] | 0.0027344 | no
1471 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231504.PNT | 1RAI:AI231504.PNT | 10MKG00GH001AI02 | GENERATOR H2 LEAKAGE RATE 2 | AI | 0.1 | 2 | % | [6 empty] | 0.0030078 | no
1472 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231405.PNT | 1RAI:AI231405.PNT | 10MKG00GH001AI03 | GENERATOR H2 LEAKAGE RATE 3 | AI | 0.1 | 2 | % | [6 empty] | 0.0022266 | no
1473 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231505.PNT | 1RAI:AI231505.PNT | 10MKG00GH001AI04 | GENERATOR H2 LEAKAGE RATE 4 | AI | 0.1 | 2 | % | [6 empty] | 0.0023437 | no
1474 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231406.PNT | 1RAI:AI231406.PNT | 10MKG00GH001AI05 | GENERATOR H2 LEAKAGE RATE 5 | AI | 0.1 | 2 | % | [6 empty] | 0.0012109 | no
1475 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231506.PNT | 1RAI:AI231506.PNT | 10MKG00GH001AI06 | GENERATOR H2 LEAKAGE RATE 6 | AI | 0.1 | 2 | % | [6 empty] | 0.0042187 | no
1476 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231407.PNT | 1RAI:AI231407.PNT | 10MKG00GH001AI07 | GENERATOR H2 LEAKAGE RATE 7 | AI | 0.1 | 2 | % | [6 empty] | 0.0039844 | no
1477 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231507.PNT | 1RAI:AI231507.PNT | 10MKG00GH001AI08 | GENERATOR H2 LEAKAGE RATE 8 | AI | 0.1 | 2 | % | [6 empty] | 0.0026172 | no
1478 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231105.PNT | 1RAI:AI231105.PNT | 10MKG10CP201 | GENERATOR INLET HYDROGEN PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.29201 | ok
1479 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI230407.PNT | 1RAI:AI230407.PNT | 10MKG10CT001 | GENERATOR INLET HYDROGEN TEMP | RTD | 0 | 100 | C | [6 empty] | 27.4738 | ok
1480 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI230501.PNT | 1RAI:AI230501.PNT | 10MKG11CT001 | GENERATOR EXHAUST HYDROGEN TEMP | RTD | 0 | 100 | C | [6 empty] | 27.7206 | ok
1481 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231403.PNT | 1RAI:AI231403.PNT | 10MKG30CQ201 | GENERATOR TURBINE SIDE HYDROGEN HUMIDITY | AI | -40 | 10 | g/m3 | [6 empty] | -39.8047 | ok
1482 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231503.PNT | 1RAI:AI231503.PNT | 10MKG30CQ202 | GENERATOR COLLECTOR SIDE HYDROGEN HUMIDITY | AI | -40 | 10 | g/m3 | [6 empty] | -40.0254 | no
1483 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-26 | OPC.AW1002.1RAI.AI231502.PNT | 1RAI:AI231502.PNT | 10MKG50CQ201 | GENERATOR HYDROGEN PURITY | AI | 0 | 100 | % |  |  | 95 |  |  |  | 94.7383 | ok
1484 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230207.PNT | 1RAI:AI230207.PNT | 10PGA33CT001 | GENERATOR HYDROGEN COOLER MAIN PIPE INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 30 | ok
1485 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230301.PNT | 1RAI:AI230301.PNT | 10PGA33CT002 | GENERATOR HYDROGEN COOLER NO.1 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 28.0194 | ok
1486 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230401.PNT | 1RAI:AI230401.PNT | 10PGA33CT003 | GENERATOR HYDROGEN COOLER NO.2 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 30.4097 | ok
1487 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230302.PNT | 1RAI:AI230302.PNT | 10PGA33CT004 | GENERATOR HYDROGEN COOLER NO.3 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 29.4095 | ok
1488 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230402.PNT | 1RAI:AI230402.PNT | 10PGA33CT005 | GENERATOR HYDROGEN COOLER NO.4 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 27.7986 | ok
1489 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 13 | GENERATOR H2 SYSTEM #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230303.PNT | 1RAI:AI230303.PNT | 10PGA33CT006 | TURBINE HOUSER COOLING RETURN WATER TEMP 3 | RTD | 0 | 50 | C | [6 empty] | 28.8768 | ok
1490 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 14 | STEADY BEARING GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227308.PNT | 1QAI:AI227308.PNT | 10MKA00CT149 | GENERATOR STEADY BEARING TEMP | RTD | 0 | 100 | C | [6 empty] | 54.5985 | ok
1491 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 14 | STEADY BEARING GENERATOR #1 | F296S-J0201-44 | OPC.AW1002.1QAI.AI227207.PNT | 1QAI:AI227207.PNT | 10MKA00CT150 | GENERATOR STEADY BEARING RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 41.322 | ok
1492 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-04 | OPC.AW1002.1SAI.AI242504.PNT | 1SAI:AI242504.PNT | 10BBT01-01 | UAT HV A PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 481.0547 | ok
1493 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-04 | OPC.AW1002.1SAI.AI242505.PNT | 1SAI:AI242505.PNT | 10BBT01-02 | UAT HV B PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 483.5938 | ok
1494 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-04 | OPC.AW1002.1SAI.AI242506.PNT | 1SAI:AI242506.PNT | 10BBT01-03 | UAT HV C PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 471.2891 | ok
1495 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-04 | OPC.AW1002.1SAI.AI242507.PNT | 1SAI:AI242507.PNT | 10BBT01-04 | UAT ACTIVE-POWER MEASUREMENT | AI | 0 | 40 | MW | [6 empty] | 13.3926 | ok
1496 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-05 | OPC.AW1002.1SAI.AI254601.PNT | 1SAI:AI254601.PNT | 10BBT01-06 | UAT WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 48.275 | ok
1497 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-05 | OPC.AW1002.1SAI.AI254602.PNT | 1SAI:AI254602.PNT | 10BBT01-07 | UAT OIL TEMPERATURE 1 | AI | 0 | 150 | C | [6 empty] | 48.1313 | ok
1498 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 | F296S-D0608-05 | OPC.AW1002.1SAI.AI254603.PNT | 1SAI:AI254603.PNT | 10BBT01-08 | UAT OIL TEMPERATURE 2 | AI | 0 | 150 | C | [6 empty] | 42.2469 | ok
1499 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0608-06 | OPC.AW1002.1SAI.AI254604.PNT | 1SAI:AI254604.PNT | 10BBA02-05 | 10BBA02 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 616.582 | ok
1500 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0607-07 | OPC.AW1002.1SAI.AI254702.PNT | 1SAI:AI254702.PNT | 10BBA04-01 | CURRENT MEASUREMENT OF SST LV SIDE | AI | 0 | 3000 | A | [6 empty] | -5.918 | no
1501 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0608-09 | OPC.AW1002.1SAI.AI254606.PNT | 1SAI:AI254606.PNT | 10BBA07-01 | VOLTAGE MEASUREMENT | AI | 0 | 7 | kV | [6 empty] | 6.2516 | ok
1502 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0610-06 | OPC.AW1002.1SAI.AI254704.PNT | 1SAI:AI254704.PNT | 10BBA11-05 | 10BBA11 BREAKER CURRENT MESUREMENT | AI | 0 | 300 | A | [6 empty] | 24.0938 | ok
1503 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0610-06 | OPC.AW1002.1SAI.AI254705.PNT | 1SAI:AI254705.PNT | 10BBA11-10 | 10BFD01 BREAKER CURRENT MEASUREMENT | AI | 0 | 4000 | A | [6 empty] | 334.5312 | ok
1504 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0608-07 | OPC.AW1002.1SAI.AI254605.PNT | 1SAI:AI254605.PNT | 10BBB02-05 | 10BBB02 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 884.0039 | ok
1505 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0607-07 | OPC.AW1002.1SAI.AI254703.PNT | 1SAI:AI254703.PNT | 10BBB04-01 | CURRENT MEASUREMENT OF SST LV SIDE | AI | 0 | 3000 | A | [6 empty] | -4.7461 | no
1506 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0608-13 | OPC.AW1002.1SAI.AI254701.PNT | 1SAI:AI254701.PNT | 10BBB06-05 | 10BBB06 BREAKER CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 88.2324 | ok
1507 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0608-10 | OPC.AW1002.1SAI.AI254607.PNT | 1SAI:AI254607.PNT | 10BBB07-01 | VOLTAGE MEASUREMENT | AI | 0 | 7 | kV | [6 empty] | 6.1805 | ok
1508 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0610-07 | OPC.AW1002.1SAI.AI254706.PNT | 1SAI:AI254706.PNT | 10BBB11-05 | 10BBB11 BREAKER CURRENT MESUREMENT | AI | 0 | 300 | A | [6 empty] | 28.7285 | ok
1509 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 2 | MEDIUM VOLTAGE SYSTEM #1 | F296S-D0610-07 | OPC.AW1002.1SAI.AI254707.PNT | 1SAI:AI254707.PNT | 10BBB11-10 | 10BFE01 BREAKER CURRENT MEASUREMENT | AI | 0 | 4000 | A | [6 empty] | 586.0938 | ok
1510 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-08 | OPC.AW1002.1TAI.AI261403.PNT | 1TAI:AI261403.PNT | 10BFA01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 391.3926 | ok
1511 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261606.PNT | 1TAI:AI261606.PNT | 10BFA02A-05 | 10BFA02A BREAKER CURRENT MEASUREMENT | AI | 0 | 800 | A | [6 empty] | 21.6699 | ok
1512 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261702.PNT | 1TAI:AI261702.PNT | 10BFA02B-05 | 10BFA02B BREAKER CURRENT MEASUREMENT | AI | 0 | 600 | A | [6 empty] | -0.19531 | no
1513 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261704.PNT | 1TAI:AI261704.PNT | 10BFA03A-05 | 10BFA03A BREAKER CURRENT MEASUREMENT | AI | 0 | 400 | A | [6 empty] | 17.793 | ok
1514 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-03 | OPC.AW1002.1TAI.AI261501.PNT | 1TAI:AI261501.PNT | 10BFA03B-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 83.5254 | ok
1515 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-07 | OPC.AW1002.1TAI.AI261401.PNT | 1TAI:AI261401.PNT | 10BFA07-06 | 10BFA07 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 1.5234 | ok
1516 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-08 | OPC.AW1002.1TAI.AI261404.PNT | 1TAI:AI261404.PNT | 10BFB01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 404.6797 | ok
1517 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261701.PNT | 1TAI:AI261701.PNT | 10BFB02A-05 | 10BFB02A BREAKER CURRENT MEASUREMENT | AI | 0 | 800 | A | [6 empty] | -0.3125 | no
1518 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261703.PNT | 1TAI:AI261703.PNT | 10BFB02B-05 | 10BFB02B BREAKER CURRENT MEASUREMENT | AI | 0 | 600 | A | [6 empty] | 64.7754 | ok
1519 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261705.PNT | 1TAI:AI261705.PNT | 10BFB03A-05 | 10BFB03A BREAKER CURRENT MEASUREMENT | AI | 0 | 400 | A | [6 empty] | 29.834 | ok
1520 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-08 | OPC.AW1002.1TAI.AI261407.PNT | 1TAI:AI261407.PNT | 10BFC01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 391.3926 | ok
1521 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610-12 | OPC.AW1002.1TAI.AI261405.PNT | 1TAI:AI261405.PNT | 10BFD01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 390.732 | ok
1522 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610- | OPC.AW1002.1TAI.AI262102.PNT | 1TAI:AI262102.PNT | 10BFD02-05 | SPARE（10BFD02 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1523 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610- | OPC.AW1002.1TAI.AI262103.PNT | 1TAI:AI262103.PNT | 10BFD03-05 | SPARE（10BFD03 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1524 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610- | OPC.AW1002.1TAI.AI262101.PNT | 1TAI:AI262101.PNT | 10BFD04-05 | SPARE（10BFD04 BREAKER CURRENT MEASUREMENT） | AI | 0 | 600 | A | [8 empty] | TIDAK DIPAKAI
1525 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610-12 | OPC.AW1002.1TAI.AI261406.PNT | 1TAI:AI261406.PNT | 10BFE01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 389.0398 | ok
1526 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610- | OPC.AW1002.1TAI.AI262104.PNT | 1TAI:AI262104.PNT | 10BFE02-05 | SPARE（10BFE02 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1527 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610- | OPC.AW1002.1TAI.AI262105.PNT | 1TAI:AI262105.PNT | 10BFE03-05 | SPARE（10BFE03 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1528 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0610-11 | OPC.AW1002.1TAI.AI261402.PNT | 1TAI:AI261402.PNT | 10BFE04-06 | 10BFE03 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | -0.64453 | no
1529 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255101.PNT | 1SAI:AI255101.PNT | 10BFT01-05 | 10BBA11 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 21.9316 | ok
1530 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255102.PNT | 1SAI:AI255102.PNT | 10BFT01-10 | 10BFA01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 250.0781 | ok
1531 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-06 | OPC.AW1002.1SAI.AI255103.PNT | 1SAI:AI255103.PNT | 10BFT02-05 | 10BBB11 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 51.3164 | ok
1532 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-06 | OPC.AW1002.1SAI.AI255104.PNT | 1SAI:AI255104.PNT | 10BFT02-10 | 10BFB01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 486.7969 | ok
1533 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255105.PNT | 1SAI:AI255105.PNT | 10BFT03-05 | 10BBA18 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 13.7578 | ok
1534 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255106.PNT | 1SAI:AI255106.PNT | 10BFT03-10 | 10BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 152.1387 | ok
1535 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255107.PNT | 1SAI:AI255107.PNT | 10BFT03-11 | 10BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 160.8105 | ok
1536 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 3 | LOW VOLTAGE SYSTEM #1 | F296S-D0609-05 | OPC.AW1002.1SAI.AI255108.PNT | 1SAI:AI255108.PNT | 10BFT03-12 | 10BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 137.7246 | ok
1537 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-03 | OPC.AW1002.1TAI.AI261502.PNT | 1TAI:AI261502.PNT | 10BFB03B-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 136.377 | ok
1538 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261706.PNT | 1TAI:AI261706.PNT | 10BFD03I-05 | 10BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 33.1543 | ok
1539 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261607.PNT | 1TAI:AI261607.PNT | 10BFD03I-06 | 10BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 46.6699 | ok
1540 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0609-09 | OPC.AW1002.1TAI.AI261608.PNT | 1TAI:AI261608.PNT | 10BFD03I-07 | 10BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 34.2627 | ok
1541 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-12 | OPC.AW1002.1TAI.AI261508.PNT | 1TAI:AI261508.PNT | 10BMA01A-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | -0.34883 | no
1542 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-11 | OPC.AW1002.1TAI.AI261506.PNT | 1TAI:AI261506.PNT | 10BMA02-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 1.6992 | ok
1543 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-11 | OPC.AW1002.1TAI.AI261507.PNT | 1TAI:AI261507.PNT | 10BMA03-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | -0.76172 | no
1544 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-07 | OPC.AW1002.1TAI.AI261504.PNT | 1TAI:AI261504.PNT | 10BMB01B-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 391.3926 | ok
1545 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-09 | OPC.AW1002.1TAI.AI261707.PNT | 1TAI:AI261707.PNT | 10BMB02D-05 | 10BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 0.087891 | ok
1546 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-09 | OPC.AW1002.1TAI.AI262107.PNT | 1TAI:AI262107.PNT | 10BMB02D-06 | 10BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | -0.23438 | no
1547 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-09 | OPC.AW1002.1TAI.AI262108.PNT | 1TAI:AI262108.PNT | 10BMB02D-07 | 10BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | -0.063477 | no
1548 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615- | OPC.AW1002.1TAI.AI262106.PNT | 1TAI:AI262106.PNT | 10BMB03-01 | SPARE（CURRENT MEASUREMENT） | AI | 0 | 150 | A | [8 empty] | TIDAK DIPAKAI
1549 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-07 | OPC.AW1002.1TAI.AI261505.PNT | 1TAI:AI261505.PNT | 10BMC01A-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 382.5457 | ok
1550 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #1 | F296S-D0615-06 | OPC.AW1002.1TAI.AI261503.PNT | 1TAI:AI261503.PNT | 10BMC02-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 1.6113 | ok
1551 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 5 | UPS #1 | F296S-D0614-07 | OPC.AW1002.1TAI.AI262201.PNT | 1TAI:AI262201.PNT | 10BRA-01 | BUSBAR VOLTAGE | AI | 0 | 300 | V | [6 empty] | 224.0273 | ok
1552 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 5 | UPS #1 | F296S-D0614-07 | OPC.AW1002.1TAI.AI262202.PNT | 1TAI:AI262202.PNT | 10BRA-02 | BUSBAR FREQUENCY | AI | 0 | 60 | Hz | [6 empty] | 49.9555 | ok
1553 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 5 | UPS #1 | F296S-D0614-07 | OPC.AW1002.1TAI.AI262203.PNT | 1TAI:AI262203.PNT | 10BRA-03 | OUTPUT CURRENT | AI | 0 | 500 | A | [6 empty] | 18.7988 | ok
1554 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-05 | OPC.AW1002.1TAI.AI262204.PNT | 1TAI:AI262204.PNT | 10BTA01-01 | #1 CHARGER CURRENT | AI | 0 | 300 | A | [6 empty] | -2.2617 | no
1555 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-05 | OPC.AW1002.1TAI.AI262205.PNT | 1TAI:AI262205.PNT | 10BTA01-02 | COMMON CHARGER CURRENT | AI | 0 | 300 | A | [6 empty] | 0 | ok
1556 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-05 | OPC.AW1002.1TAI.AI262206.PNT | 1TAI:AI262206.PNT | 10BTA01-03 | BATERY BANK CURRENT | AI | 0 | 1250 | A | [6 empty] | -7.5474 | no
1557 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-05 | OPC.AW1002.1TAI.AI262207.PNT | 1TAI:AI262207.PNT | 10BTA01-04 | ML VOLTAGE | AI | 0 | 300 | V | [6 empty] | 236.6719 | ok
1558 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262301.PNT | 1TAI:AI262301.PNT | 10BTB-01 | #1 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 9.4375 | ok
1559 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262302.PNT | 1TAI:AI262302.PNT | 10BTB-02 | #2 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 2.5898 | ok
1560 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262303.PNT | 1TAI:AI262303.PNT | 10BTB-03 | #2 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 0 | ok | OUT OFF RANGE
1561 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262304.PNT | 1TAI:AI262304.PNT | 10BTB-04 | BATERY BANK 1 CURRENT | AI | 0 | 400 | A | [6 empty] | 10.2656 | ok
1562 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262305.PNT | 1TAI:AI262305.PNT | 10BTB-05 | ML 1 VOLTAGE(0~150V) | AI | 0 | 150 | V | [6 empty] | 113.9648 | ok
1563 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262306.PNT | 1TAI:AI262306.PNT | 10BTB-06 | BATERY BANK 2 CURRENT | AI | 0 | 400 | A | [6 empty] | 10.5625 | ok
1564 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 6 | DC POWER SYSTEM #1 | F296S-D0612-16 | OPC.AW1002.1TAI.AI262307.PNT | 1TAI:AI262307.PNT | 10BTB-07 | ML 2 VOLTAGE(0~150V) | AI | 0 | 150 | V | [6 empty] | 114.0908 | ok
1565 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 7 | EMERGENCY DIESEL GENERATOR #1 | F296S-D0615-13 | OPC.AW1002.1TAI.AI261601.PNT | 1TAI:AI261601.PNT | 10MJAGC001-01 | STATOR CURRENT MEASUREMENT | AI | 0 | 1200 | A | [6 empty] | 1.7812 | ok
1566 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 7 | EMERGENCY DIESEL GENERATOR #1 | F296S-D0615-13 | OPC.AW1002.1TAI.AI261602.PNT | 1TAI:AI261602.PNT | 10MJAGC001-02 | STATOR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | -2.6048 | no
1567 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 7 | EMERGENCY DIESEL GENERATOR #1 | F296S-D0615-13 | OPC.AW1002.1TAI.AI261603.PNT | 1TAI:AI261603.PNT | 10MJAGC001-03 | FREQUENCY MEASUREMENT | AI | 0 | 60 | Hz | [6 empty] | 51.6527 | ok
1568 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 7 | EMERGENCY DIESEL GENERATOR #1 | F296S-D0615-13 | OPC.AW1002.1TAI.AI261604.PNT | 1TAI:AI261604.PNT | 10MJAGC001-04 | ACTIVE POWER MEASUREMENT | AI | 0 | 800 | kW | [6 empty] | 75.2832 | ok
1569 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 7 | EMERGENCY DIESEL GENERATOR #1 | F296S-D0615-13 | OPC.AW1002.1TAI.AI261605.PNT | 1TAI:AI261605.PNT | 10MJAGC001-05 | REACTIVE POWER MEASUREMENT | AI | 0 | 800 | kVar | [6 empty] | 9.4834 | ok
1570 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1M_FULSTM2.AO162502.OUT | 1M_FULSTM2:AO162502.OUT | 00LCE13AA101XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1571 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1M_FULSTM.AO162802.OUT | 1M_FULSTM:AO162802.OUT | 00LCE13AA102XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1572 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161504.PNT | 1MAI:AI161504.PNT | 00LCE13AA101XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1573 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1M_CNCURT.AO162503.OUT | 1M_CNCURT:AO162503.OUT | 10LCE13AA102XB11 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1574 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161505.PNT | 1MAI:AI161505.PNT | 10LCE13AA102XB12 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.25391 | ok
1575 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161408.PNT | 1MAI:AI161408.PNT | 00LCE13AA102XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1576 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1EAI.AI051706.PNT | 1EAI:AI051706.PNT | 10HJF50CF201 | SUPPLYING OIL FLOW | AI | 0 | 40 | t/h | [6 empty] | 0 | ok
1577 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1EAI.AI051406.PNT | 1EAI:AI051406.PNT | 10HJF50CP201 | SUPPLYING OIL PRESSURE | AI | 0 | 4.0 | MPa | [6 empty] | 0.062969 | ok
1578 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1EAI.AI052303.PNT | 1EAI:AI052303.PNT | 10HJF60AA101XB12 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.73828 | no
1579 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1EAI.AI052104.PNT | 1EAI:AI052104.PNT | 10HJF60CF201 | RETURNED OIL FLOW | AI | 0 | 40 | t/h | [6 empty] | 0 | ok
1580 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1LAI.AI140607.PNT | 1LAI:AI140607.PNT | 10HJF60CP201 | RETURN OIL PRESSURE | AI | 0 | 1.0 | MPa | [6 empty] | 0.54656 | ok
1581 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1E_FUELOIL.AO052706.OUT | 1E_FUELOIL:AO052706.OUT | 10HJF60AA101XB11 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1582 | 1 | UJPCT #1 | 11 | FUEL OIL SYSTEM #1 | 1 | FUEL OIL #1 | 50-F296S-J0201-17 | OPC.AW1002.1IAI.AI100304.PNT | 1IAI:AI100304.PNT | 10HJF50CT001 | SUPPLYING OIL TEMPERATURE | RTD | 0 | 100 | °C | [6 empty] | 28.9288 | ok
1583 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | F296S-J0201-06 | OPC.AW1002.1QAI.AI212101.PNT | 1QAI:AI212101.PNT | 10(20)LBG10CT001 | AUXILIARY STEAM HEADER TEMP | TC | 0 | 350 | C | [6 empty] | 309.2457 | ok
1584 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | F296S-J0201-06 | OPC.AW1002.1MAI.AI160603.PNT | 1MAI:AI160603.PNT | 10LBG10CP201 | AUXILIARY STEAM HEADER PRESS | AI | 0 | 1.2 | MPa | [6 empty] | 0.90673 | ok
1585 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | F296S-J0201-06 | OPC.AW1002.1M_AUXHDR.AO162401.OUT | 1M_AUXHDR:AO162401.OUT | 10LBG13AA101 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 64.4325 | ok
1586 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 1 | AUXILIARY STEAM #1 | F296S-J0201-06 | OPC.AW1002.1MAI.AI161401.PNT | 1MAI:AI161401.PNT | 10LBG13AA101XB12 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 64.8496 | ok
1587 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | F296S-J0201-11 | OPC.AW1002.1OAI.AI191304.PNT | 1OAI:AI191304.PNT | 10MAW10AA001XB12 | REGULATING FLOW VALVE (RFV) POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1588 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | F296S-J0201-11 | OPC.AW1002.1QAI.AI213106.PNT | 1QAI:AI213106.PNT | 10MAW10CP201 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX PRESS | AI | 0 | 6.5 | MPa | [6 empty] | 0.02666 | ok
1589 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | F296S-J0201-11 | OPC.AW1002.1QAI.AI212201.PNT | 1QAI:AI212201.PNT | 10MAW10CT001 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX TEMP | TC | 0 | 600 | C | [6 empty] | 128.4051 | ok
1590 | 1 | UJPCT #1 | 12 | AUXILIARY STEAM SYSTEM #1 | 2 | TURBINE PROPER AUXILIARY STEAM #1 | F296S-J0201-11 | OPC.AW1002.1MAI.AI163306.PNT | 1MAI:AI163306.PNT | 10MAW10CT002 | IP CYLINDER START STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 177.5117 | ok
1591 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1IAI.AI100601.PNT | 1IAI:AI100601.PNT | 10HJF71CB201B | 1# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.30469 | ok
1592 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1IAI.AI100602.PNT | 1IAI:AI100602.PNT | 10HJF72CB201B | 2# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.30078 | ok
1593 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1IAI.AI100603.PNT | 1IAI:AI100603.PNT | 10HJF73CB201B | 3# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.33984 | ok
1594 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1IAI.AI100604.PNT | 1IAI:AI100604.PNT | 10HJF74CB201B | 4# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.28125 | ok
1595 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1HAI.AI091201.PNT | 1HAI:AI091201.PNT | 10HJF71CB202B | 1# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.25781 | ok
1596 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1HAI.AI091202.PNT | 1HAI:AI091202.PNT | 10HJF72CB202B | 2# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.33984 | ok
1597 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1HAI.AI091203.PNT | 1HAI:AI091203.PNT | 10HJF73CB202B | 3# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.27148 | ok
1598 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1HAI.AI091204.PNT | 1HAI:AI091204.PNT | 10HJF74CB202B | 4# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.2793 | ok
1599 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1GAI.AI071201.PNT | 1GAI:AI071201.PNT | 10HJF71CB203B | 1# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.18359 | ok
1600 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1GAI.AI071202.PNT | 1GAI:AI071202.PNT | 10HJF72CB203B | 2# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.14062 | ok
1601 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1GAI.AI071203.PNT | 1GAI:AI071203.PNT | 10HJF73CB203B | 3# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.33008 | ok
1602 | 1 | UJPCT #1 | 13 | IGNITION FIRING SYSYTEM#1 | 1 | FUEL OIL BURNER #1 | 50-F296S-J0201-17 | OPC.AW1002.1GAI.AI071204.PNT | 1GAI:AI071204.PNT | 10HJF74CB203B | 4# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.40625 | ok
1603 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 1 | INTERMITTENT BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1JAI.AI112701.PNT | 1JAI:AI112701.PNT | 10EGR11AP001XB13 | INTERMITTENT BLOWDOWN PIT DISCHARGE PUMP A CURRENT | AI | 0 | 500 | A | [6 empty] | -0.88867 | no
1604 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 1 | INTERMITTENT BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1JAI.AI112702.PNT | 1JAI:AI112702.PNT | 10EGR12AP001XB13 | INTERMITTENT BLOWDOWN PIT DISCHARGE PUMP B CURRENT | AI | 0 | 500 | A | [6 empty] | -2.0801 | no
1605 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 1 | INTERMITTENT BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI062105.PNT | 1FAI:AI062105.PNT | 10ERG00CL201 | INTERMITTENT BLOWDOWN PIT LEVEL | AI | 0 | 2050 | mm | [6 empty] | 772.834 | ok
1606 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 1 | INTERMITTENT BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI060101.PNT | 1FAI:AI060101.PNT | 10ERG00CT001 | INTERMITTENT BLOWDOWN PIT TEMP. | RTD | 0 | 100 | ℃ | [6 empty] | 86.6468 | ok
1607 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI062106.PNT | 1FAI:AI062106.PNT | 10LCQ10AA101XB12 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.35742 | no
1608 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI060506.PNT | 1FAI:AI060506.PNT | 10LCQ10CF201 | DRUM CONTINUOUS BLOWDOWN FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
1609 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI060604.PNT | 1FAI:AI060604.PNT | 10LCQ10CL201 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL | AI | 0 | 10 | KPa | [6 empty] | -11.9648 | no
1610 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI062107.PNT | 1FAI:AI062107.PNT | 10LCQ11AA101XB12 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.4023 | ok
1611 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1FAI.AI062201.PNT | 1FAI:AI062201.PNT | 10LCQ20AA101XB12 | INTERMITTENT BLOWDOWN PIT INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.11523 | ok
1612 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1F_BLFLOW.AO063505.OUT | 1F_BLFLOW:AO063505.OUT | 10LCQ10AA101XB11 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1613 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1F_BLLVL.AO063506.OUT | 1F_BLLVL:AO063506.OUT | 10LCQ11AA101XB11 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 100 | ok
1614 | 1 | UJPCT #1 | 14 | DRAIN SYSTEM#1 | 2 | CONTINUOUS BLOWDOWN #1 | 50-F296S-J0201-16 | OPC.AW1002.1F_BLDPV.AO063507.OUT | 1F_BLDPV:AO063507.OUT | 10LCQ20AA101XB11 | INTERMITTENT BLOWDOWN PIT INLET CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1615 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1M_GLDHDRP.AO163204.OUT | 1M_GLDHDRP:AO163204.OUT | 10LBW12AA101XB11 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok | REVISI TAG
1616 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI162301.PNT | 1MAI:AI162301.PNT | 10LBW12AA101XB12 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.10547 | ok
1617 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1M_GLDHDRP.AO163203.OUT | 1M_GLDHDRP:AO163203.OUT | 10LBW13AA101XB11 | HP STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1618 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI162205.PNT | 1MAI:AI162205.PNT | 10LBW13AA101XB12 | HP STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.20312 | ok
1619 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1M_GLDHDRP.AO163205.OUT | 1M_GLDHDRP:AO163205.OUT | 10LBW14AA101XB11 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1620 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI162302.PNT | 1MAI:AI162302.PNT | 10LBW14AA101XB12 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.93555 | ok
1621 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1M_GLDESUP.AO163206.OUT | 1M_GLDESUP:AO163206.OUT | 10LBW15AA101XB11 | LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.0021373 | ok
1622 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI162303.PNT | 1MAI:AI162303.PNT | 10LBW15AA101XB12 | LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.046875 | no
1623 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1M_GLDEBFP.AO162708.OUT | 1M_GLDEBFP:AO162708.OUT | 10LBW30AA404XB11 | BFP TURBINELP LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMANDBFP | AO | 0 | 100 | % | [6 empty] | 0.7 | ok
1624 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI161306.PNT | 1MAI:AI161306.PNT | 10LBW30AA404XB12 | BFP TURBINELP LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.3184 | ok | REVISI TAG
1625 | 1 | UJPCT #1 | 15 | GLAND SEAL STEAM SYSTEM #1 | 1 | GLAND SEAL STEAM #1 | F296S-J0201-10 | OPC.AW1002.1MAI.AI163304.PNT | 1MAI:AI163304.PNT | 10LBW30CT001 | BFP TURBINE GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | TC | 0 | 300 | C | [6 empty] | 105.0911 | ok
1626 | 1 | UJPCT #1 | 81 | TURBINE SEALING #1 | 3 | IP CYLINDER STARTUP STEAM PIPE #1 | F296S-J0201-07 | OPC.AW1002.1M_IPSTDESUP.AO162407.OUT | 1M_IPSTDESUP:AO162407.OUT | 10LCE12AA101XB11 | IP CYLINDER STARTUP STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1627 | 1 | UJPCT #1 | 81 | TURBINE SEALING #1 | 3 | IP CYLINDER STARTUP STEAM PIPE #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161503.PNT | 1MAI:AI161503.PNT | 10LCE12AA101XB12 | IP CYLINDER STARTUP STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.34961 | no
1628 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | MOT #1 | F296S-J0201-19 | OPC.AW1002.1OAI.AI191305.PNT | 1OAI:AI191305.PNT | 10MAV00CL201 | MAIN OIL TANK LEVEL | AI | 0 | 2200 | mm |  | 1240 | 1320 | 1820 | 2000 |  | 1273.668 | ok
1629 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | MOT #1 | F296S-J0201-19 | OPC.AW1002.1OAI.AI192507.PNT | 1OAI:AI192507.PNT | 10MAV00CT001 | MAIN OIL TANK OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 50.6883 | ok
1630 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 1 | MOT #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD116AIN.PNT_2 | 1ATC:1BD116AIN.PNT_2 | 10MAV00CT002 | MAIN OIL TANK OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 51.4028 | ok
1631 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | OIL COOLER #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI213305.PNT | 1QAI:AI213305.PNT | 10MAV15CP201 | OIL COOLER OUTLET MAIN PIPE OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.27261 | ok
1632 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | OIL COOLER #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI210504.PNT | 1QAI:AI210504.PNT | 10MAV15CT001 | OIL COOLER INLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 52.2082 | ok
1633 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | OIL COOLER #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI210405.PNT | 1QAI:AI210405.PNT | 10MAV15CT002 | OIL COOLER OUTLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 37.7755 | ok
1634 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | OIL COOLER #1 | F296S-J0201-14 | OPC.AW1002.1NAI.AI172403.PNT | 1NAI:AI172403.PNT | 10PGA34AA001XB12 | TURBINE LUBE-OIL COOLER COOLING RETURN WATER MANIFOLD MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 18.5254 | ok
1635 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 4 | OIL COOLER #1 | F296S-J0201-14 | OPC.AW1002.1RAI.AI230107.PNT | 1RAI:AI230107.PNT | 10PGA34CT001 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 30.3838 | ok
1636 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 6 | MOP #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI213304.PNT | 1QAI:AI213304.PNT | 10MAV00CP201 | MAIN OIL PUMP OUTLET PRESS | AI | 0 | 2.5 | MPa |  |  | 1.65 | 2.5 |  |  | 1.906 | ok
1637 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 7 | AOP AC #1 | F296S-J0201-19 | OPC.AW1002.1OAI.AI191307.PNT | 1OAI:AI191307.PNT | 10MAV20AP101XB13 | TURBINE AC OIL PUMP CURRENT | AI | 0 | 150 | A |  |  |  | 82.1 |  |  | -0.035156 | no
1638 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 7 | AOP AC #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI213403.PNT | 1QAI:AI213403.PNT | 10MAV20CP201 | A.C. LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.0024492 | ok
1639 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 8 | JACKING OIL A #1 | F296S-J0201-40 | OPC.AW1002.1RAI.AI231205.PNT | 1RAI:AI231205.PNT | 10MAV18CP216 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 2.499 | ok
1640 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 8 | JACKING OIL A #1 | F296S-J0201-40 | OPC.AW1002.1PAI.AI202802.PNT | 1PAI:AI202802.PNT | 10MAV30AP101XB13 | TURBINE JACKING OIL PUMP A CURRENT | AI | 0 | 150 | A |  |  |  | 103.3 |  |  | 0.20215 | ok
1641 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 9 | JACKING OIL B #1 | F296S-J0201-40 | OPC.AW1002.1PAI.AI202803.PNT | 1PAI:AI202803.PNT | 10MAV40AP101XB13 | TURBINE JACKING OIL PUMP B CURRENT | AI | 0 | 150 | A |  |  |  | 103.3 |  |  | -0.043945 | no
1642 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 10 | LUBE OIL PIPE #1 | F296S-J0201-19 | OPC.AW1002.1VALVE.1AD111AIN.PNT_2 | 1VALVE:1AD111AIN.PNT_2 | 10MAV00CP204 | LUBE OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.2802 | ok
1643 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 10 | LUBE OIL PIPE #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD116AIN.PNT_1 | 1ATC:1BD116AIN.PNT_1 | 10MAV00CT042 | LUBE OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 38.2821 | ok
1644 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 11 | AOP DC #1 | F296S-J0201-19 | OPC.AW1002.1OAI.AI191306.PNT | 1OAI:AI191306.PNT | 10MAV10AP101XB13 | TURBINE DC EMERGENCY OIL PUMP CURRENT | AI | 0 | 150 | A |  |  |  | 114.2 |  |  | -0.24609 | no
1645 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 11 | AOP DC #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI213303.PNT | 1QAI:AI213303.PNT | 10MAV10CP201 | D.C. EMERGENCY LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.0031289 | ok
1646 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_1 | 1ATC:1BD115AIN.PNT_1 | 10MAV00CT005 | #1 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 47.5965 | ok
1647 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD116AIN.PNT_5 | 1ATC:1BD116AIN.PNT_5 | 10MAV00CT012 | #1 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 88.9461 | ok
1648 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD116AIN.PNT_6 | 1ATC:1BD116AIN.PNT_6 | 10MAV00CT013 | #1 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 86.9325 | ok
1649 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD103AIN.PNT_7 | 1ATC:1BD103AIN.PNT_7 | 10TSIDEH08 | SHAFT NO.1 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 13.9297 | ok
1650 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD103AIN.PNT_8 | 1ATC:1BD103AIN.PNT_8 | 10TSIDEH09 | SHAFT NO.1 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 15.6797 | ok
1651 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 1 | BEARING TURBIN NO.1 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_3 | 1ATC:1BD105AIN.PNT_3 | 10TSIDEH20 | BEARING COVER NO.1 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 4.9854 | ok
1652 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_2 | 1ATC:1BD115AIN.PNT_2 | 10MAV00CT006 | #2 BEARING OIL DRAIN TEMP | RTD | 0 | 120 | C | [6 empty] | 47.1029 | ok
1653 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD116AIN.PNT_7 | 1ATC:1BD116AIN.PNT_7 | 10MAV00CT014 | #2 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 100.4085 | ok
1654 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_1 | 1ATC:1BD117AIN.PNT_1 | 10MAV00CT015 | #2 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 99.0727 | ok
1655 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_1 | 1ATC:1BD104AIN.PNT_1 | 10TSIDEH10 | SHAFT NO.2 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 27.7031 | ok
1656 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_2 | 1ATC:1BD104AIN.PNT_2 | 10TSIDEH11 | SHAFT NO.2 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 20.8516 | ok
1657 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 2 | BEARING TURBIN NO.2 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_4 | 1ATC:1BD105AIN.PNT_4 | 10TSIDEH21 | BEARING COVER NO.2 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 7.9175 | ok
1658 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_3 | 1ATC:1BD115AIN.PNT_3 | 10MAV00CT010 | #3 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 57.4435 | ok
1659 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_2 | 1ATC:1BD117AIN.PNT_2 | 10MAV00CT016 | #3 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 56.5601 | ok
1660 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_3 | 1ATC:1BD117AIN.PNT_3 | 10MAV00CT017 | #3 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 61.3148 | ok
1661 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_3 | 1ATC:1BD104AIN.PNT_3 | 10TSIDEH12 | SHAFT NO.3 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 38.8516 | ok
1662 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_4 | 1ATC:1BD104AIN.PNT_4 | 10TSIDEH13 | SHAFT NO.3 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 18.4844 | ok
1663 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 3 | BEARING TURBIN NO.3 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_5 | 1ATC:1BD105AIN.PNT_5 | 10TSIDEH22 | BEARING COVER NO.3 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 13.1348 | ok
1664 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD115AIN.PNT_4 | 1ATC:1BD115AIN.PNT_4 | 10MAV00CT011 | #4 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 57.1837 | ok
1665 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_4 | 1ATC:1BD117AIN.PNT_4 | 10MAV00CT018 | #4 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 73.0844 | ok
1666 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD117AIN.PNT_5 | 1ATC:1BD117AIN.PNT_5 | 10MAV00CT019 | #4 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 57.5604 | ok
1667 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_5 | 1ATC:1BD104AIN.PNT_5 | 10TSIDEH14 | SHAFT NO.4 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 44.1797 | ok
1668 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD104AIN.PNT_6 | 1ATC:1BD104AIN.PNT_6 | 10TSIDEH15 | SHAFT NO.4 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 40.4766 | ok
1669 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 4 | BEARING TURBIN NO.4 #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD105AIN.PNT_6 | 1ATC:1BD105AIN.PNT_6 | 10TSIDEH23 | BEARING COVER NO.4 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 20.4053 | ok
1670 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI210804.PNT | 1QAI:AI210804.PNT | 10MAV00CT007 | POSITION THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 44.7256 | ok
1671 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI210505.PNT | 1QAI:AI210505.PNT | 10MAV00CT008 | THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
1672 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1QAI.AI210805.PNT | 1QAI:AI210805.PNT | 10MAV00CT009 | WORK THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 49.0645 | ok
1673 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_4 | 1ATC:1BD113AIN.PNT_4 | 10MAV00CT020 | #1 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 70.9279 | ok
1674 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_5 | 1ATC:1BD113AIN.PNT_5 | 10MAV00CT021 | #2 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 82.4637 | ok
1675 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_6 | 1ATC:1BD113AIN.PNT_6 | 10MAV00CT022 | #3 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 89.037 | ok
1676 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_7 | 1ATC:1BD113AIN.PNT_7 | 10MAV00CT023 | #4 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 100.9427 | ok
1677 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_8 | 1ATC:1BD113AIN.PNT_8 | 10MAV00CT024 | #5 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 78.5925 | ok
1678 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_1 | 1ATC:1BD114AIN.PNT_1 | 10MAV00CT025 | #6 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 59.7039 | ok
1679 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_2 | 1ATC:1BD114AIN.PNT_2 | 10MAV00CT026 | #7 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 73.617 | ok
1680 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_3 | 1ATC:1BD114AIN.PNT_3 | 10MAV00CT027 | #8 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 94.9868 | ok
1681 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_4 | 1ATC:1BD114AIN.PNT_4 | 10MAV00CT028 | #9 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 57.0018 | ok
1682 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_5 | 1ATC:1BD114AIN.PNT_5 | 10MAV00CT029 | #10 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 87.2573 | ok
1683 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD114AIN.PNT_6 | 1ATC:1BD114AIN.PNT_6 | 10MAV00CT030 | #11 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 55.6768 | ok
1684 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_1 | 1ATC:1BD112AIN.PNT_1 | 10MAV00CT031 | #1 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.1146 | ok
1685 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_2 | 1ATC:1BD112AIN.PNT_2 | 10MAV00CT032 | #2 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.3223 | ok
1686 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_3 | 1ATC:1BD112AIN.PNT_3 | 10MAV00CT033 | #3 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 41.7247 | ok
1687 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_4 | 1ATC:1BD112AIN.PNT_4 | 10MAV00CT034 | #4 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.9588 | ok
1688 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_5 | 1ATC:1BD112AIN.PNT_5 | 10MAV00CT035 | #5 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.764 | ok
1689 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_6 | 1ATC:1BD112AIN.PNT_6 | 10MAV00CT036 | #6 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.634 | ok
1690 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_7 | 1ATC:1BD112AIN.PNT_7 | 10MAV00CT037 | #7 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.2443 | ok
1691 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD112AIN.PNT_8 | 1ATC:1BD112AIN.PNT_8 | 10MAV00CT038 | #8 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.1664 | ok
1692 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_1 | 1ATC:1BD113AIN.PNT_1 | 10MAV00CT039 | #9 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.764 | ok
1693 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_2 | 1ATC:1BD113AIN.PNT_2 | 10MAV00CT040 | #10 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 41.7507 | ok
1694 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD113AIN.PNT_3 | 1ATC:1BD113AIN.PNT_3 | 10MAV00CT041 | #11 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 42.686 | ok
1695 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD124AIN.PNT_1 | 1ATC:1BD124AIN.PNT_1 | 10TSIDEH03 | AXIAL DISPLACEMENT NO.1 OUTPUT | AI | -2 | 2 | um | [6 empty] | -0.18086 | ok
1696 | 1 | UJPCT #1 | 83 | TURBINE BEARING #1 | 5 | THRUST BEARING TURBIN #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD124AIN.PNT_2 | 1ATC:1BD124AIN.PNT_2 | 10TSIDEH04 | AXIAL DISPLACEMENT NO.2 OUTPUT (4~20mA) | AI | -2 | 2 | um | [6 empty] | -0.15492 | ok
1697 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-08 | OPC.AW1002.1R_HBP.AO232404.OUT | 1R_HBP:AO232404.OUT | 10LAB21AA101XB11 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1698 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-08 | OPC.AW1002.1RAI.AI232206.PNT | 1RAI:AI232206.PNT | 10LAB21AA101XB12 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.48633 | ok
1699 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-08 | OPC.AW1002.1RAI.AI231304.PNT | 1RAI:AI231304.PNT | 10LAB21CP201 | HP BYPASS DESUPERHEATING WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 2.2715 | ok
1700 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231207.PNT | 1RAI:AI231207.PNT | 10LBA30CP201 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.9268 | ok
1701 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231302.PNT | 1RAI:AI231302.PNT | 10LBA30CP202 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.9565 | ok
1702 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230606.PNT | 1RAI:AI230606.PNT | 10LBA30CT001 | HP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 394.0748 | ok
1703 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231303.PNT | 1RAI:AI231303.PNT | 10LBC30CP201 | HP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.0475 | ok
1704 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230706.PNT | 1RAI:AI230706.PNT | 10LBC30CT001 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 186.9489 | ok
1705 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230607.PNT | 1RAI:AI230607.PNT | 10LBC30CT002 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 220.2091 | ok
1706 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1R_HBP.AO232401.OUT | 1R_HBP:AO232401.OUT | 10LBF10AA101XB11 | HP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1707 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 9 | HP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI232304.PNT | 1RAI:AI232304.PNT | 10LBF10AA101XB12 | HP BYPASS PRESS CONTROL VALVE CONTROL POSITION | AI | 0 | 100 | % | [6 empty] | -0.38867 | no
1708 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231206.PNT | 1RAI:AI231206.PNT | 10LBB30CP201 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.1034 | ok
1709 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231107.PNT | 1RAI:AI231107.PNT | 10LBB30CP202 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.0978 | ok
1710 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230704.PNT | 1RAI:AI230704.PNT | 10LBB30CT001 | LP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 292.8082 | ok
1711 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231301.PNT | 1RAI:AI231301.PNT | 10LBB40CP201 | LP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 1 | MPa | [6 empty] | -0.0066211 | no
1712 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230605.PNT | 1RAI:AI230605.PNT | 10LBB40CT001 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 39.6517 | ok
1713 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI230705.PNT | 1RAI:AI230705.PNT | 10LBB40CT002 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 39.5565 | ok
1714 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI163301.PNT | 1MAI:AI163301.PNT | 10LBB41CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CONDENSER PIPE 1 TEMP | TC | 0 | 600 | C | [6 empty] | 38.051 | ok
1715 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI163302.PNT | 1MAI:AI163302.PNT | 10LBB42CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CONDENSER PIPE 2 TEMP | TC | 0 | 600 | C | [6 empty] | 39.2965 | ok
1716 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1M_LP3RD_1.AO162504.OUT | 1M_LP3RD_1:AO162504.OUT | 10LCE16AA101XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 1 CONTROL COMM | AO | 0 | 100 | % | [6 empty] | 0 | ok
1717 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161506.PNT | 1MAI:AI161506.PNT | 10LCE16AA101XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok
1718 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1M_LP3RD_2.AO162601.OUT | 1M_LP3RD_2:AO162601.OUT | 10LCE16AA102XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 2 CONTROL COMMA | AO | 0 | 100 | % | [6 empty] | 0 | ok
1719 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1MAI.AI161603.PNT | 1MAI:AI161603.PNT | 10LCE16AA102XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok
1720 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1R_LBP.AO232403.OUT | 1R_LBP:AO232403.OUT | 10LCE17AA101XB11 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1721 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-07 | OPC.AW1002.1RAI.AI232305.PNT | 1RAI:AI232305.PNT | 10LCE17AA101XB12 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.043 | ok
1722 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1R_LBP.AO232402.OUT | 1R_LBP:AO232402.OUT | 10MAN10AA101XB11 | LP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1723 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 10 | LP BYPASS VALVE #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI232205.PNT | 1RAI:AI232205.PNT | 10MAN10AA101XB12 | LP BYPASS PRESS CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 2.8965 | ok
1724 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 11 | BY PASS HYDRAULIC STATION #1 | F296S-J0201-41 | OPC.AW1002.1RAI.AI232306.PNT | 1RAI:AI232306.PNT | 10LBF20GC001AI01 | BYPASS HYDRAULIC OIL STATION OIL LEVEL | AI | 0 | 580 | mm | [6 empty] | 479.1991 | ok
1725 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 11 | BY PASS HYDRAULIC STATION #1 | F296S-J0201-41 | OPC.AW1002.1RAI.AI232207.PNT | 1RAI:AI232207.PNT | 10LBF20GC001AI02 | BYPASS HYDRAULIC OIL STATION OIL PRESS. | AI | 0 | 27.6 | MPa | [6 empty] | 15.132 | ok
1726 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 11 | BY PASS HYDRAULIC STATION #1 | F296S-J0201-41 | OPC.AW1002.1RAI.AI230502.PNT | 1RAI:AI230502.PNT | 10LBF20GC001AI03 | BYPASS HYDRAULIC OIL STATION OIL TANK TEMP | RTD | 0 | 100 | C | [6 empty] | 48.1941 | ok
1727 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 13 | FLUID CONTROL SYSTEM #1 | F296S-J0201-23(2) | OPC.AW1002.1VALVE.1AD112AIN.PNT_2 | 1VALVE:1AD112AIN.PNT_2 | 10MAX10CP201 | CONTROL FLUID MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 14.1738 | ok
1728 | 1 | UJPCT #1 | 84 | HYDRAULIC SYSTEM #1 | 13 | FLUID CONTROL SYSTEM #1 | F296S-J0201-23(2) | OPC.AW1002.1ATC.1BD115AIN.PNT_7 | 1ATC:1BD115AIN.PNT_7 | 10MAX10CT001 | CONTROL FLUID TANK OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 41.309 | ok
1729 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 2 | FLUID CONTROL SYSTEM #1 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.AW1002.1ATC.1BD124AIN.PNT_4 | 1ATC:1BD124AIN.PNT_4 | 10MAX20AA001XB12 | MSV2 POSITION | AI | 0 | 100 | % | [6 empty] | 94.3887 | ok
1730 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 2 | FLUID CONTROL SYSTEM #1 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.AW1002.1ATC.1BD12405AOUT.OUT | 1ATC:1BD12405AOUT.OUT | 10MAX20AA001XB11 | MSV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1731 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 3 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD111AIN.PNT_4 | 1VALVE:1AD111AIN.PNT_4 | 10MAX10AA102XB12 | CV4 POSITION | AI | 0 | 100 | % | [6 empty] | -0.68555 | no
1732 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 3 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD11105AOUT.OUT | 1VALVE:1AD11105AOUT.OUT | 10MAX10AA102XB11 | CV4 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | -3 | no
1733 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 4 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD106AIN.PNT_4 | 1VALVE:1AD106AIN.PNT_4 | 10MAX10AA101XB12 | CV1 POSITION | AI | 0 | 100 | % | [6 empty] | 88.3379 | ok
1734 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 4 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD10605AOUT.OUT | 1VALVE:1AD10605AOUT.OUT | 10MAX10AA101XB11 | CV1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 88.606 | ok
1735 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 5 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD107AIN.PNT_4 | 1VALVE:1AD107AIN.PNT_4 | 10MAX20AA101XB12 | CV2 POSITION | AI | 0 | 100 | % | [6 empty] | 89.8887 | ok
1736 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 5 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD10705AOUT.OUT | 1VALVE:1AD10705AOUT.OUT | 10MAX20AA101XB11 | CV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 88.606 | ok
1737 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI212301.PNT | 1QAI:AI212301.PNT | 10LBA12CP202 | HP GOV VALVE STEAM PRESS | AI | 0 | 18 | MPa | [6 empty] | 8.524 | ok
1738 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 6 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD108AIN.PNT_4 | 1VALVE:1AD108AIN.PNT_4 | 10MAX20AA102XB12 | CV3 POSITION | AI | 0 | 100 | % | [6 empty] | 15.2871 | ok
1739 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 6 | FLUID CONTROL SYSTEM #1 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD10805AOUT.OUT | 1VALVE:1AD10805AOUT.OUT | 10MAX20AA102XB11 | CV3 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 14.9593 | ok
1740 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 7 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW1002.1QAI.AI212302.PNT | 1QAI:AI212302.PNT | 10LBB11CP202 | IP GOV VALVE REAR STEAM PRESS (LEFT) | AI | 0 | 6 | MPa | [6 empty] | 1.7021 | ok
1741 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 7 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD112AIN.PNT_4 | 1VALVE:1AD112AIN.PNT_4 | 10MAB10AA001XB12 | ICV1 POSITION | AI | 0 | 100 | % | [6 empty] | 99.5117 | ok
1742 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 7 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD11205AOUT.OUT | 1VALVE:1AD11205AOUT.OUT | 10MAB10AA001XB11 | ICV1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1743 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 8 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW1002.1QAI.AI212402.PNT | 1QAI:AI212402.PNT | 10LBB12CP202 | IP GOV VALVE REAR STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa | [6 empty] | 1.7121 | ok
1744 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 8 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD113AIN.PNT_4 | 1VALVE:1AD113AIN.PNT_4 | 10MAB20AA001XB12 | ICV2 POSITION | AI | 0 | 100 | % | [6 empty] | 100.1035 | no
1745 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 8 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW1002.1VALVE.1AD11305AOUT.OUT | 1VALVE:1AD11305AOUT.OUT | 10MAB20AA001XB11 | ICV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1746 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-K0606 | OPC.AW1002.1VALVE.1AD11106AOUT.OUT | 1VALVE:1AD11106AOUT.OUT | 10DEHDCSAO01 | TURBINE POSITION | AO | 0 | 100 | % | [6 empty] | 78.0332 | ok
1747 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-K0606 | OPC.AW1002.1EAI.AI052406.PNT | 1EAI:AI052406.PNT | 10DEHDCSAI01 | TURBINE LOAD | AI | 0 | 100 | % | [6 empty] | 77.9922 | ok
1748 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1VALVE.1AD111AIN.PNT_1 | 1VALVE:1AD111AIN.PNT_1 | 10LBA11CP201 | MAIN STEAM PRESS(LEFT) | AI | 0 | 18 | MPa | [6 empty] | 11.9303 | ok
1749 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD106AIN.PNT_1 | 1ATC:1BD106AIN.PNT_1 | 10LBA11CT001 | MAIN STEAM TEMPERATURE (LEFT) | TC | 0 | 600 | C | [6 empty] | 540.0538 | ok
1750 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1VALVE.1AD112AIN.PNT_1 | 1VALVE:1AD112AIN.PNT_1 | 10LBA12CP201 | MAIN STEAM PRESS(RIGHT) | AI | 0 | 18 | MPa | [6 empty] | 11.9229 | ok
1751 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD106AIN.PNT_2 | 1ATC:1BD106AIN.PNT_2 | 10LBA12CT001 | MAIN STEAM TEMPERATURE (RIGHT) | TC | 0 | 600 | C | [6 empty] | 539.5242 | ok
1752 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211101.PNT | 1QAI:AI211101.PNT | 10LBC11CT001 | HP EXHAUSTING PIPE(LEFT) TOP TEMP | TC | 0 | 600 | C | [6 empty] | 331.4538 | ok
1753 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211201.PNT | 1QAI:AI211201.PNT | 10LBC11CT002 | HP EXHAUSTING PIPE(LEFT) BOTTOM TEMP | TC | 0 | 600 | C | [6 empty] | 285.9821 | ok
1754 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211102.PNT | 1QAI:AI211102.PNT | 10LBC12CT001 | HP EXHAUSTING PIPE(RIGHT) TOP TEMP | TC | 0 | 600 | C | [6 empty] | 314.8246 | ok
1755 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211202.PNT | 1QAI:AI211202.PNT | 10LBC12CT002 | HP EXHAUSTING PIPE(RIGHT) BOTTOM TEMP | TC | 0 | 600 | C | [6 empty] | 332.8947 | ok
1756 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1VALVE.1AD107AIN.PNT_2 | 1VALVE:1AD107AIN.PNT_2 | 10MAA10CP201 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.4378 | ok
1757 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1M_MSTFLOW_1.SIGSEL2OUT.PNT | 1M_MSTFLOW_1:SIGSEL2OUT.PNT | 10MAA10CP202C1 | STEAM PRESSURE AFTER GOV STAGE SIGSEL | AI | 0 | 20 | MPa | [6 empty] | 7.4284 | ok
1758 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160402.PNT | 1MAI:AI160402.PNT | 10MAA10CP202 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.4256 | ok
1759 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160502.PNT | 1MAI:AI160502.PNT | 10MAA10CP203 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.4266 | ok
1760 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1MAI.AI160602.PNT | 1MAI:AI160602.PNT | 10MAA10CP204 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.4191 | ok
1761 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1RAI.AI231106.PNT | 1RAI:AI231106.PNT | 10MAA10CP205 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.4472 | ok
1762 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI212401.PNT | 1QAI:AI212401.PNT | 10MAA10CP206 | HP SIXTH STAGE STEAM PRESS | AI | 0 | 10 | MPa | [6 empty] | 3.7227 | ok
1763 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1VALVE.1AD108AIN.PNT_2 | 1VALVE:1AD108AIN.PNT_2 | 10MAA10CP207 | HP EXHAUSTING STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.2672 | ok
1764 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD107AIN.PNT_2 | 1ATC:1BD107AIN.PNT_2 | 10MAA10CT001 | HP EXHAUSTING TEMP (UPPER) | TC | 0 | 600 | C | [6 empty] | 334.0263 | ok
1765 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD111AIN.PNT_1 | 1ATC:1BD111AIN.PNT_1 | 10MAA10CT002 | HP EXHAUSTING TEMP (LOWER) | TC | 0 | 600 | C | [6 empty] | 334.9051 | ok
1766 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD107AIN.PNT_1 | 1ATC:1BD107AIN.PNT_1 | 10MAA10CT003 | STEAM TEMP AFTER HP GOV STAGE | TC | 0 | 600 | C | [6 empty] | 492.3121 | ok
1767 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_5 | 1ATC:1BD108AIN.PNT_5 | 10MAA10CT004 | HP EXHAUSTING UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 332.6085 | ok
1768 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_6 | 1ATC:1BD108AIN.PNT_6 | 10MAA10CT005 | HP EXHAUSTING BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 322.762 | ok
1769 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD107AIN.PNT_4 | 1ATC:1BD107AIN.PNT_4 | 10MAA10CT006 | HP INNER CYLINDER UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 504.6686 | ok
1770 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD107AIN.PNT_6 | 1ATC:1BD107AIN.PNT_6 | 10MAA10CT007 | HP INNER CYLINDER UPPER HALF OUTER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 508.7286 | ok
1771 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD107AIN.PNT_5 | 1ATC:1BD107AIN.PNT_5 | 10MAA10CT008 | HP INNER CYLINDER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 500.3438 | ok
1772 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD107AIN.PNT_7 | 1ATC:1BD107AIN.PNT_7 | 10MAA10CT009 | HP INNER CYLINDER BOTTOM HALF OUTER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 251.434 | ok
1773 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224101.PNT | 1QAI:AI224101.PNT | 10MAA10CT010 | HP INNER & OUTER CYLINDER INTERLAY BAFFLE PLATE FRONT TEMP | TC | 0 | 600 | C | [6 empty] | 339.5456 | ok
1774 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224102.PNT | 1QAI:AI224102.PNT | 10MAA10CT011 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 455.7412 | ok
1775 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224103.PNT | 1QAI:AI224103.PNT | 10MAA10CT012 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 426.6476 | ok
1776 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224104.PNT | 1QAI:AI224104.PNT | 10MAA10CT013 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 481.4058 | ok
1777 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224105.PNT | 1QAI:AI224105.PNT | 10MAA10CT014 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 470.7851 | ok
1778 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224106.PNT | 1QAI:AI224106.PNT | 10MAA10CT015 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 477.3091 | ok
1779 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224107.PNT | 1QAI:AI224107.PNT | 10MAA10CT016 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 444.9724 | ok
1780 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD106AIN.PNT_7 | 1ATC:1BD106AIN.PNT_7 | 10MAA10CT017 | HP MSV INNER WALL METAL TEMP (LEFT) | TC | 0 | 600 | C | [6 empty] | 535.1112 | ok
1781 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD106AIN.PNT_5 | 1ATC:1BD106AIN.PNT_5 | 10MAA10CT018 | HP MSV OUTER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 518.989 | ok
1782 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD106AIN.PNT_8 | 1ATC:1BD106AIN.PNT_8 | 10MAA10CT019 | HP MSV INNER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 538.4946 | ok
1783 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD106AIN.PNT_6 | 1ATC:1BD106AIN.PNT_6 | 10MAA10CT020 | HP MSV OUTER WALL METAL TEMP (RIGHT) | TC | 0 | 600 | C | [6 empty] | 523.1961 | ok
1784 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD111AIN.PNT_4 | 1ATC:1BD111AIN.PNT_4 | 10MAA10CT021 | HP MSCV INNER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 529.5374 | ok
1785 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD111AIN.PNT_5 | 1ATC:1BD111AIN.PNT_5 | 10MAA10CT022 | HP MSCV OUTER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 450.0893 | ok
1786 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224108.PNT | 1QAI:AI224108.PNT | 10MAA10CT023 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 530.1255 | ok
1787 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224201.PNT | 1QAI:AI224201.PNT | 10MAA10CT024 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 487.0795 | ok
1788 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224202.PNT | 1QAI:AI224202.PNT | 10MAA10CT025 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 465.4263 | ok
1789 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224203.PNT | 1QAI:AI224203.PNT | 10MAA10CT026 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 493.0518 | ok
1790 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224204.PNT | 1QAI:AI224204.PNT | 10MAA10CT027 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 476.8118 | ok
1791 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224205.PNT | 1QAI:AI224205.PNT | 10MAA10CT028 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 459.0685 | ok
1792 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224206.PNT | 1QAI:AI224206.PNT | 10MAA10CT029 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 491.6984 | ok
1793 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224207.PNT | 1QAI:AI224207.PNT | 10MAA10CT030 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 490.6982 | ok
1794 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224208.PNT | 1QAI:AI224208.PNT | 10MAA10CT031 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 524.7028 | ok
1795 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224301.PNT | 1QAI:AI224301.PNT | 10MAA10CT032 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 528.6952 | ok
1796 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224302.PNT | 1QAI:AI224302.PNT | 10MAA10CT033 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 476.6804 | ok
1797 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-43 | OPC.AW1002.1QAI.AI224303.PNT | 1QAI:AI224303.PNT | 10MAA10CT034 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 450.284 | ok
1798 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-K0610 | OPC.AW1002.1RAI.AI231606.PNT | 1RAI:AI231606.PNT | 10TSIDCSAI01 | TURBINE SPEED (4~20mA) | AI | 0 | 4000 | rpm |  |  | 2850 | 3390 |  |  | 2996.918 | ok
1799 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-19 | OPC.AW1002.1VALVE.1AD113AIN.PNT_1 | 1VALVE:1AD113AIN.PNT_1 | 10TSIDEH01 | ECCENTRICITY OUTPUT (4~20mA) | AI | 0 | 100 | um | [6 empty] | 11.8125 | ok
1800 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-19 | OPC.AW1002.1VALVE.1AD111AIN.PNT_3 | 1VALVE:1AD111AIN.PNT_3 | 10TSIDEH02 | HP/IP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | -7 | 9 | um | [6 empty] | 2.115 | ok
1801 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD103AIN.PNT_5 | 1ATC:1BD103AIN.PNT_5 | 10TSIDEH06 | HP CYLINDER(LEFT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm | [6 empty] | 38.825 | ok
1802 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD103AIN.PNT_6 | 1ATC:1BD103AIN.PNT_6 | 10TSIDEH07 | HP CYLINDER(RIGHT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm | [6 empty] | 24.9375 | ok
1803 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 7 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD103AIN.PNT_1 | 1ATC:1BD103AIN.PNT_1 | 10LBB11CP201 | IP GOV VALVE FRONT STEAM PRESS (LEFT) | AI | 0 | 6 | MPa | [6 empty] | 2.0612 | ok
1804 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 7 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD106AIN.PNT_3 | 1ATC:1BD106AIN.PNT_3 | 10LBB11CT001 | REHEAT STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 540.9658 | ok
1805 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 8 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD103AIN.PNT_2 | 1ATC:1BD103AIN.PNT_2 | 10LBB12CP201 | IP GOV VALVE FRONT STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa | [6 empty] | 2.0843 | ok
1806 | 1 | UJPCT #1 | 85 | TURBINE VALVE #1 | 8 | IP TURBINE #1 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD106AIN.PNT_4 | 1ATC:1BD106AIN.PNT_4 | 10LBB12CT001 | REHEAT STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 539.3183 | ok
1807 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1VALVE.1AD108AIN.PNT_3 | 1VALVE:1AD108AIN.PNT_3 | 10MAB10CP201 | IP EXHAUSTING STEAM PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.53016 | ok
1808 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI212303.PNT | 1QAI:AI212303.PNT | 10MAB10CP202 | IP THIRD STAGE STEAM PRESS | AI | 0 | 2 | MPa | [6 empty] | 1.0886 | ok
1809 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD107AIN.PNT_3 | 1ATC:1BD107AIN.PNT_3 | 10MAB10CT001 | IP EXHAUSTING STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 353.6077 | ok
1810 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_2 | 1ATC:1BD108AIN.PNT_2 | 10MAB10CT002 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 512.2029 | ok
1811 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_4 | 1ATC:1BD108AIN.PNT_4 | 10MAB10CT003 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF OUTER TEMP | TC | 0 | 600 | C | [6 empty] | 529.7668 | ok
1812 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_1 | 1ATC:1BD108AIN.PNT_1 | 10MAB10CT004 | HP/IP OUTER CYLINDER IP STEAM INLET UPPER HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 520.9996 | ok
1813 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_3 | 1ATC:1BD108AIN.PNT_3 | 10MAB10CT005 | HP/IP OUTER CYLINDER IP STEAM INLETA UPPER HALF OUTER TEMP | TC | 0 | 600 | C | [6 empty] | 535.5331 | ok
1814 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_8 | 1ATC:1BD108AIN.PNT_8 | 10MAB10CT006 | IP EXHAUSTING BOTTOM HALF INNER METAL TEMP | TC | 0 | 600 | C | [6 empty] | 345.8464 | ok
1815 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD108AIN.PNT_7 | 1ATC:1BD108AIN.PNT_7 | 10MAB10CT007 | IP EXHAUSTING UPPER HALF INNER METAL TEMP | TC | 0 | 600 | C | [6 empty] | 328.9793 | ok
1816 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD111AIN.PNT_3 | 1ATC:1BD111AIN.PNT_3 | 10MAB10CT008 | CLAPBOARD BOTTOM HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 538.0103 | ok
1817 | 1 | UJPCT #1 | 86 | TURBINE #1 | 2 | IP TURBINE SYSTEM #1 | F296Z-J0201-43 | OPC.AW1002.1ATC.1BD111AIN.PNT_2 | 1ATC:1BD111AIN.PNT_2 | 10MAB10CT009 | CLAPBOARD UPPER HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 537.2748 | ok
1818 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD116AIN.PNT_3 | 1ATC:1BD116AIN.PNT_3 | 10MAC10CT001A | LP EXHAUSTING STEAM TEMP（FRONT & RIGHT） | RTD | 0 | 120 | C | [6 empty] | 122.4 | no
1819 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1NAI.AI172501.PNT | 1NAI:AI172501.PNT | 10MAC10CT001B | LP EXHAUSTING STEAM TEMP(FRONT & RIGHT) | RTD | 0 | 150 | C |  |  |  | 80 | 110 |  | 7.6239 | ok
1820 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296Z-J0201-04 | OPC.AW1002.1ATC.1BD116AIN.PNT_4 | 1ATC:1BD116AIN.PNT_4 | 10MAC10CT002A | LP EXHAUSTING STEAM TEMP（BACK & LEFT） | RTD | 0 | 120 | C | [6 empty] | 41.0362 | ok
1821 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1NAI.AI172502.PNT | 1NAI:AI172502.PNT | 10MAC10CT002B | LP EXHAUSTING STEAM TEMP(REAR & LEFT) | RTD | 0 | 150 | C |  |  |  | 80 | 110 |  | 41.0622 | ok
1822 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211103.PNT | 1QAI:AI211103.PNT | 10MAC10CT003 | BACKWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 193.8478 | ok
1823 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211203.PNT | 1QAI:AI211203.PNT | 10MAC10CT004 | FORWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 200.4782 | ok
1824 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211104.PNT | 1QAI:AI211104.PNT | 10MAC10CT005 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 113.9813 | ok
1825 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211204.PNT | 1QAI:AI211204.PNT | 10MAC10CT006 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 127.4872 | ok
1826 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211105.PNT | 1QAI:AI211105.PNT | 10MAC10CT007 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 119.8805 | ok
1827 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-04 | OPC.AW1002.1QAI.AI211205.PNT | 1QAI:AI211205.PNT | 10MAC10CT008 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 129.2721 | ok
1828 | 1 | UJPCT #1 | 86 | TURBINE #1 | 3 | LP TURBINE SYSTEM #1 | F296S-J0201-19 | OPC.AW1002.1ATC.1BD124AIN.PNT_3 | 1ATC:1BD124AIN.PNT_3 | 10TSIDEH05 | LP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | 0 | 16 | um | [6 empty] | 7.1919 | ok
1829 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI050703.PNT | 0CAI:AI050703.PNT | 10PAC11AP001XB13 | UNIT #1 CWP A CURRENT | AI | 0 | 300 | A | [6 empty] | 231.9023 | ok
1830 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094605.PNT | 0CAI:AI094605.PNT | 10PAA21CL201 | BEFORE UNIT #1 BAR SCREEN A WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 8.0508 | ok
1831 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094605.PNT | 0CAI:AI094605.PNT | 10PAA21CL202 | AFTER UNIT #1 BAR SCREEN A WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 8.0508 | ok | REVISI TAG
1832 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094603.PNT | 0CAI:AI094603.PNT | 10PAA31CL201 | BEFORE UNIT #1 TRAVELLING BAND A SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 8.1736 | ok
1833 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094604.PNT | 0CAI:AI094604.PNT | 10PAA31CL202 | AFTER UNIT #1 TRAVELLING BAND A SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 7 | ok
1834 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI095103.PNT | 0CAI:AI095103.PNT | 10PAB11CF201 | UNIT 1 CIRCULATING WATER OUTLET WATER FLOW | AI | 0 |  | t/h | [6 empty] | -0.97852 | no
1835 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094607.PNT | 0CAI:AI094607.PNT | 10PAB11GC001AI01 | UNIT #1 HYDRAULIC CONTROL BUTTERFLY VALVE A POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0 | ok | OUT OFF RANGE
1836 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094501.PNT | 0CAI:AI094501.PNT | 10PAC11CP201 | 1A# CIRCULATING WATER PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.2576 | ok
1837 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094101.PNT | 0CAI:AI094101.PNT | 10PAC11CT001 | 1A# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 87.1144 | ok
1838 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094201.PNT | 0CAI:AI094201.PNT | 10PAC11CT002 | 1A# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 88.6603 | ok
1839 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094102.PNT | 0CAI:AI094102.PNT | 10PAC11CT003 | 1A# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 89.5047 | ok
1840 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094202.PNT | 0CAI:AI094202.PNT | 10PAC11CT004 | 1A# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 87.0105 | ok
1841 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094103.PNT | 0CAI:AI094103.PNT | 10PAC11CT005 | 1A# CIRCULATING WATER PUMP W PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 86.7117 | ok
1842 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094203.PNT | 0CAI:AI094203.PNT | 10PAC11CT006 | 1A# CIRCULATING WATER PUMP W PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 88.2836 | ok
1843 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094106.PNT | 0CAI:AI094106.PNT | 10PAC11CT007 | 1A# CIRCULATING WATER PUMP LOWER BEARING TEMP | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 50.3765 | ok
1844 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094104.PNT | 0CAI:AI094104.PNT | 10PAC11CT008 | 1A# CIRCULATING WATER PUMP THRUST BEARING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 74.1756 | ok
1845 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094204.PNT | 0CAI:AI094204.PNT | 10PAC11CT009 | 1A# CIRCULATING WATER PUMP THRUST BEARING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 73.5001 | ok
1846 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094105.PNT | 0CAI:AI094105.PNT | 10PAC11CT010 | 1A# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 50.4025 | ok
1847 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094205.PNT | 0CAI:AI094205.PNT | 10PAC11CT011 | 1A# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 51.4938 | ok
1848 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094601.PNT | 0CAI:AI094601.PNT | 10PAC11CY201X | 1A# CIRCULATING WATER PUMP BEARING X DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 11.4284 | no
1849 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A | K0802-02 | OPC.AW0003.0CAI.AI094602.PNT | 0CAI:AI094602.PNT | 10PAC11CY201Y | 1A# CIRCULATING WATER PUMP BEARING Y DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 5.5027 | ok
1850 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI050608.PNT | 0CAI:AI050608.PNT | 10PAC12AP001XB13 | UNIT #1 CWP B CURRENT | AI | 0 | 300 | A | [6 empty] | 231.8027 | ok
1851 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094705.PNT | 0CAI:AI094705.PNT | 10PAA22CL201 | BEFORE UNIT #1 BAR SCREEN B WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 8.0518 | ok
1852 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094705.PNT | 0CAI:AI094705.PNT | 10PAA22CL202 | AFTER UNIT #1 BAR SCREEN B WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 8.0518 | ok | REVISI TAG
1853 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094703.PNT | 0CAI:AI094703.PNT | 10PAA32CL201 | BEFORE UNIT #1 TRAVELLING BAND B SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 8.1738 | ok
1854 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094704.PNT | 0CAI:AI094704.PNT | 10PAA32CL202 | AFTER UNIT #1 TRAVELLING BAND B SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 7 | ok
1855 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094707.PNT | 0CAI:AI094707.PNT | 10PAB12GC001AI01 | UNIT #1 HYDRAULIC BUTTERFLY VAVLE B POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 99.9805 | ok
1856 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094502.PNT | 0CAI:AI094502.PNT | 10PAC12CP201 | 1B# CIRCULATING WATER PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.21539 | ok
1857 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094301.PNT | 0CAI:AI094301.PNT | 10PAC12CT001 | 1B# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 86.6987 | ok
1858 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094401.PNT | 0CAI:AI094401.PNT | 10PAC12CT002 | 1B# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 85.4776 | ok
1859 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094302.PNT | 0CAI:AI094302.PNT | 10PAC12CT003 | 1B# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 85.0099 | ok
1860 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094402.PNT | 0CAI:AI094402.PNT | 10PAC12CT004 | 1B# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 82.6456 | ok
1861 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094303.PNT | 0CAI:AI094303.PNT | 10PAC12CT005 | 1B# CIRCULATING WATER PUMP W PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 86.0492 | ok
1862 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094403.PNT | 0CAI:AI094403.PNT | 10PAC12CT006 | 1B# CIRCULATING WATER PUMP W PHASE STATOR WINGDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 80.3332 | ok
1863 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094306.PNT | 0CAI:AI094306.PNT | 10PAC12CT007 | 1B# CIRCULATING WATER PUMP LOWER BEARING TEMP | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 51.8445 | ok
1864 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094304.PNT | 0CAI:AI094304.PNT | 10PAC12CT008 | 1B# CIRCULATING WATER PUMP THRUST BEARING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 63.0036 | ok
1865 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094404.PNT | 0CAI:AI094404.PNT | 10PAC12CT009 | 1B# CIRCULATING WATER PUMP THRUST BEARING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 63.9129 | ok
1866 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094305.PNT | 0CAI:AI094305.PNT | 10PAC12CT010 | 1B# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 50.5584 | ok
1867 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094405.PNT | 0CAI:AI094405.PNT | 10PAC12CT011 | 1B# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 50.0518 | ok
1868 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094701.PNT | 0CAI:AI094701.PNT | 10PAC12CY201X | 1B# CIRCULATING WATER PUMP BEARING X DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 21.9762 | no
1869 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI094702.PNT | 0CAI:AI094702.PNT | 10PAC12CY201Y | 1B# CIRCULATING WATER PUMP BEARING Y DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 3.6466 | ok
1870 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1E_IDF.SIGSEL1OUT.PNT | 1E_IDF:SIGSEL1OUT.PNT | 10H10CP201C1 | FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -29.6719 | ok
1871 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1E_AIRFLOW.FURA1AIN.PNT | 1E_AIRFLOW:FURA1AIN.PNT | 10H10CF205C1 | SEC A OUT FLOW | AI | 0 | 600 | T/H |  | 45 | 180 |  |  |  | 311.3098 | ok
1872 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1E_AIRFLOW.FURB1AIN.PNT | 1E_AIRFLOW:FURB1AIN.PNT | 10H20CF205C1 | SEC B OUT FLOW | AI | 0 | 600 | T/H |  | 45 | 180 |  |  |  | 347.5324 | ok
1873 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1E_FDF.CHARC1OUT.PNT | 1E_FDF:CHARC1OUT.PNT | 10H10CF201C1 | TOTAL AIR FLOW | AI | 0 | 1400 | T/H | [6 empty] | 1016.0096 | ok
1874 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 | 50-F296S-J0201-33 | OPC.AW1002.1E_FUELC.CALCA1OUT.PNT | 1E_FUELC:CALCA1OUT.PNT | 10HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H | [6 empty] | 123.2096 | ok
1875 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 |  | 10H10CT907 | 10H10CT907 | 10H10CT907 | Diff Temp Side A Side B | CALC | 0 | 700 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI142206.PNT)-(OPC.AW1002.1LAI.AI142306.PNT)
1876 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 |  | 10H10CT908 | 10H10CT908 | 10H10CT908 | Diff Temp Side A Side B | CALC | 0 | 700 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI142207.PNT)-(OPC.AW1002.1LAI.AI142307.PNT)
1877 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 7 | FURNACE #1 |  | 10H10CP904 | 10H10CP904 | 10H10CP904 | Diff Pressure Side A Side B | CALC | -300 | 300 | Pa | [8 empty] | (OPC.AW1002.1LAI.AI140304.PNT)-(OPC.AW1002.1LAI.AI140404.PNT)
1878 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10HAH11CT901 | 10HAH11CT901 | 10HAH11CT901 | Diff temp First stage superheated steam desupp | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI141701.PNT)-(AVG(OPC.AW1002.1FAI.AI060201.PNT);(OPC.AW1002.1FAI.AI060301.PNT))
1879 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10LAE41AA901XB | 10LAE41AA901XB | 10LAE41AA901XB | Diff ctrl and Poss of first stage desup | CALC | -100 | 100 | % | [8 empty] | (OPC.AW1002.1F_SH1.AO063502.OUT)-(OPC.AW1002.1FAI.AI061706.PNT)
1880 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10HAH21CT901 | 10HAH21CT901 | 10HAH21CT901 | Diff temp second stage superheated steam desupp A side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI141702.PNT)-(AVG(OPC.AW1002.1FAI.AI060202.PNT);(OPC.AW1002.1FAI.AI060203.PNT))
1881 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10HAH22CT901 | 10HAH22CT901 | 10HAH22CT901 | Diff temp second stage superheated steam desupp B side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI141703.PNT)-(AVG(OPC.AW1002.1FAI.AI060401.PNT);(OPC.AW1002.1FAI.AI060203.PNT))
1882 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10HAH21CT904 | 10HAH21CT904 | 10HAH21CT904 | Diff temp third stage superheated steam desupp A side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI141704.PNT)-(AVG(OPC.AW1002.1FAI.AI060204.PNT);(OPC.AW1002.1FAI.AI060303.PNT))
1883 | 1 | UJPCT #1 | 6 | BOILER & FURNACE SYSTEM #1 | 4 | SUPERHEATER #1 |  | 10HAH22CT904 | 10HAH22CT904 | 10HAH22CT904 | Diff temp third stage superheated steam desupp B side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW1002.1LAI.AI141705.PNT)-(AVG(OPC.AW1002.1FAI.AI060402.PNT);(OPC.AW1002.1FAI.AI060205.PNT))
1884 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 7 | GLAND STEAM CONDENSER #1 |  | 10LBW22CT901 | 10LBW22CT901 | 10LBW22CT901 | Delta Gland Main Pipe Temp | CALC | -100 | 300 | C | [8 empty] | (OPC.AW1002.1MAI.AI160102.PNT)-(OPC.AW1002.1QAI.AI212205.PNT)
1885 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 |  | 10LBS50CP901 | 10LBS50CP901 | 10LBS50CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.6 | 0.6 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212602.PNT)-(OPC.AW1002.1QAI.AI212503.PNT)
1886 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 |  | 10LCJ50CT902 | 10LCJ50CT902 | 10LCJ50CT902 | DCA LPH5 #1 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW1002.1QAI.AI212105.PNT )-(OPC.AW1002.1QAI.AI210106.PNT)
1887 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 14 | LP HEATER NO.5 #1 |  | 10LBS50CT902 | 10LBS50CT902 | 10LBS50CT902 | TTD LPH5 #1 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW1002.1QAI.AI211503.PNT)-(OPC.AW1002.1QAI.AI210107.PNT)
1888 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 |  | 10LBS60CP901 | 10LBS60CP901 | 10LBS60CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.4 | 0.4 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212603.PNT)-(OPC.AW1002.1QAI.AI212504.PNT)
1889 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 |  | 10LCJ60CT902 | 10LCJ60CT902 | 10LCJ60CT902 | DCA LPH6 #1 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW1002.1QAI.AI211706.PNT)-(OPC.AW1002.1QAI.AI210105.PNT)
1890 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 12 | LP HEATER NO.6 #1 |  | 10LBS60CT902 | 10LBS60CT902 | 10LBS60CT902 | TTD LPH6 #1 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW1002.1QAI.AI211505.PNT)-(OPC.AW1002.1QAI.AI210106.PNT)
1891 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 |  | 10LBS70CP901 | 10LBS70CP901 | 10LBS70CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.1 | 0.15 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212604.PNT)-(OPC.AW1002.1QAI.AI212505.PNT)
1892 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 |  | 10LCJ70CT902 | 10LCJ70CT902 | 10LCJ70CT902 | DCA LPH7 #1 | CALC | -100 | 140 | C | [8 empty] | (OPC.AW1002.1QAI.AI212106.PNT)-(OPC.AW1002.1QAI.AI210105.PNT)
1893 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 10 | LP HEATER NO.7 #1 |  | 10LBS70CT902 | 10LBS70CT902 | 10LBS70CT902 | TTD LPH7 #1 | CALC | -100 | 140 | C | [8 empty] | (OPC.AW1002.1QAI.AI211606.PNT)-(OPC.AW1002.1QAI.AI210105.PNT)
1894 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 |  | 10LBS80CP901 | 10LBS80CP901 | 10LBS80CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.1 | 0.15 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212605.PNT)-(OPC.AW1002.1QAI.AI212506.PNT)
1895 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 |  | 10LCJ80CT902 | 10LCJ80CT902 | 10LCJ80CT902 | DCA LPH8#1 | CALC | -100 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211707.PNT)-(OPC.AW1002.1QAI.AI210105.PNT)
1896 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 9 | LP HEATER NO.8 #1 |  | 10LBS80CT902 | 10LBS80CT902 | 10LBS80CT902 | TTD LPH8#1 | CALC | -100 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211607.PNT)-(OPC.AW1002.1QAI.AI210105.PNT)
1897 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 |  | 10PAH31CP901 | 10PAH31CP901 | 10PAH31CP901 | CONDENSER SIDE A CIRCULATING WATER DELTA PRESS | CALC | 0 | 0.2 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI213201.PNT)-(OPC.AW1002.1QAI.AI212707.PNT)
1898 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 |  | 10PAH31CT901 | 10PAH31CT901 | 10PAH31CT901 | CONDENSER SIDE A CIRCULATING WATER DELTA TEMP | CALC | 0 | 100 | C | [8 empty] | (OPC.AW1002.1QAI.AI210203.PNT)-(OPC.AW1002.1QAI.AI210202.PNT)
1899 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 |  | 10PAH32CP901 | 10PAH32CP901 | 10PAH32CP901 | CONDENSER SIDE B CIRCULATING WATER DELTA PRESS | CALC | 0 | 0.2 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI213107.PNT)-(OPC.AW1002.1QAI.AI213202.PNT)
1900 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 1 | CONDENSER #1 |  | 10PAH32CT901 | 10PAH32CT901 | 10PAH32CT901 | CONDENSER SIDE B CIRCULATING WATER DELTA TEMP | CALC | 0 | 100 | C | [8 empty] | (OPC.AW1002.1QAI.AI210302.PNT)-(OPC.AW1002.1QAI.AI210301.PNT)
1901 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A |  | 10PCC21CT905 | 10PCC21CT905 | 10PCC21CT905 | Average coil temp phase A CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI171105.PNT);(OPC.AW1002.1NAI.AI173404.PNT))
1902 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A |  | 10PCC21CT906 | 10PCC21CT906 | 10PCC21CT906 | Average coil temp phase B CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI171106.PNT);(OPC.AW1002.1NAI.AI173405.PNT))
1903 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 1 | SWBP #1A |  | 10PCC21CT907 | 10PCC21CT907 | 10PCC21CT907 | Average coil temp phase C CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI171107.PNT);(OPC.AW1002.1NAI.AI173406.PNT))
1904 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B |  | 10PCC22CT905 | 10PCC22CT905 | 10PCC22CT905 | Average coil temp phase A CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI173303.PNT);(OPC.AW1002.1NAI.AI173304.PNT))
1905 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B |  | 10PCC22CT906 | 10PCC22CT906 | 10PCC22CT906 | Average coil temp phase B CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI173305.PNT);(OPC.AW1002.1NAI.AI173306.PNT))
1906 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B |  | 10PCC22CT907 | 10PCC22CT907 | 10PCC22CT907 | Average coil temp phase C CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW1002.1NAI.AI173307.PNT);(OPC.AW1002.1NAI.AI173308.PNT))
1907 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 |  | 10PGA40CT901 | 10PGA40CT901 | 10PGA40CT901 | Delta T BOILER#1 | CALC | 0 | 50 | C | [8 empty] | (OPC.AW1002.1RAI.AI230103.PNT)-(OPC.AW1002.1RAI.AI230203.PNT)
1908 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 7 | CLOSED COOLING WATER PIPE #1 |  | 10PGA31CT901 | 10PGA31CT901 | 10PGA31CT901 | Delta T TURBINE#1 | CALC | 0 | 50 | C | [8 empty] | (OPC.AW1002.1RAI.AI230204.PNT)-(OPC.AW1002.1RAI.AI230106.PNT)
1909 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A |  | 10PAA21CL901 | 10PAA21CL901 | 10PAA21CL901 | DP LEVEL UNIT #1 BAR SCREEN A WITH RAKING DEVICE LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0CAI.AI094603.PNT)-(OPC.AW0003.0CAI.AI094604.PNT)
1910 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 1 | CIRCULATING WATER PUMP #1 A |  | 10PAA31CL901 | 10PAA31CL901 | 10PAA31CL901 | DP LEVEL UNIT #1 TRAVELLING BAND B SCREEN LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0CAI.AI094703.PNT)-(OPC.AW0003.0CAI.AI094704.PNT)
1911 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B |  | 10PAA22CL901 | 10PAA22CL901 | 10PAA22CL901 | DP LEVEL UNIT #1 BAR SCREEN A WITH RAKING DEVICE LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0CAI.AI094705.PNT)-(OPC.AW0003.0CAI.AI094705.PNT)
1912 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B |  | 10PAA32CL901 | 10PAA32CL901 | 10PAA32CL901 | DP LEVEL UNIT #1 TRAVELLING BAND B SCREEN LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0CAI.AI094703.PNT)-(OPC.AW0003.0CAI.AI094704.PNT)
1913 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 |  | 10BBT01-901 | 10BBT01-901 | 10BBT01-901 | UAT HV SIDE CURRENT UNBALANCE PHASE A | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW1002.1SAI.AI242504.PNT)-(((OPC.AW1002.1SAI.AI242504.PNT)+(OPC.AW1002.1SAI.AI242505.PNT)+(OPC.AW1002.1SAI.AI242506.PNT))/3))/(((OPC.AW1002.1SAI.AI242504.PNT)+(OPC.AW1002.1SAI.AI242505.PNT)+(OPC.AW1002.1SAI.AI242506.PNT))/3))*100%
1914 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 |  | 10BBT01-902 | 10BBT01-902 | 10BBT01-902 | UAT HV SIDE CURRENT UNBALANCE PHASE B | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW1002.1SAI.AI242505.PNT)-((OPC.AW1002.1SAI.AI242504.PNT+OPC.AW1002.1SAI.AI242505.PNT+OPC.AW1002.1SAI.AI242506.PNT)/3))/((OPC.AW1002.1SAI.AI242504.PNT+OPC.AW1002.1SAI.AI242505.PNT+OPC.AW1002.1SAI.AI242506.PNT)/3))*100%
1915 | 1 | UJPCT #1 | 10 | ELECTRICAL SYSTEM #1 | 1 | TRANSFORMER UAT #1 |  | 10BBT01-903 | 10BBT01-903 | 10BBT01-903 | UAT HV SIDE CURRENT UNBALANCE PHASE C | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW1002.1SAI.AI242506.PNT)-((OPC.AW1002.1SAI.AI242504.PNT+OPC.AW1002.1SAI.AI242505.PNT+OPC.AW1002.1SAI.AI242506.PNT)/3))/((OPC.AW1002.1SAI.AI242504.PNT+OPC.AW1002.1SAI.AI242505.PNT+OPC.AW1002.1SAI.AI242506.PNT)/3))*100%
1916 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 |  | 10LBQ10CP901 | 10LBQ10CP901 | 10LBQ10CP901 | Diff steam press HP turbine side and HPH side | CALC | 0 | 6.6 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212304.PNT)-(OPC.AW1002.1QAI.AI212404.PNT)
1917 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 |  | 10LAB30CT901 | 10LAB30CT901 | 10LAB30CT901 | DCA HPH1 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211704.PNT)-(OPC.AW1002.1QAI.AI211703.PNT)
1918 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 10 | HP HEATER NO.1 #1 |  | 10LBQ10CT904 | 10LBQ10CT904 | 10LBQ10CT904 | TTD HPH1 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211206.PNT)-(OPC.AW1002.1QAI.AI212103.PNT)
1919 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 |  | 10LBQ20CP901 | 10LBQ20CP901 | 10LBQ20CP901 | Diff steam press HPH2 side | CALC | 0 | 4 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212305.PNT)-(OPC.AW1002.1QAI.AI212405.PNT)
1920 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 |  | 10LAB20CT903 | 10LAB20CT903 | 10LAB20CT903 | DCA HPH2 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI212104.PNT)-(OPC.AW1002.1QAI.AI212102.PNT)
1921 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 8 | HP HEATER NO.2 #1 |  | 10LBQ20CT902 | 10LBQ20CT902 | 10LBQ20CT902 | TTD HPH2 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211401.PNT)-(OPC.AW1002.1QAI.AI212102.PNT)
1922 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 |  | 10LBQ30CP901 | 10LBQ30CP901 | 10LBQ30CP901 | Diff steam press HPH3 side | CALC | 0 | 1.9 | MPa | [8 empty] | (OPC.AW1002.1QAI.AI212306.PNT)-(OPC.AW1002.1QAI.AI212406.PNT)
1923 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 |  | 10LAB30CT903 | 10LAB30CT903 | 10LAB30CT903 | DCA HPH3 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211705.PNT)-(OPC.AW1002.1QAI.AI212102.PNT)
1924 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 6 | HP HEATER NO.3 #1 |  | 10LBQ30CT904 | 10LBQ30CT904 | 10LBQ30CT904 | TTD HPH3 #1 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI211403.PNT)-(OPC.AW1002.1QAI.AI212102.PNT)
1925 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A |  | 10MAV50CT901 | 10MAV50CT901 | 10MAV50CT901 | DIFFERENTIAL TEMPERATUR BFP TURBINE A LUBE-OIL COOLER | CALC | -50 | 100 | C | [8 empty] | (OPC.AW1002.1QAI.AI210406.PNT)-(OPC.AW1002.1QAI.AI210506.PNT)
1926 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A |  | 10LAC11CT909 | 10LAC11CT909 | 10LAC11CT909 | T-BFP A WATER END MAIN BODY TOP DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1OAI.AI193305.PNT)-(OPC.AW1002.1OAI.AI193303.PNT)
1927 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 2 | T-BFP #1A |  | 10LAC11CT910 | 10LAC11CT910 | 10LAC11CT910 | T-BFP A WATER END MAIN BODY BOTTOM DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1OAI.AI193306.PNT)-(OPC.AW1002.1OAI.AI193304.PNT)
1928 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B |  | 10MAV60CT901 | 10MAV60CT901 | 10MAV60CT901 | DIFFERENTIAL TEMPERATUR BFP TURBINE B LUBE-OIL COOLER | CALC | -50 | 100 | C | [8 empty] | (OPC.AW1002.1PAI.AI202704.PNT)-(OPC.AW1002.1PAI.AI202702.PNT)
1929 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B |  | 10LAC12CT909 | 10LAC12CT909 | 10LAC12CT909 | T-BFP B WATER END MAIN BODY TOP DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1PAI.AI202705.PNT)-(OPC.AW1002.1PAI.AI202703.PNT)
1930 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B |  | 10LAC12CT910 | 10LAC12CT910 | 10LAC12CT910 | T-BFP B WATER END MAIN BODY BOTTOM DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW1002.1QAI.AI210604.PNT)-(OPC.AW1002.1QAI.AI210705.PNT)
1931 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1QAI.AI210101.PNT | 1QAI:AI210101.PNT | 10LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 200 | C | [6 empty] | 39.815 | ok
1932 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 3 | CEP #1B | F296S-J0201-07 | OPC.AW1002.1NAI.AI173803.PNT | 1NAI:AI173803.PNT | 10LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa |  |  | 1.3 |  |  |  | 2.9164 | ok
1933 | 1 | UJPCT #1 | 2 | CONDENSATE SYSTEM #1 | 5 | AIR REMOVAL #1 - VACUUM PUMP B | F296S-J0201-14 | OPC.AW1002.1RAI.AI230201.PNT | 1RAI:AI230201.PNT | 10PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 26.3306 | ok
1934 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173804.PNT | 1NAI:AI173804.PNT | 10PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.4 | MPa | [6 empty] | 0.031688 | ok
1935 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 2 | SWBP #1B | F296S-J0201-14 | OPC.AW1002.1RAI.AI230101.PNT | 1RAI:AI230101.PNT | 10PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.5512 | ok
1936 | 1 | UJPCT #1 | 3 | CLOSE COOLING SYSTEM #1 | 6 | CCWP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI173805.PNT | 1NAI:AI173805.PNT | 10PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 0.8 | MPa |  |  | 0.5 |  |  |  | 0.5617 | ok
1937 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI212307.PNT | 1QAI:AI212307.PNT | 10LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.504 | ok
1938 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI211405.PNT | 1QAI:AI211405.PNT | 10LBS41CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 342.1165 | ok
1939 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI211307.PNT | 1QAI:AI211307.PNT | 10LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 272.6427 | ok
1940 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-05 | OPC.AW1002.1QAI.AI211407.PNT | 1QAI:AI211407.PNT | 10LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 266.0258 | ok
1941 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-04 | OPC.AW1002.1Q_FLOW.BFPSTMAIN.PNT | 1Q_FLOW:BFPSTMAIN.PNT | 10LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | t/h | [6 empty] | 3.7717 | ok
1942 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-14 | OPC.AW1002.1NAI.AI172404.PNT | 1NAI:AI172404.PNT | 10PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 97.1602 | ok
1943 | 1 | UJPCT #1 | 4 | FEEDWATER SYSTEM #1 | 4 | T-BFP #1B | F296S-J0201-14 | OPC.AW1002.1RAI.AI230205.PNT | 1RAI:AI230205.PNT | 10PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 26.9542 | ok
1944 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-19 | OPC.AW1002.1QAI.AI213404.PNT | 1QAI:AI213404.PNT | 10MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.019043 | ok
1945 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1PAI.AI203602.PNT | 1PAI:AI203602.PNT | 10MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 1000 | mm |  |  | 300 | 600 |  |  | 596.1797 | ok
1946 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1RAI.AI231204.PNT | 1RAI:AI231204.PNT | 10MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 2 | MPa | [6 empty] | 0.35266 | ok
1947 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230305.PNT | 1RAI:AI230305.PNT | 10MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C | [6 empty] | 63.5102 | ok
1948 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230405.PNT | 1RAI:AI230405.PNT | 10MKW10CT003 | GENERATOR H2 SIDE RETURN OIL TEMP(EXCITER SIDE) | RTD | 0 | 100 | C | [6 empty] | 60.5223 | ok
1949 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 2 | GENERATOR SEAL OIL - H2 SIDE #1B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230307.PNT | 1RAI:AI230307.PNT | 10MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 30.1239 | ok
1950 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 4 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230404.PNT | 1RAI:AI230404.PNT | 10MKW10CT001 | GENERATOR AIR SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 48.8047 | ok
1951 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 4 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230306.PNT | 1RAI:AI230306.PNT | 10MKW10CT004 | GENERATOR TURBINE SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 60.3924 | ok
1952 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 4 | GENERATOR SEAL OIL #1 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW1002.1RAI.AI230406.PNT | 1RAI:AI230406.PNT | 10MKW10CT005 | GENERATOR EXCITER SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 57.1187 | ok
1953 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1M_GESTAT.AO162608.OUT | 1M_GESTAT:AO162608.OUT | 10MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 12.2438 | ok
1954 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1MAI.AI162304.PNT | 1MAI:AI162304.PNT | 10MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 11.0605 | ok
1955 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1R_FLOW.GENAIN.PNT | 1R_FLOW:GENAIN.PNT | 10MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 50 | t/h |  |  | 5 | 45 |  |  | 44.0852 | ok
1956 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1RAI.AI231501.PNT | 1RAI:AI231501.PNT | 10MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2 |  |  | 0.19023 | ok
1957 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1RAI.AI231402.PNT | 1RAI:AI231402.PNT | 10MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5 |  |  | 0.3668 | ok
1958 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1MAI.AI160101.PNT | 1MAI:AI160101.PNT | 10MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | C |  |  |  | 48 |  |  | 45.6349 | ok
1959 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1NAI.AI172206.PNT | 1NAI:AI172206.PNT | 10MKF11AH001XB12 | TURBINE FLAGE&BOLT HEATER CURRENT | AI | 0 | 100 | A | [8 empty] | TIDAK DIPAKAI
1960 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1RAI.AI231103.PNT | 1RAI:AI231103.PNT | 10MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.22724 | ok
1961 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1RAI.AI231203.PNT | 1RAI:AI231203.PNT | 10MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.051431 | ok
1962 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-24 | OPC.AW1002.1RAI.AI230304.PNT | 1RAI:AI230304.PNT | 10MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | C |  |  |  | 80 |  |  | 47.1938 | ok
1963 | 1 | UJPCT #1 | 9 | GENERATOR SYSTEM #1 | 7 | GENERATOR STATOR COOLING #1B | F296S-J0201-14 | OPC.AW1002.1RAI.AI230206.PNT | 1RAI:AI230206.PNT | 10PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 41.5688 | ok
1964 | 1 | UJPCT #1 | 82 | LUBRICATION SUPPLY SYSTEM #1 | 9 | JACKING OIL B #1 | F296S-J0201-40 | OPC.AW1002.1RAI.AI231205.PNT | 1RAI:AI231205.PNT | 10MAV18CP216 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 2.499 | ok
1965 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #1 | 2 | CIRCULATING WATER PUMP #1 B | K0802-02 | OPC.AW0003.0CAI.AI095103.PNT | 0CAI:AI095103.PNT | 10PAB11CF201 | UNIT 1 CIRCULATING WATER OUTLET WATER FLOW | AI | 0 |  | t/h | [6 empty] | -0.97852 | no
1769 | 1 | UJPCT #1 | 86 | TURBINE #1 | 1 | HP TURBINE SYSTEM #1 | F296Z-J0201-43 | 10MAA10CT906 | 10MAA10CT906 | 10MAA10CT906 | DELTA HP INNER CYLINDER UPPER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [8 empty] | AVG((OPC.AW1002.1ATC.1BD107AIN.PNT_4);(OPC.AW1002.1ATC.1BD107AIN.PNT_5))

## UJPCT#2 (hidden)
NO | NO UNIT | NAME UNIT | NO SYSTEM | NAME SYSTEM | NO EQUIPMENT | NAME EQUIPMENT | DRAWING | TAG AT OPC | TAG AT DCS | KKS | DESCRIPTION | TYPE I/O | RANGE LO | RANGE HI | UNIT | ALARM LLL | ALARM LL | ALARM L | ALARM H | ALARM HH | ALARM HHH | SAMPLE VALUE | STATUS | REMARKS
1 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161405.PNT | 2MAI:AI161405.PNT | 20MAG10CL201 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 700.8984 | ok
2 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161501.PNT | 2MAI:AI161501.PNT | 20MAG10CL202 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 711.7969 | ok
3 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161601.PNT | 2MAI:AI161601.PNT | 20MAG10CL203 | CONDENSER LEVEL | AI | 0 | 1200 | mm |  | 200 | 425 | 975 | 1075 |  | 699.6797 | ok
4 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2NAI.AI172205.PNT | 2NAI:AI172205.PNT | 20PAH11GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM A SIDE DIFF.PRESS | AI | -1 | 9 | KPa | [6 empty] | 0.24824 | ok
5 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2NAI.AI172302.PNT | 2NAI:AI172302.PNT | 20PAH12GC001AI01 | CONDENSER RUBBER BALL CLEANING SYSTEM B SIDE DIFF.PRESS | AI | -1 | 9 | KPa | [6 empty] | 1.9637 | ok
6 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI212707.PNT | 2QAI:AI212707.PNT | 20PAH21CP201 | CONDENSER SIDE A CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.11901 | ok
7 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI210202.PNT | 2QAI:AI210202.PNT | 20PAH21CT001 | CONDENSER SIDE A CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.4862 | ok
8 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI213202.PNT | 2QAI:AI213202.PNT | 20PAH22CP201 | CONDENSER SIDE B CIRCULATING WATER INLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.086773 | ok
9 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI210301.PNT | 2QAI:AI210301.PNT | 20PAH22CT001 | CONDENSER SIDE B CIRCULATING WATER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.5772 | ok
10 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2NAI.AI172204.PNT | 2NAI:AI172204.PNT | 20PAH31AA001XB12 | CONDENSER A SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.1094 | ok
11 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI213201.PNT | 2QAI:AI213201.PNT | 20PAH31CP201 | CONDENSER SIDE A CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.14323 | ok
12 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI210203.PNT | 2QAI:AI210203.PNT | 20PAH31CT001 | CONDENSER SIDE A CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 39 | ok
13 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2NAI.AI172301.PNT | 2NAI:AI172301.PNT | 20PAH32AA001XB12 | CONDENSER B SIDE CIRCULATING WATER OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 71.4648 | ok
14 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI213107.PNT | 2QAI:AI213107.PNT | 20PAH32CP201 | CONDENSER SIDE B CIRCULATING WATER OUTLET PRESS | AI | 0 | 0.2 | MPa | [6 empty] | 0.012738 | ok
15 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-13 | OPC.AW2002.2QAI.AI210302.PNT | 2QAI:AI210302.PNT | 20PAH32CT001 | CONDENSER SIDE B CIRCULATING WATER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 33.4106 | ok
16 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 | F296S-J0201-15 | OPC.AW2002.2VALVE.VACUUM.PNT | 2VALVE:VACUUM.PNT | 20MAG10CP201 | CONDENSER VACUUM | AI | -100 | 150 | KPa |  |  |  | -85.3 | -80.3 |  | -91.1328 | ok
17 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2QAI.AI210101.PNT | 2QAI:AI210101.PNT | 20LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 200 | C | [6 empty] | 44.7515 | ok
18 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2QAI.AI212701.PNT | 2QAI:AI212701.PNT | 20LCA12CP201 | CONDENSATE PUMP A OUTLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 2.7513 | ok
19 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI173803.PNT | 2NAI:AI173803.PNT | 20LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa |  |  | 1.3 |  |  |  | 2.7473 | ok
20 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI173105.PNT | 2NAI:AI173105.PNT | 20LCB12AP001XB13 | CONDENSER PUMP A CURRENT | AI | 0 | 200 | A |  |  |  | 110.4 |  |  | -0.25 | no
21 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172507.PNT | 2NAI:AI172507.PNT | 20LCB12CT001 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 32.3843 | ok
22 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172603.PNT | 2NAI:AI172603.PNT | 20LCB12CT002 | CONDENSATE PUMP A THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 32.7221 | ok
23 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2OAI.AI192501.PNT | 2OAI:AI192501.PNT | 20LCB12CT003 | CONDENSATE PUMP A MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 32.7351 | ok
24 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2OAI.AI192502.PNT | 2OAI:AI192502.PNT | 20LCB12CT004 | CONDENSATE PUMP A MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 33.9562 | ok
25 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172604.PNT | 2NAI:AI172604.PNT | 20LCB12CT005 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 34.3329 | ok
26 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172701.PNT | 2NAI:AI172701.PNT | 20LCB12CT006 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 33.7613 | ok
27 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172605.PNT | 2NAI:AI172605.PNT | 20LCB12CT007 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 34.229 | ok
28 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172702.PNT | 2NAI:AI172702.PNT | 20LCB12CT008 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 33.7354 | ok
29 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172801.PNT | 2NAI:AI172801.PNT | 20LCB12CT009 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 33.8393 | ok
30 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2NAI.AI172606.PNT | 2NAI:AI172606.PNT | 20LCB12CT010 | CONDENSATE PUMP A MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 33.8653 | ok
31 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2QAI.AI213307.PNT | 2QAI:AI213307.PNT | 20LCB12CY201X | CONDENSATE PUMP A DRIVING END X DIRECTION VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0 | ok
32 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 2 | CEP #2A | F296S-J0201-07 | OPC.AW2002.2QAI.AI213401.PNT | 2QAI:AI213401.PNT | 20LCB12CY201Y | CONDENSATE PUMP A DRIVING END X DIRECTION VIBRATION Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.042188 | ok
33 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2QAI.AI213101.PNT | 2QAI:AI213101.PNT | 20LCA13CP201 | CONDENSATE PUMP B OUTLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 2.7499 | ok
34 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172202.PNT | 2NAI:AI172202.PNT | 20LCB13AP001XB13 | CONDENSER PUMP B CURRENT | AI | 0 | 200 | A |  |  |  | 110.4 |  |  | 95.0078 | ok
35 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172607.PNT | 2NAI:AI172607.PNT | 20LCB13CT001 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 50.0258 | ok
36 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172703.PNT | 2NAI:AI172703.PNT | 20LCB13CT002 | CONDENSATE PUMP B THRUST BEARING TEMPERATURE NO.2 | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 61.3667 | ok
37 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2PAI.AI202501.PNT | 2PAI:AI202501.PNT | 20LCB13CT003 | CONDENSATE PUMP B MOTOR UPPER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 45.8428 | ok
38 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2PAI.AI202502.PNT | 2PAI:AI202502.PNT | 20LCB13CT004 | CONDENSATE PUMP B MOTOR LOWER BEARING TEMPERATURE | RTD | 0 | 100 | C |  |  |  | 70 | 80 |  | 54.8194 | ok
39 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172704.PNT | 2NAI:AI172704.PNT | 20LCB13CT005 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 83.7888 | ok
40 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172802.PNT | 2NAI:AI172802.PNT | 20LCB13CT006 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE A NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 82.8405 | ok
41 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172705.PNT | 2NAI:AI172705.PNT | 20LCB13CT007 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 83.5679 | ok
42 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172803.PNT | 2NAI:AI172803.PNT | 20LCB13CT008 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 82.8535 | ok
43 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172706.PNT | 2NAI:AI172706.PNT | 20LCB13CT009 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.1 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 83.3341 | ok
44 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI172804.PNT | 2NAI:AI172804.PNT | 20LCB13CT010 | CONDENSATE PUMP B MOTOR STATOR WINDING TEMPERATURE C NO.2 | RTD | 0 | 150 | C |  |  |  | 130 | 140 |  | 82.8275 | ok
45 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2QAI.AI213302.PNT | 2QAI:AI213302.PNT | 20LCB13CY201X | CONDENSATE PUMP B DRIVING END X DIRECTION VIBRATION X | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.61289 | ok
46 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2QAI.AI213402.PNT | 2QAI:AI213402.PNT | 20LCB13CY201Y | CONDENSATE PUMP B DRIVING END X DIRECTION VIBRATION Y | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.55742 | ok
47 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2NAI.AI173107.PNT | 2NAI:AI173107.PNT | 20MAJ21AP001XB13 | VACUUM PUMP A CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | -0.33594 | no
48 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2NAI.AI173207.PNT | 2NAI:AI173207.PNT | 20MAJ21AP002XB13 | VACUUM PUMP A RECIRCULATING PUMP CURRENT | AI | 0 | 10 | A |  |  |  | 6.5 |  |  | 3.8859 | ok
49 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210204.PNT | 2QAI:AI210204.PNT | 20MAJ21CT001 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 36 | ok
50 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210303.PNT | 2QAI:AI210303.PNT | 20MAJ21CT002 | VACUUM PUMP A MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
51 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210205.PNT | 2QAI:AI210205.PNT | 20MAJ21CT003 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 32.2934 | ok
52 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210304.PNT | 2QAI:AI210304.PNT | 20MAJ21CT004 | VACUUM PUMP A MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
53 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210206.PNT | 2QAI:AI210206.PNT | 20MAJ21CT005 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 31.371 | ok
54 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210305.PNT | 2QAI:AI210305.PNT | 20MAJ21CT006 | VACUUM PUMP A MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
55 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210207.PNT | 2QAI:AI210207.PNT | 20MAJ21CT007 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 31.3191 | ok
56 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-15 | OPC.AW2002.2QAI.AI210306.PNT | 2QAI:AI210306.PNT | 20MAJ21CT008 | VACUUM PUMP A MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 30.8384 | ok
57 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 4 | AIR REMOVAL #2 - VACUUM PUMP A | F296S-J0201-14 | OPC.AW2002.2RAI.AI230201.PNT | 2RAI:AI230201.PNT | 20PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 26.2137 | ok
58 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210307.PNT | 2QAI:AI210307.PNT | 20MAJ21CT009 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 75.8644 | ok
59 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210401.PNT | 2QAI:AI210401.PNT | 20MAJ21CT010 | VACUUM PUMP B MOTOR STATOR COIL U TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
60 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210501.PNT | 2QAI:AI210501.PNT | 20MAJ21CT011 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 77.7091 | ok
61 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210402.PNT | 2QAI:AI210402.PNT | 20MAJ21CT012 | VACUUM PUMP B MOTOR STATOR COIL V TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
62 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210502.PNT | 2QAI:AI210502.PNT | 20MAJ21CT013 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 74.3315 | ok
63 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210403.PNT | 2QAI:AI210403.PNT | 20MAJ21CT014 | VACUUM PUMP B MOTOR STATOR COIL W TEMP 2 | RTD | 0 | 100 | C | [8 empty] | TIDAK DIPAKAI
64 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210503.PNT | 2QAI:AI210503.PNT | 20MAJ21CT015 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.1 | RTD | 0 | 200 | C |  |  |  | 140 | 150 |  | 41.8676 | ok
65 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2QAI.AI210404.PNT | 2QAI:AI210404.PNT | 20MAJ21CT016 | VACUUM PUMP B MOTOR BEARING THERMO-RESISTANCE TEMP NO.2 | RTD | 0 | 200 | C |  |  |  | 105 | 110 |  | 53.2605 | ok
66 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2NAI.AI172305.PNT | 2NAI:AI172305.PNT | 20MAJ22AP001XB13 | VACUUM PUMP B CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | 155.4609 | ok
67 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-15 | OPC.AW2002.2NAI.AI172306.PNT | 2NAI:AI172306.PNT | 20MAJ22AP002XB13 | VACUUM PUMP B RECIRCULATING PUMP CURRENT | AI | 0 | 10 | A |  |  |  | 6.5 |  |  | 4.4406 | ok
68 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2OAI.AI191303.PNT | 2OAI:AI191303.PNT | 20LBW20AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN A CURRENT | AI | 0 | 50 | A |  |  |  | 21.3 |  |  | -0.0048828 | no
69 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2PAI.AI202108.PNT | 2PAI:AI202108.PNT | 20LBW21AN001XB13 | GLAND STEAM CONDENSER EXTRACTION FAN B CURRENT | AI | 0 | 50 | A |  |  |  | 21.3 |  |  | 9.0029 | ok
70 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI160102.PNT | 2MAI:AI160102.PNT | 20LBW22CT001 | GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | RTD | 0 | 300 | C | [6 empty] | 156.7492 | ok
71 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI161301.PNT | 2MAI:AI161301.PNT | 20LBW24CP201 | GLAND MAIN PIPE PRESS | AI | 0 | 0.13 | MPa | [6 empty] | 0.071259 | ok
72 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2QAI.AI212205.PNT | 2QAI:AI212205.PNT | 20LBW24CT001 | GLAND MAIN PIPE TEMP(BEFORE TEMPERATURE REDUCING DEVICE) | TC | 0 | 600 | C | [6 empty] | 386.0581 | ok
73 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210102.PNT | 2QAI:AI210102.PNT | 20LCA10CT001 | GLAND STEAM CONDENSER INLET TEMP | RTD | 0 | 200 | C | [6 empty] | 46.2195 | ok
74 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210103.PNT | 2QAI:AI210103.PNT | 20LCA10CT002 | GLAND STEAM CONDENSER OUTLET MAIN PIPE TEMP | RTD | 0 | 200 | C | [6 empty] | 46.7002 | ok
75 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI213108.PNT | 2QAI:AI213108.PNT | 20LCE10CP201 | TEMP REDUCE MAIN MAIN PIPE PRESS | AI | 0 | 3 | MPa | [6 empty] | 1.9191 | ok
76 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 | F296S-J0201-10 | OPC.AW2002.2QAI.AI212706.PNT | 2QAI:AI212706.PNT | 20MAV80CP201 | GLAND STEAM CONDENSER INLET STEAM PRESS | AI | -100 | 600 | KPa | [6 empty] | -0.43633 | ok
77 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212605.PNT | 2QAI:AI212605.PNT | 20LBS80CP201 | #8 EXTRACTION STEAM PRESS(LEFT) | AI | -0.1 | 0.15 | MPa | [6 empty] | -0.016958 | ok
78 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212506.PNT | 2QAI:AI212506.PNT | 20LBS80CP202 | #8 EXTRACTION STEAM PRESS(RIGHT) | AI | -0.1 | 0.15 | MPa | [6 empty] | -0.016782 | ok
79 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211607.PNT | 2QAI:AI211607.PNT | 20LBS80CT001 | #8 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 95 | C | [8 empty] | TIDAK DIPAKAI
80 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211701.PNT | 2QAI:AI211701.PNT | 20LBS80CT002 | #8 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 95 | C | [8 empty] | TIDAK DIPAKAI
81 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI212702.PNT | 2QAI:AI212702.PNT | 20LCA10CP201 | #8 LP HEATER INLET PRESS | AI | 0 | 4 | MPa | [6 empty] | 0.80508 | ok
82 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210104.PNT | 2QAI:AI210104.PNT | 20LCA10CT003 | #8 LP HEATER INLET WATER TEMP | RTD | 0 | 200 | C | [6 empty] | 47.4796 | ok
83 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.232.RO01 | 2PMS:232.RO01 | 20LCA10CT003C1 | #7&8 LP TEMP RISE | RTD | -50 | 200 | C | [6 empty] | 53.5166 | ok
84 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.241.RO01 | 2PMS:241.RO01 | 20LCA10CT003C2 | #7&8 LP DIFF. TEMP | RTD | -50 | 200 | C | [6 empty] | -29.5005 | ok
85 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI160706.PNT | 2MAI:AI160706.PNT | 20LCC80CL201 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -55.2812 | ok
86 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP8LVL_1.SIGSEL1OUT.PNT | 2M_LP8LVL_1:SIGSEL1OUT.PNT | 20LCC80CL201C1 | #8 LP HEATER LEVEL SIGSEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -19.7705 | ok
87 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161106.PNT | 2MAI:AI161106.PNT | 20LCC80CL202 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -4.7627 | ok
88 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161206.PNT | 2MAI:AI161206.PNT | 20LCC80CL203 | #8 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -19.8369 | ok
89 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP8LVL.AO163201.OUT | 2M_LP8LVL:AO163201.OUT | 20LCJ80AA101XB11 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 35.8777 | ok
90 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162203.PNT | 2MAI:AI162203.PNT | 20LCJ80AA101XB12 | #8 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 34.8906 | ok
91 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2QAI.AI211707.PNT | 2QAI:AI211707.PNT | 20LCJ80CT001 | #8 LP HEATER DRAIN WATER TEMP | TC | 0 | 300 | C | [6 empty] | 51.1038 | ok
92 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP8LVL.AO163202.OUT | 2M_LP8LVL:AO163202.OUT | 20LCJ81AA101XB11 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0.12397 | ok
93 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162204.PNT | 2MAI:AI162204.PNT | 20LCJ81AA101XB12 | #8 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -1.0176 | no
94 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212604.PNT | 2QAI:AI212604.PNT | 20LBS70CP201 | #7 EXTRACTION STEAM PRESS(LEFT) | AI | -0.1 | 0.15 | MPa | [6 empty] | 0.043301 | ok
95 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212505.PNT | 2QAI:AI212505.PNT | 20LBS70CP202 | #7 EXTRACTION STEAM PRESS(RIGHT) | AI | -0.1 | 0.15 | MPa | [6 empty] | 0.043926 | ok
96 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211606.PNT | 2QAI:AI211606.PNT | 20LBS70CT001 | #7 EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 140 | C | [8 empty] | TIDAK DIPAKAI
97 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211507.PNT | 2QAI:AI211507.PNT | 20LBS70CT002 | #7 EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 140 | C | [8 empty] | TIDAK DIPAKAI
98 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210105.PNT | 2QAI:AI210105.PNT | 20LCA20CT001 | #7 LP HEATER OUTLET WATER TEMP | RTD | 0 | 120 | C | [6 empty] | 100.9962 | ok
99 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI160705.PNT | 2MAI:AI160705.PNT | 20LCC70CL201 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -12.4492 | ok
100 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP7LVL_1.SIGSEL1OUT.PNT | 2M_LP7LVL_1:SIGSEL1OUT.PNT | 20LCC70CL201C1 | #7 LP HEATER LEVEL SIGSEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -23.29 | ok
101 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161105.PNT | 2MAI:AI161105.PNT | 20LCC70CL202 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -22.8916 | ok
102 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161205.PNT | 2MAI:AI161205.PNT | 20LCC70CL203 | #7 LP HEATER LEVEL | AI | -450 | 400 | mm |  | -90 | -50 | 50 | 90 | 130 | -44.8555 | ok
103 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP7LVL.AO162707.OUT | 2M_LP7LVL:AO162707.OUT | 20LCJ70AA101XB11 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 28.3062 | ok
104 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162201.PNT | 2MAI:AI162201.PNT | 20LCJ70AA101XB12 | #7 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 33.9551 | ok
105 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2QAI.AI212106.PNT | 2QAI:AI212106.PNT | 20LCJ70CT001 | #7 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 82.515 | ok
106 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP7LVL.AO163105.OUT | 2M_LP7LVL:AO163105.OUT | 20LCJ71AA101XB11 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
107 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162202.PNT | 2MAI:AI162202.PNT | 20LCJ71AA101XB12 | #7 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.94531 | ok
108 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212603.PNT | 2QAI:AI212603.PNT | 20LBS60CP201 | #6 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.4 | MPa | [6 empty] | 0.10363 | ok
109 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212504.PNT | 2QAI:AI212504.PNT | 20LBS60CP202 | #6 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.4 | MPa | [6 empty] | 0.10496 | ok
110 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211604.PNT | 2QAI:AI211604.PNT | 20LBS60CT001 | #6 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 237.8235 | ok
111 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211605.PNT | 2QAI:AI211605.PNT | 20LBS60CT002 | #6 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 146.7714 | ok
112 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211506.PNT | 2QAI:AI211506.PNT | 20LBS60CT003 | #6 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 212.9419 | ok
113 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211505.PNT | 2QAI:AI211505.PNT | 20LBS60CT004 | #6 EXTRACTION STEAM TEMP (LP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 236.3651 | ok
114 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210106.PNT | 2QAI:AI210106.PNT | 20LCA30CT001 | #6 LP HEATER OUTLET WATER TEMP | RTD | 0 | 160 | C | [6 empty] | 120.4977 | ok
115 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.240.RO01 | 2PMS:240.RO01 | 20LCA30CT001C1 | #6 LP DIFF. TEMP | RTD | -50 | 160 | C | [6 empty] | -19.8584 | ok
116 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.231.RO01 | 2PMS:231.RO01 | 20LCA30CT001C2 | #6 LP TEMP RISE | RTD | -50 | 160 | C | [6 empty] | 19.5016 | ok
117 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI160704.PNT | 2MAI:AI160704.PNT | 20LCC60CL201 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -25.8516 | ok
118 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP6LVL_1.SIGSEL1OUT.PNT | 2M_LP6LVL_1:SIGSEL1OUT.PNT | 20LCC60CL201C1 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -19.8984 | ok
119 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161104.PNT | 2MAI:AI161104.PNT | 20LCC60CL202 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -19.875 | ok
120 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161204.PNT | 2MAI:AI161204.PNT | 20LCC60CL203 | #6 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -12.1172 | ok
121 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP6LVL.AO162706.OUT | 2M_LP6LVL:AO162706.OUT | 20LCJ60AA101XB11 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 61.2447 | ok
122 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162106.PNT | 2MAI:AI162106.PNT | 20LCJ60AA101XB12 | #6 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 61.8672 | ok
123 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2QAI.AI211706.PNT | 2QAI:AI211706.PNT | 20LCJ60CT001 | #6 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 104.4394 | ok
124 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP6LVL.AO163104.OUT | 2M_LP6LVL:AO163104.PNT | 20LCJ61AA101XB11 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok | REVISI TAG
125 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162107.PNT | 2MAI:AI162107.PNT | 20LCJ61AA101XB12 | #6 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok | OUT OFF RANGE
126 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212602.PNT | 2QAI:AI212602.PNT | 20LBS50CP201 | #5 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 0.6 | MPa | [6 empty] | 0.26115 | ok
127 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212503.PNT | 2QAI:AI212503.PNT | 20LBS50CP202 | #5 EXTRACTION STEAM PRESS (LP HEATER SIDE) | AI | 0 | 0.6 | MPa | [6 empty] | 0.26321 | ok
128 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211602.PNT | 2QAI:AI211602.PNT | 20LBS50CT001 | #5 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 300.8013 | ok
129 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211603.PNT | 2QAI:AI211603.PNT | 20LBS50CT002 | #5 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 160.5644 | ok
130 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211504.PNT | 2QAI:AI211504.PNT | 20LBS50CT003 | #5 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 270.9095 | ok
131 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211503.PNT | 2QAI:AI211503.PNT | 20LBS50CT004 | #5 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 298.066 | ok
132 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210107.PNT | 2QAI:AI210107.PNT | 20LCA40CT001 | #5 LP HEATER OUTLET WATER TEMP | RTD | 0 | 160 | C | [6 empty] | 130.1993 | ok
133 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.239.RO01 | 2PMS:239.RO01 | 20LCA40CT001C1 | #5 LP DIFF. TEMP | RTD | -50 | 160 | C | [6 empty] | -0.87741 | ok
134 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-07 | OPC.AW2002.2PMS.230.RO01 | 2PMS:230.RO01 | 20LCA40CT001C2 | #5 LP TEMP RISE | RTD | -50 | 160 | C | [6 empty] | 9.7016 | ok
135 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI160703.PNT | 2MAI:AI160703.PNT | 20LCC50CL201 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -25.5352 | ok
136 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP5LVL_1.SIGSEL1OUT.PNT | 2M_LP5LVL_1:SIGSEL1OUT.PNT | 20LCC50CL201C1 | #5 LP HEATER LEVEL SIGSEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -22.5938 | ok
137 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161103.PNT | 2MAI:AI161103.PNT | 20LCC50CL202 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -22.7227 | ok
138 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161203.PNT | 2MAI:AI161203.PNT | 20LCC50CL203 | #5 LP HEATER LEVEL | AI | -420 | 180 | mm |  | -80 | -40 | 40 | 80 | 120 | -21.0117 | ok
139 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP5LVL.AO162705.OUT | 2M_LP5LVL:AO162705.OUT | 20LCJ50AA101XB11 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 40.0604 | ok
140 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI161707.PNT | 2MAI:AI161707.PNT | 20LCJ50AA101XB12 | #5 LP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 38.5 | ok
141 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2QAI.AI212105.PNT | 2QAI:AI212105.PNT | 20LCJ50CT001 | #5 LP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 119.8467 | ok
142 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2M_LP5LVL.AO163103.OUT | 2M_LP5LVL:AO163103.OUT | 20LCJ51AA101XB11 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
143 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 | F296S-J0201-09(2/2) | OPC.AW2002.2MAI.AI162105.PNT | 2MAI:AI162105.PNT | 20LCJ51AA101XB12 | #5 LP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.94336 | ok
144 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-09(1/2) | OPC.AW2002.2NAI.AI172203.PNT | 2NAI:AI172203.PNT | 20LAA40AA501XB12 | DEARATOR EXHAUST MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 5.8066 | ok
145 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-09(1/2) | OPC.AW2002.2NAI.AI172107.PNT | 2NAI:AI172107.PNT | 20LAA40AA502XB12 | DEARATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 62.4629 | ok
146 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-09(1/2) | OPC.AW2002.2NAI.AI172108.PNT | 2NAI:AI172108.PNT | 20LAA40AA503XB12 | DEARATOR EXHAUST MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 5.5488 | ok
147 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI160405.PNT | 2MAI:AI160405.PNT | 20LAA40CL201 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2445.1956 | ok
148 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI160505.PNT | 2MAI:AI160505.PNT | 20LAA40CL202 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2450.3062 | ok
149 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI160605.PNT | 2MAI:AI160605.PNT | 20LAA40CL203 | DEARATOR TANK LEVEL | AI | 0 | 2940 | mm |  | 1300 | 2250 | 2650 | 2750 |  | 2445.655 | ok
150 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI210201.PNT | 2QAI:AI210201.PNT | 20LAA40CT001 | DEARATOR TANK TEMP | RTD | 0 | 500 | C | [6 empty] | 150.4847 | ok
151 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-06 | OPC.AW2002.2M_DAPRESS.AO162402.OUT | 2M_DAPRESS:AO162402.OUT | 20LBG17AA101XB11 | AUXILIARY HEADER TO DEARATOR SUPPLY STEAM CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
152 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-06 | OPC.AW2002.2MAI.AI161402.PNT | 2MAI:AI161402.PNT | 20LBG17AA101XB12 | AUXILIARY HEADER TO DEARATOR SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.38672 | ok
153 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI172105.PNT | 2NAI:AI172105.PNT | 20LBS40AA005XB12 | AUXILIARY STEAM HEADER TO DEARATOR INCHING MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 11.8652 | ok
154 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI173801.PNT | 2NAI:AI173801.PNT | 20LBS40CP201 | #4 EXTRACTION STEAM PIPE 1 PRESS 1 (TURBINE SIDE) | AI | 0 | 1 | MPa | [6 empty] | 0.5373 | ok
155 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI173802.PNT | 2NAI:AI173802.PNT | 20LBS40CP202 | #4 EXTRACTION STEAM PIPE 1 PRESS 2 (TURBINE SIDE) | AI | 0 | 1 | MPa | [6 empty] | 0.5374 | ok
156 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2MAI.AI160403.PNT | 2MAI:AI160403.PNT | 20LBS40CP203 | DEARATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.40018 | ok
157 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2MAI.AI160503.PNT | 2MAI:AI160503.PNT | 20LBS40CP204 | DEARATOR STEAM SIDE PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.40869 | ok
158 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211305.PNT | 2QAI:AI211305.PNT | 20LBS40CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 600 | C | [6 empty] | 340.8848 | ok
159 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211306.PNT | 2QAI:AI211306.PNT | 20LBS40CT002 | #4 EXTRACTION STEAM PIPE 1 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 298.9997 | ok
160 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211406.PNT | 2QAI:AI211406.PNT | 20LBS40CT003 | #4 EXTRACTION STEAM PIPE 1 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 287.6068 | ok
161 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211501.PNT | 2QAI:AI211501.PNT | 20LBS40CT004 | #4 EXTRACTION STEAM PIPE TEMP (DEAERATOR SIDE) | TC | 0 | 600 | C | [6 empty] | 356.1638 | ok
162 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI172106.PNT | 2NAI:AI172106.PNT | 20LBS43AA001XB12 | OPEN #4 EXTRACTION STEAM PIPE TO DEARATOR INCHING MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 14.1602 | ok
163 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173103.PNT | 2NAI:AI173103.PNT | 20LCA10AA004XB12 | DEARATOR LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.11133 | no
164 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2M_DALVL.AO162406.OUT | 2M_DALVL:AO162406.OUT | 20LCA10AA101XB11 | DEARATOR WATER LEVEL CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 12.6299 | ok
165 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161407.PNT | 2MAI:AI161407.PNT | 20LCA10AA101XB12 | DEARATOR WATER LEVEL CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 13.1836 | ok
166 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2M_DALVL.AO162501.OUT | 2M_DALVL:AO162501.OUT | 20LCA10AA102XB11 | DEARATOR WATER LEVEL CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
167 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 16 | DEAERATOR #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161502.PNT | 2MAI:AI161502.PNT | 20LCA10AA102XB12 | DEARATOR WATER LEVEL CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 0.14844 | ok
168 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_FLOW.COND1OUT.PNT | 2M_FLOW:COND1OUT.PNT | 20LCA40CF201 | CONDENSATE WATER FLOW | AI | 0 | 1000 | t/h | [6 empty] | 520.1591 | ok
169 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_FLOW.COND2OUT.PNT | 2M_FLOW:COND2OUT.PNT | 20LCA40CF202 | CONDENSATE WATER FLOW | AI | 0 | 1000 | t/h | [6 empty] | 518.1088 | ok
170 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173102.PNT | 2NAI:AI173102.PNT | 20LCA42AA001XB12 | OPEN CONDENSATE RECIRCULATING CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.25586 | no
171 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_CNREC.AO162405.OUT | 2M_CNREC:AO162405.OUT | 20LCA42AA101XB11 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
172 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_CNREC.ZT161602.PNT | 2M_CNREC:ZT161602.PNT | 20LCA42AA101XB12 | CONDENSATE RECIRCULATING FLOW CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 77.2129 | ok
173 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 17 | CONDENSATE PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_FLOW.CNRAIN.PNT | 2M_FLOW:CNRAIN.PNT | 20LCA42CF201 | CONDENSATE WATER RECIRCULATING FLOW | AI | 0 | 1000 | t/h | [6 empty] | 834.9119 | ok
174 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2M_CNMKUP.AO162408.OUT | 2M_CNMKUP:AO162408.OUT | 20LCA21AA101XB91 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
175 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173101.PNT | 2NAI:AI173101.PNT | 20LCA21AA101XB92C1 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.41016 | no | REVISI TAG
176 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173101.PNT | 2NAI:AI173101.PNT | 20LCA21AA101XB92 | CONDENSATE RETURN MAKE-UP WATER TANK MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.41016 | no
177 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2M_CNMKUP.AO162506.OUT | 2M_CNMKUP:AO162506.OUT | 20LCD10AA101XB11 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 3.4541 | ok
178 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161604.PNT | 2MAI:AI161604.PNT | 20LCD10AA101XB12 | CONDENSATE MAKE-UP WATER TANK INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 2.7363 | ok
179 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2M_CNLVL.AO162507.OUT | 2M_CNLVL:AO162507.OUT | 20LCP10AA101XB11 | CONDENSER WATER LEVEL CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
180 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161605.PNT | 2MAI:AI161605.PNT | 20LCP10AA101XB12 | CONDENSER WATER LEVEL CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.10938 | no
181 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173108.PNT | 2NAI:AI173108.PNT | 20LCP10AP001XB13 | CONDENSATE MAKE-UP WATER PUMP CURRENT | AI | 0 | 100 | A | [6 empty] | -0.038281 | no
182 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2Q_FLOW.CNMAKEAIN.PNT | 2Q_FLOW:CNMAKEAIN.PNT | 20LCP10CF201 | CONDENSATE MAKE-UP WATER FLOW | AI | 0 | 80 | t/h | [6 empty] | 0 | ok
183 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161406.PNT | 2MAI:AI161406.PNT | 20LCP10CL201 | CONDENSATE MAKE-UP TANK LEVEL | AI | 0 | 4500 | mm |  | 500 | 800 | 3200 | 3400 |  | 2799.0527 | ok
184 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2QAI.AI213102.PNT | 2QAI:AI213102.PNT | 20LCP10CP201 | CONDENSATE MAKE-UP WATER PUMP OUTLET PRESS | AI | 0 | 0.8 | MPa | [6 empty] | 0.04175 | ok
185 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173104.PNT | 2NAI:AI173104.PNT | 20LCP11AA001XB12 | CONDENSER WATER LEVEL CONTROL VALVE BYPASS MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.0019531 | ok
186 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 18 | CONDENSATE MAKE-UP SYSYEM #2 | F296S-J0201-07 | OPC.AW2002.2NAI.AI173106.PNT | 2NAI:AI173106.PNT | 20LCP20AP001XB13 | BOILER STARTUP FEEDWATER PUMP CURRENT | AI | 0 | 200 | A | [6 empty] | -0.10156 | no
187 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 19 | PRIMING PUMP #2 | F296S-J0201-15 | OPC.AW2002.2NAI.AI173208.PNT | 2NAI:AI173208.PNT | 20MAJ30AP001XB13 | CONDENSER WATER BOX VACUUM PUMP CURRENT | AI | 0 | 25 | A |  |  |  | 15.6 |  |  | -0.022949 | no
188 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230601.PNT | 2RAI:AI230601.PNT | 20LCT10CT001 | NO.1 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 45.19 | ok
189 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230701.PNT | 2RAI:AI230701.PNT | 20LCT10CT002 | NO.2 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 45.356 | ok
190 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230602.PNT | 2RAI:AI230602.PNT | 20LCT10CT003 | NO.3 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 285.1991 | ok
191 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230702.PNT | 2RAI:AI230702.PNT | 20LCT10CT004 | NO.4 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 45.3863 | ok
192 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230603.PNT | 2RAI:AI230603.PNT | 20LCT10CT005 | NO.5 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 193.6339 | ok
193 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230703.PNT | 2RAI:AI230703.PNT | 20LCT10CT006 | NO.6 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 600 | C | [6 empty] | 48.23 | ok
194 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 20 | DRAIN FLASH TANK 1 #2 | F296S-J0201-12 | OPC.AW2002.2RAI.AI230604.PNT | 2RAI:AI230604.PNT | 20LCT10CT007 | NO.7 MANIFOLD OF CONDENSER DRAIN TEMP | TC | 0 | 180 | C | [6 empty] | 70.3905 | ok
195 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173804.PNT | 2NAI:AI173804.PNT | 20PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.4 | MPa | [6 empty] | 0.074227 | ok
196 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2RAI.AI230101.PNT | 2RAI:AI230101.PNT | 20PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.4862 | ok
197 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172406.PNT | 2NAI:AI172406.PNT | 20PCC21AP001XB13 | CIRCULATING-WATER BOOSTER PUMP A CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | 0.023438 | ok
198 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI171103.PNT | 2NAI:AI171103.PNT | 20PCC21CT001 | CIRCULATING WATER BOOSTER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 25 | ok
199 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173402.PNT | 2NAI:AI173402.PNT | 20PCC21CT002 | CIRCULATING WATER BOOSTER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 27.0321 | ok
200 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI171104.PNT | 2NAI:AI171104.PNT | 20PCC21CT003 | CIRCULATING WATER BOOSTER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
201 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173403.PNT | 2NAI:AI173403.PNT | 20PCC21CT004 | CLOSED CIRCULATING WATER BOOSTER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
202 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI171105.PNT | 2NAI:AI171105.PNT | 20PCC21CT005 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.1 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
203 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173404.PNT | 2NAI:AI173404.PNT | 20PCC21CT006 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.2 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
204 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI171106.PNT | 2NAI:AI171106.PNT | 20PCC21CT007 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.3 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
205 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173405.PNT | 2NAI:AI173405.PNT | 20PCC21CT008 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.4 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
206 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI171107.PNT | 2NAI:AI171107.PNT | 20PCC21CT009 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.5 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
207 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173406.PNT | 2NAI:AI173406.PNT | 20PCC21CT010 | CIRCULATING WATER BOOSTER PUMP A MOTOR STATOR COIL TEMPERATURE NO.6 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
208 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI172303.PNT | 2NAI:AI172303.PNT | 20PCC22AP001XB13 | CIRCULATING-WATER BOOSTER PUMP B CURRENT | AI | 0 | 400 | A |  |  |  | 226 |  |  | 0.28711 | ok
209 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173407.PNT | 2NAI:AI173407.PNT | 20PCC22CT001 | CIRCULATING WATER BOOSTER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 27 | ok
210 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173408.PNT | 2NAI:AI173408.PNT | 20PCC22CT002 | CIRCULATING WATER BOOSTER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 75 | 85 |  | 30 | ok
211 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173301.PNT | 2NAI:AI173301.PNT | 20PCC22CT003 | CIRCULATING WATER BOOSTER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
212 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173302.PNT | 2NAI:AI173302.PNT | 20PCC22CT004 | CLOSED CIRCULATING WATER BOOSTER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  |  |  | TIDAK DIPAKAI
213 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173303.PNT | 2NAI:AI173303.PNT | 20PCC22CT005 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.1 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
214 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173304.PNT | 2NAI:AI173304.PNT | 20PCC22CT006 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.2 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
215 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173305.PNT | 2NAI:AI173305.PNT | 20PCC22CT007 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.3 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
216 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173306.PNT | 2NAI:AI173306.PNT | 20PCC22CT008 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.4 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
217 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173307.PNT | 2NAI:AI173307.PNT | 20PCC22CT009 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.5 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
218 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173308.PNT | 2NAI:AI173308.PNT | 20PCC22CT010 | CIRCULATING WATER BOOSTER PUMP B MOTOR STATOR COIL TEMPERATURE NO.6 | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
219 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CWHE #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173201.PNT | 2NAI:AI173201.PNT | 20PCB31AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A SEA WATER SIDE OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 96.7617 | ok
220 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CWHE #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173205.PNT | 2NAI:AI173205.PNT | 20PGA21AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER A COOLING WATER INLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.2402 | ok
221 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CWHE #2A | F296S-J0201-14 | OPC.AW2002.2RAI.AI231101.PNT | 2RAI:AI231101.PNT | 20PGA21CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.49303 | ok
222 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 3 | CWHE #2A | F296S-J0201-14 | OPC.AW2002.2RAI.AI230102.PNT | 2RAI:AI230102.PNT | 20PGA21CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER A OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 29.7472 | ok
223 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CWHE #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173202.PNT | 2NAI:AI173202.PNT | 20PCB32AA002XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B SEA WATER SIDE OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 69.8242 | ok
224 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CWHE #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173206.PNT | 2NAI:AI173206.PNT | 20PGA22AA001XB12 | CLOSED CIRCUIT COOLING WATER HEAT EXCHANGER B COOLING WATER INLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -1.1328 | no
225 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CWHE #2B | F296S-J0201-14 | OPC.AW2002.2RAI.AI231201.PNT | 2RAI:AI231201.PNT | 20PGA22CP201 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.484 | ok
226 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 4 | CWHE #2B | F296S-J0201-14 | OPC.AW2002.2RAI.AI230202.PNT | 2RAI:AI230202.PNT | 20PGA22CT001 | CLOSED CIRCIIT COOLING WATER HEAT EXCHANGER B OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 29.6822 | ok
227 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173203.PNT | 2NAI:AI173203.PNT | 20PGA11AA001XB12 | CLOSED CIRCULATING-WATER PUMP A OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 93.0664 | ok
228 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172407.PNT | 2NAI:AI172407.PNT | 20PGA11AP001XB13 | CLOSED CIRCULATING-WATER PUMP A CURRENT | AI | 0 | 200 | A |  |  |  | 32.5 |  |  | -0.03125 | no
229 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172707.PNT | 2NAI:AI172707.PNT | 20PGA11CT001 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 1 | RTD | 0 | 100 | C |  |  |  | 75 | 85 |  | 26.9282 | ok
230 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172805.PNT | 2NAI:AI172805.PNT | 20PGA11CT002 | CLOSED CIRCULATING WATER PUMP A THRUST BEARING TEMPERATURE 2 | RTD | 0 | 100 | C |  |  |  | 75 | 85 |  | 27.6817 | ok
231 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172806.PNT | 2NAI:AI172806.PNT | 20PGA11CT003 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 100 | C |  |  |  | 90 | 95 |  | 27.6297 | ok
232 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170101.PNT | 2NAI:AI170101.PNT | 20PGA11CT004 | CLOSED CIRCULATING WATER PUMP A MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 28.5261 | ok
233 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170102.PNT | 2NAI:AI170102.PNT | 20PGA11CT005 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.7862 | ok
234 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170201.PNT | 2NAI:AI170201.PNT | 20PGA11CT006 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL U TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.7082 | ok
235 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170103.PNT | 2NAI:AI170103.PNT | 20PGA11CT007 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.5653 | ok
236 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170202.PNT | 2NAI:AI170202.PNT | 20PGA11CT008 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL V TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 29.1106 | ok
237 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170104.PNT | 2NAI:AI170104.PNT | 20PGA11CT009 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 30.1499 | ok
238 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI170203.PNT | 2NAI:AI170203.PNT | 20PGA11CT010 | CLOSED CIRCULATING WATER PUMP A MOTOR STATOR COIL W TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 28.6819 | ok
239 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 5 | CCWP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI173805.PNT | 2NAI:AI173805.PNT | 20PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 0.8 | MPa |  |  | 0.5 |  |  |  | 0.54278 | ok
240 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173204.PNT | 2NAI:AI173204.PNT | 20PGA12AA001XB12 | CLOSED CIRCULATING-WATER PUMP B OUTLET MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 87.748 | ok
241 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI172304.PNT | 2NAI:AI172304.PNT | 20PGA12AP001XB13 | CLOSED CIRCULATING-WATER PUMP B CURRENT | AI | 0 | 200 | A |  |  |  | 32.5 |  |  | 29.7383 | ok
242 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170105.PNT | 2NAI:AI170105.PNT | 20PGA12CT001 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 1 | RTD | 0 | 150 | C |  |  |  | 80 | 85 |  | 31.449 | ok
243 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170204.PNT | 2NAI:AI170204.PNT | 20PGA12CT002 | CLOSED CIRCULATING WATER PUMP B THRUST BEARING TEMPERATURE 2 | RTD | 0 | 150 | C |  |  |  | 80 | 85 |  | 29.6563 | ok
244 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170106.PNT | 2NAI:AI170106.PNT | 20PGA12CT003 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 42.5821 | ok
245 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170205.PNT | 2NAI:AI170205.PNT | 20PGA12CT004 | CLOSED CIRCULATING WATER PUMP B MOTOR BEARING TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 90 | 95 |  | 36.3075 | ok
246 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170107.PNT | 2NAI:AI170107.PNT | 20PGA12CT005 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 74.9811 | ok
247 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170206.PNT | 2NAI:AI170206.PNT | 20PGA12CT006 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL U TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 75.007 | ok
248 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI170207.PNT | 2NAI:AI170207.PNT | 20PGA12CT007 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 76.475 | ok
249 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI171101.PNT | 2NAI:AI171101.PNT | 20PGA12CT008 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL V TEMPERATURE B NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 75.4227 | ok
250 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI171102.PNT | 2NAI:AI171102.PNT | 20PGA12CT009 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE NO.1 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 74.6303 | ok
251 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173401.PNT | 2NAI:AI173401.PNT | 20PGA12CT010 | CLOSED CIRCULATING WATER PUMP B MOTOR STATOR COIL W TEMPERATURE NO.2 | RTD | 0 | 150 | C |  |  |  | 125 | 130 |  | 75.9294 | ok
252 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2NAI.AI172402.PNT | 2NAI:AI172402.PNT | 20PGA31AA002XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 97.6895 | ok
253 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI231202.PNT | 2RAI:AI231202.PNT | 20PGA31CP201 | TURBINE HOUSE COOLING WATER INLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.47402 | ok
254 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230204.PNT | 2RAI:AI230204.PNT | 20PGA31CT001 | TURBINE HOUSE COOLING WATER INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 30.1499 | ok
255 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230105.PNT | 2RAI:AI230105.PNT | 20PGA31CT002 | TURBINE HOUSER COOLING RETURN WATER TEMP 1 | RTD | 0 | 50 | C | [6 empty] | 29.8901 | ok
256 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230106.PNT | 2RAI:AI230106.PNT | 20PGA31CT004 | TURBINE HOUSER COOLING RETURN WATER TEMP 2 | RTD | 0 | 50 | C | [6 empty] | 30.3967 | ok
257 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2NAI.AI172405.PNT | 2NAI:AI172405.PNT | 20PGA33AA001XB12 | TURBINE HOUSE COOLING RETURN WATER MOTORIZED VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 89.6055 | ok
258 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI231102.PNT | 2RAI:AI231102.PNT | 20PGA40CP201 | BOILER HOUSE COOLING WATER MAIN PIPE INLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.34133 | ok
259 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230103.PNT | 2RAI:AI230103.PNT | 20PGA40CT001 | BOILER HOUSE COOLING WATER MAIN PIPE INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 29.7602 | ok
260 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2NAI.AI172401.PNT | 2NAI:AI172401.PNT | 20PGA50AA001XB12 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.4121 | ok
261 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230203.PNT | 2RAI:AI230203.PNT | 20PGA50CT001 | BOILER HOUSE COOLING RENTURN WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 31.2152 | ok
262 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230104.PNT | 2RAI:AI230104.PNT | 20PGA50CT002 | BOILER HOUSE COOLING RETURN WATER MAIN PIPE TEMP | RTD | 0 | 50 | C | [6 empty] | 30.7865 | ok
263 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | F296S-J0201-07 | OPC.AW2002.2M_CWEXTNK.AO162505.OUT | 2M_CWEXTNK:AO162505.OUT | 20LCE18AA101XB11 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAN | AO | 0 | 100 | % | [6 empty] | 0 | ok
264 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161507.PNT | 2MAI:AI161507.PNT | 20LCE18AA101XB12 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.88281 | ok
265 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 8 | CW EXPANSION TANK #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI231401.PNT | 2RAI:AI231401.PNT | 20PGA10CL201 | CLOSED CIRCUIT COOLING WATER EXPANSION TANK LEVEL | AI | 0 | 2500 | mm |  | 540 | 940 | 1600 | 1800 |  | 1595.9961 | ok
266 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #2A - BOOSTER PUMP | F296S-J0201-08 | OPC.AW2002.2OAI.AI192102.PNT | 2OAI:AI192102.PNT | 20LAC11AP001XB13 | BOOSTER PUMP FOR T-BFP A CURRENT | AI | 0 | 400 | A |  |  |  | 237 |  |  | 159.2656 | ok
267 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #2A - BOOSTER PUMP | F296S-J0201-31 | OPC.AW2002.2OAI.AI193106.PNT | 2OAI:AI193106.PNT | 20LAC11CT001 | BOOSTER PUMP FOR T-BFP A DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 46.3364 | ok
268 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 1 | T-BFP #2A - BOOSTER PUMP | F296S-J0201-31 | OPC.AW2002.2OAI.AI193107.PNT | 2OAI:AI193107.PNT | 20LAC11CT002 | BOOSTER PUMP FOR T-BFP A FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 47.2847 | ok
269 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-08 | OPC.AW2002.2M_TFPAREC.AO162603.OUT | 2M_TFPAREC:AO162603.OUT | 20LAB11AA101XB11 | T-BFP A MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
270 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-08 | OPC.AW2002.2MAI.AI161607.PNT | 2MAI:AI161607.PNT | 20LAB11AA101XB12 | T-BFP A MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.16406 | no
271 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-08 | OPC.AW2002.2M_FLOW.BFPAAIN.PNT | 2M_FLOW:BFPAAIN.PNT | 20LAB11CF201 | T-BFP A INLET WATER FLOW | AI | 0 | 800 | t/h |  | 120 | 140 |  |  |  | 380.1953 | ok
272 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-08 | OPC.AW2002.2OAI.AI193502.PNT | 2OAI:AI193502.PNT | 20LAB11CP201 | T-BFP A INLET WATER PRESS | AI | 0 | 2 | MPa |  | 1.25 | 1.4 |  |  |  | 1.1274 | ok
273 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-08 | OPC.AW2002.2QAI.AI212704.PNT | 2QAI:AI212704.PNT | 20LAB11CP202 | T-BFP A OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.5879 | ok
274 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193204.PNT | 2OAI:AI193204.PNT | 20LAC11CT003 | T-BFP A INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 57.0018 | ok
275 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193205.PNT | 2OAI:AI193205.PNT | 20LAC11CT004 | T-BFP A OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 58.9115 | ok
276 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193206.PNT | 2OAI:AI193206.PNT | 20LAC11CT005 | T-BFP A THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 65.7316 | ok
277 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193207.PNT | 2OAI:AI193207.PNT | 20LAC11CT006 | T-BFP A THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 48.7397 | ok
278 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193301.PNT | 2OAI:AI193301.PNT | 20LAC11CT007 | T-BFP A INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 38.8148 | ok
279 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193302.PNT | 2OAI:AI193302.PNT | 20LAC11CT008 | T-BFP A OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 57.5474 | ok
280 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193303.PNT | 2OAI:AI193303.PNT | 20LAC11CT009 | T-BFP A WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 134.603 | ok
281 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193304.PNT | 2OAI:AI193304.PNT | 20LAC11CT010 | T-BFP A WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 136.9405 | ok
282 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193305.PNT | 2OAI:AI193305.PNT | 20LAC11CT011 | T-BFP A WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 141.5086 | ok
283 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-31 | OPC.AW2002.2OAI.AI193306.PNT | 2OAI:AI193306.PNT | 20LAC11CT012 | T-BFP A WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 138.6502 | ok
284 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2RAI.AI231601.PNT | 2RAI:AI231601.PNT | 20LAC11CY201X | T-BFP A WATER INLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
285 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2RAI.AI231701.PNT | 2RAI:AI231701.PNT | 20LAC11CY202Y | T-BFP A WATER INLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
286 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2RAI.AI231602.PNT | 2RAI:AI231602.PNT | 20LAC11CY203X | T-BFP A WATER OUTLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
287 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2RAI.AI231702.PNT | 2RAI:AI231702.PNT | 20LAC11CY204Y | T-BFP A WATER OUTLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
288 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-04 | OPC.AW2002.2Q_FLOW.BFPSTMAIN.PNT | 2Q_FLOW:BFPSTMAIN.PNT | 20LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | t/h | [6 empty] | -0.1191 | no
289 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2Q_FLOW.BFPSTMAAIN.PNT | 2Q_FLOW:BFPSTMAAIN.PNT | 20LBR21CF201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30 | t/h | [6 empty] | 10.1253 | ok
290 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI212407.PNT | 2QAI:AI212407.PNT | 20LBR21CP201 | BFP TURBINE A INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.53082 | ok
291 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI211601.PNT | 2QAI:AI211601.PNT | 20LBR21CT001 | BFP TURBINE A INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 600 | C | [6 empty] | 333.5241 | ok
292 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI212601.PNT | 2QAI:AI212601.PNT | 20LBR31CP201 | BFP TURBINE A EXHAUST STEAM PRESS | AI | -100 | 100 | KPa |  |  |  | -67.71 | -47.45 |  | -91.9531 | ok
293 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2NAI.AI172503.PNT | 2NAI:AI172503.PNT | 20LBR31CT001 | BFP TURBINE A EXHAUST STEAM TEMP | RTD | 0 | 200 | C | [6 empty] | 48.0382 | ok
294 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2NAI.AI172504.PNT | 2NAI:AI172504.PNT | 20LBR31CT002 | BFP TURBINE A EXHAUST STEAM TEMP 1 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 52.2342 | ok
295 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2NAI.AI172601.PNT | 2NAI:AI172601.PNT | 20LBR31CT003 | BFP TURBINE A EXHAUST STEAM TEMP 2 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 57.2357 | ok
296 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI212307.PNT | 2QAI:AI212307.PNT | 20LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.5192 | ok
297 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI211405.PNT | 2QAI:AI211405.PNT | 20LBS41CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 343.1463 | ok
298 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI211307.PNT | 2QAI:AI211307.PNT | 20LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 222.2734 | ok
299 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-05 | OPC.AW2002.2QAI.AI211407.PNT | 2QAI:AI211407.PNT | 20LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 297.7211 | ok
300 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2OAI.AI192103.PNT | 2OAI:AI192103.PNT | 20MAV50AP101XB13 | BFP TURBINE A LUBE-OIL SYSTEM MAIN OIL PUMP A CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | -0.016406 | no
301 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2OAI.AI192104.PNT | 2OAI:AI192104.PNT | 20MAV50AP102XB13 | BFP TURBINE A LUBE-OIL SYSTEM MAIN OIL PUMP B CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | 25.0324 | ok
302 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2OAI.AI192105.PNT | 2OAI:AI192105.PNT | 20MAV50AP103XB13 | BFP TURBINE A LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 40.8 |  |  | -0.088867 | no
303 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI213405.PNT | 2QAI:AI213405.PNT | 20MAV50CL201 | BFP TURBINE A LUBE-OIL TANK LEVEL | AI | 0 | 1050 | mm |  | 195 | 322 | 525 | 1050 |  | 370.7617 | ok
304 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2QAI.AI210406.PNT | 2QAI:AI210406.PNT | 20MAV50CT001 | BFP TURBINE A LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 50.3376 | ok
305 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2QAI.AI210506.PNT | 2QAI:AI210506.PNT | 20MAV50CT002 | BFP TURBINE A LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 35.9308 | ok
306 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2OAI.AI192503.PNT | 2OAI:AI192503.PNT | 20MAV50CT003 | BFP TURBINE A LUBE-OIL TANK TEMP. | RTD | 0 | 100 | C | [6 empty] | 51.9354 | ok
307 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2OAI.AI192504.PNT | 2OAI:AI192504.PNT | 20MAV50CT009 | BFP TURBINE A SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 46.4144 | ok
308 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2OAI.AI192505.PNT | 2OAI:AI192505.PNT | 20MAV50CT010 | BFP TURBINE A THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 44.9464 | ok
309 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F290S-J0201-20 | OPC.AW2002.2OAI.AI192506.PNT | 2OAI:AI192506.PNT | 20MAV50CT011 | BFP TURBINE A #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | C | [6 empty] | 47.8693 | ok
310 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2OAI.AI191403.PNT | 2OAI:AI191403.PNT | 20MAV50GC001AI01 | BFP TURBINE A TURNING GEAR CURRENT | AI | 0 | 50 | A | [6 empty] | -0.015625 | no
311 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2MAI.AI162206.PNT | 2MAI:AI162206.PNT | 20MEHADCS01 | BFP TURBINE A SPEED SET POINT SIGNAL | AI | 0 | 100 | % | [6 empty] | 30.6777 | ok
312 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231706.PNT | 2RAI:AI231706.PNT | 20MTSIADCS01 | BFP TURBINE A SPEED (4~20mA) | AI | 0 | 10000 | rpm | [6 empty] | 3788.3594 | ok
313 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231607.PNT | 2RAI:AI231607.PNT | 20MTSIADCS02 | BFP TURBINE A NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 24.5068 | ok
314 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231707.PNT | 2RAI:AI231707.PNT | 20MTSIADCS03 | BFP TURBINE A NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 18.7148 | ok
315 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231801.PNT | 2RAI:AI231801.PNT | 20MTSIADCS04 | BFP TURBINE A NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 28.5264 | ok
316 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI232101.PNT | 2RAI:AI232101.PNT | 20MTSIADCS05 | BFP TURBINE A NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 24.1377 | ok
317 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231802.PNT | 2RAI:AI231802.PNT | 20MTSIADCS06 | BFP TURBINE A NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 19.1807 | ok
318 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI232102.PNT | 2RAI:AI232102.PNT | 20MTSIADCS07 | BFP TURBINE A NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 10.8369 | ok
319 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231803.PNT | 2RAI:AI231803.PNT | 20MTSIADCS08 | BFP TURBINE A NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 12.2373 | ok
320 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI232103.PNT | 2RAI:AI232103.PNT | 20MTSIADCS09 | BFP TURBINE A NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 15.4453 | ok
321 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231804.PNT | 2RAI:AI231804.PNT | 20MTSIADCS10 | BFP TURBINE A AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | 0.18325 | ok
322 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI232104.PNT | 2RAI:AI232104.PNT | 20MTSIADCS11 | BFP TURBINE A AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | 0.18088 | ok
323 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-K0611-02 | OPC.AW2002.2RAI.AI231805.PNT | 2RAI:AI231805.PNT | 20MTSIADCS12 | BFP TURBINE A ECCENTRICTIY (4~20mA) | AI | 0 | 100 | um |  |  |  | 30 |  |  | 0.033203 | ok
324 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-14 | OPC.AW2002.2NAI.AI172404.PNT | 2NAI:AI172404.PNT | 20PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 85.9727 | ok
325 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-14 | OPC.AW2002.2RAI.AI230205.PNT | 2RAI:AI230205.PNT | 20PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 30.2798 | ok
326 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210407.PNT | 2QAI:AI210407.PNT | 20XAC11CT001 | BFP TURBINE A POSITION THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 43.5564 | ok
327 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210507.PNT | 2QAI:AI210507.PNT | 20XAC11CT002 | BFP TURBINE A POSITION THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 43.5304 | ok
328 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210601.PNT | 2QAI:AI210601.PNT | 20XAC11CT003 | BFP TURBINE A WORK THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 59.9377 | ok
329 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210701.PNT | 2QAI:AI210701.PNT | 20XAC11CT004 | BFP TURBINE A WORK THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 54.4946 | ok
330 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210602.PNT | 2QAI:AI210602.PNT | 20XAC11CT005 | BFP TURBINE A SUPPORT PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 71.9282 | ok
331 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210702.PNT | 2QAI:AI210702.PNT | 20XAC11CT006 | BFP TURBINE A SUPPORT PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 65.6407 | ok
332 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210603.PNT | 2QAI:AI210603.PNT | 20XAC11CT007 | BFP TURBINE A #2 BEARING PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 82.3208 | ok
333 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI210703.PNT | 2QAI:AI210703.PNT | 20XAC11CT008 | BFP TURBINE A #2 BEARING PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 61.4057 | ok
334 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A | F296S-J0201-20 | OPC.AW2002.2QAI.AI212204.PNT | 2QAI:AI212204.PNT | 20XAC11CT009 | FRONT CYLINDER METAL WALL TEMP | TC | 0 | 600 | C | [6 empty] | 185.3606 | ok
335 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #2B - BOOSTER PUMP | F296S-J0201-08 | OPC.AW2002.2PAI.AI202102.PNT | 2PAI:AI202102.PNT | 20LAC12AP001XB13 | BOOSTER PUMP FOR T-BFP B CURRENT | AI | 0 | 400 | A |  |  |  | 237 |  |  | 161.7109 | ok
336 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #2B - BOOSTER PUMP | F296S-J0201-32 | OPC.AW2002.2PAI.AI202601.PNT | 2PAI:AI202601.PNT | 20LAC12CT001 | BOOSTER PUMP FOR T-BFP B DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 50.4935 | ok
337 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 3 | T-BFP #2B - BOOSTER PUMP | F296S-J0201-32 | OPC.AW2002.2PAI.AI202602.PNT | 2PAI:AI202602.PNT | 20LAC12CT002 | BOOSTER PUMP FOR T-BFP B FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 49.1684 | ok
338 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-08 | OPC.AW2002.2M_TFPBREC.AO162701.OUT | 2M_TFPBREC:AO162701.OUT | 20LAB12AA101XB11 | T-BFP B MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok | REVISI TAG
339 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-08 | OPC.AW2002.2MAI.AI161701.PNT | 2MAI:AI161701.PNT | 20LAB12AA101XB12 | T-BFP B MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.2793 | ok
340 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-08 | OPC.AW2002.2M_FLOW.BFPBAIN.PNT | 2M_FLOW:BFPBAIN.PNT | 20LAB12CF201 | T-BFP B INLET WATER FLOW | AI | 0 | 800 | t/h |  | 120 | 140 |  |  |  | 389.1 | ok
341 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-08 | OPC.AW2002.2PAI.AI203601.PNT | 2PAI:AI203601.PNT | 20LAB12CP201 | T-BFP B INLET WATER PRESS | AI | 0 | 2 | MPa |  | 1.25 | 1.4 |  |  |  | 1.1277 | ok
342 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-08 | OPC.AW2002.2QAI.AI213104.PNT | 2QAI:AI213104.PNT | 20LAB12CP202 | T-BFP B OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.5669 | ok
343 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202603.PNT | 2PAI:AI202603.PNT | 20LAC12CT003 | T-BFP B INLET WATER END RADIAL BEARING TEMP (TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 49.9219 | ok
344 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202604.PNT | 2PAI:AI202604.PNT | 20LAC12CT004 | T-BFP B OUTLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 47.2718 | ok
345 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202605.PNT | 2PAI:AI202605.PNT | 20LAC12CT005 | T-BFP B THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 44.2319 | ok
346 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202606.PNT | 2PAI:AI202606.PNT | 20LAC12CT006 | T-BFP B THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 43.5434 | ok
347 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202607.PNT | 2PAI:AI202607.PNT | 20LAC12CT007 | T-BFP B INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 44.3228 | ok
348 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202701.PNT | 2PAI:AI202701.PNT | 20LAC12CT008 | T-BFP B OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 56.6381 | ok
349 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202702.PNT | 2PAI:AI202702.PNT | 20LAC12CT009 | T-BFP B WATER INLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 137.9957 | ok
350 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202703.PNT | 2PAI:AI202703.PNT | 20LAC12CT010 | T-BFP B WATER INLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 136.9405 | ok
351 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202704.PNT | 2PAI:AI202704.PNT | 20LAC12CT011 | T-BFP B WATER OUTLET END MAIN BODY TOP TEMP | RTD | 0 | 200 | C | [6 empty] | 140.8541 | ok
352 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-32 | OPC.AW2002.2PAI.AI202705.PNT | 2PAI:AI202705.PNT | 20LAC12CT012 | T-BFP B WATER OUTLET END MAIN BODY BOTTOM TEMP | RTD | 0 | 200 | C | [6 empty] | 138.3029 | ok
353 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2RAI.AI231603.PNT | 2RAI:AI231603.PNT | 20LAC12CY201X | T-BFP B WATER INLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
354 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2RAI.AI231703.PNT | 2RAI:AI231703.PNT | 20LAC12CY202Y | T-BFP B WATER INLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
355 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2RAI.AI231604.PNT | 2RAI:AI231604.PNT | 20LAC12CY203X | T-BFP B WATER OUTLET END BEARING VIBRATION (X DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
356 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2RAI.AI231704.PNT | 2RAI:AI231704.PNT | 20LAC12CY204Y | T-BFP B WATER OUTLET END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 100 | mm/s | [8 empty] | TIDAK DIPAKAI
357 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2Q_FLOW.BFPSTMBAIN.PNT | 2Q_FLOW:BFPSTMBAIN.PNT | 20LBR22CF201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) FLOW | AI | 0 | 30 | t/h | [6 empty] | 10.7489 | ok
358 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI212501.PNT | 2QAI:AI212501.PNT | 20LBR22CP201 | BFP TURBINE B INLET STEAM(#4 EXTRACTION STEAM) PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.84295 | ok
359 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI211502.PNT | 2QAI:AI211502.PNT | 20LBR22CT001 | BFP TURBINE B INLET STEAM (#4 EXTRACTION STEAM) TEMP | TC | 0 | 600 | C | [6 empty] | 318.7409 | ok
360 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI212502.PNT | 2QAI:AI212502.PNT | 20LBR32CP201 | BFP TURBINE B EXHAUST STEAM PRESS | AI | -100 | 100 | KPa |  |  |  | -67.71 | -47.45 |  | -91.7266 | ok
361 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2NAI.AI172505.PNT | 2NAI:AI172505.PNT | 20LBR32CT001 | BFP TURBINE B EXHAUST STEAM TEMP | RTD | 0 | 200 | C | [6 empty] | 44.6996 | ok
362 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2NAI.AI172506.PNT | 2NAI:AI172506.PNT | 20LBR32CT002 | BFP TURBINE B EXHAUST STEAM TEMP 1 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 45.2971 | ok
363 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2NAI.AI172602.PNT | 2NAI:AI172602.PNT | 20LBR32CT003 | BFP TURBINE B EXHAUST STEAM TEMP 2 | RTD | 0 | 200 | C |  |  |  | 135 | 150 |  | 52.572 | ok
364 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202103.PNT | 2PAI:AI202103.PNT | 20MAV60AP101XB13 | BFP TURBINE B LUBE-OIL SYSTEM MAIN OIL PUMP A CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | -0.0035156 | no
365 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202104.PNT | 2PAI:AI202104.PNT | 20MAV60AP102XB13 | BFP TURBINE B LUBE-OIL SYSTEM MAIN OIL PUMP B CURRENT | AI | 0 | 60 | A |  |  |  | 35.1 |  |  | 24.1008 | ok
366 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202105.PNT | 2PAI:AI202105.PNT | 20MAV60AP103XB13 | BFP TURBINE B LUBE-OIL SYSTEM D.C. EMERGENCY LUBE-OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 40.8 |  |  | 12.4863 | ok
367 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI213306.PNT | 2QAI:AI213306.PNT | 20MAV60CL201 | BFP TURBINE B LUBE-OIL TANK LEVEL | AI | 0 | 1050 | mm |  | 195 | 322 | 525 | 1050 |  | 494.6094 | ok
368 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210604.PNT | 2QAI:AI210604.PNT | 20MAV60CT001 | BFP TURBINE B LUBE-OIL COOLER INLET TEMP | RTD | 0 | 100 | C | [6 empty] | 43.6343 | ok
369 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210705.PNT | 2QAI:AI210705.PNT | 20MAV60CT002 | BFP TURBINE B LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 34.0471 | ok
370 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202505.PNT | 2PAI:AI202505.PNT | 20MAV60CT003 | BFP TURBINE B LUBE-OIL TANK TEMP. | RTD | 0 | 100 | C | [6 empty] | 44.5307 | ok
371 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202506.PNT | 2PAI:AI202506.PNT | 20MAV60CT009 | BFP TURBINE B SUPPORT BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 45.8557 | ok
372 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202503.PNT | 2PAI:AI202503.PNT | 20MAV60CT010 | BFP TURBINE B THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 46.2974 | ok
373 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202504.PNT | 2PAI:AI202504.PNT | 20MAV60CT011 | BFP TURBINE B #2 BEARING OIL RETURN TEMP | RTD | 0 | 100 | C | [6 empty] | 42.0365 | ok
374 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2PAI.AI202804.PNT | 2PAI:AI202804.PNT | 20MAV60GC001AI01 | BFP TURBINE B TURNING GEAR CURRENT | AI | 0 | 50 | A | [6 empty] | -0.40527 | no
375 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2MAI.AI162305.PNT | 2MAI:AI162305.PNT | 20MEHBDCS01 | BFP TURBINE B SPEED SET POINT SIGNAL | AI | 0 | 100 | % | [6 empty] | 30.6621 | ok
376 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232105.PNT | 2RAI:AI232105.PNT | 20MTSIBDCS01 | BFP TURBINE B SPEED (4~20mA) | AI | 0 | 10000 | rpm | [6 empty] | 3794.0234 | ok
377 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI231806.PNT | 2RAI:AI231806.PNT | 20MTSIBDCS02 | BFP TURBINE B NO.1 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 22.1338 | ok
378 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232106.PNT | 2RAI:AI232106.PNT | 20MTSIBDCS03 | BFP TURBINE B NO.1 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 18.7588 | ok
379 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI231807.PNT | 2RAI:AI231807.PNT | 20MTSIBDCS04 | BFP TURBINE B NO.2 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 26.0391 | ok
380 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232107.PNT | 2RAI:AI232107.PNT | 20MTSIBDCS05 | BFP TURBINE B NO.2 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 27.832 | ok
381 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232201.PNT | 2RAI:AI232201.PNT | 20MTSIBDCS06 | BFP TURBINE B NO.3 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 44.5166 | ok
382 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232301.PNT | 2RAI:AI232301.PNT | 20MTSIBDCS07 | BFP TURBINE B NO.3 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 49.1982 | ok
383 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232202.PNT | 2RAI:AI232202.PNT | 20MTSIBDCS08 | BFP TURBINE B NO.4 SHAFT VIBRATION (X DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 20.8301 | ok
384 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232302.PNT | 2RAI:AI232302.PNT | 20MTSIBDCS09 | BFP TURBINE B NO.4 SHAFT VIBRATION (Y DIRECTION) (4~20mA) | AI | 0 | 150 | mm/s |  |  |  | 80 | 125 |  | 18.2578 | ok
385 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232203.PNT | 2RAI:AI232203.PNT | 20MTSIBDCS10 | BFP TURBINE B AXIAL DISPLACEMENT NO.1 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | 0.077344 | ok
386 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232303.PNT | 2RAI:AI232303.PNT | 20MTSIBDCS11 | BFP TURBINE B AXIAL DISPLACEMENT NO.2 (4~20mA) | AI | -0.8 | 0.8 | mm/s |  | -0.62 | -0.55 | 0.3 | 0.4 |  | 0.023719 | ok
387 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-K0611-03 | OPC.AW2002.2RAI.AI232204.PNT | 2RAI:AI232204.PNT | 20MTSIBDCS12 | BFP TURBINE B ECCENTRICTIY (4~20mA) | AI | 0 | 100 | um |  |  |  | 30 |  |  | 0.052734 | ok
388 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210605.PNT | 2QAI:AI210605.PNT | 20XAC12CT001 | BFP TURBINE B POSITION THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 47.2847 | ok
389 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210706.PNT | 2QAI:AI210706.PNT | 20XAC12CT002 | BFP TURBINE B POSITION THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 43.1796 | ok
390 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210606.PNT | 2QAI:AI210606.PNT | 20XAC12CT003 | BFP TURBINE B WORK THRUST PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 49.1294 | ok
391 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210801.PNT | 2QAI:AI210801.PNT | 20XAC12CT004 | BFP TURBINE B WORK THRUST PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 44.9074 | ok
392 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210607.PNT | 2QAI:AI210607.PNT | 20XAC12CT005 | BFP TURBINE B SUPPORT PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 62.5359 | ok
393 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210802.PNT | 2QAI:AI210802.PNT | 20XAC12CT006 | BFP TURBINE B SUPPORT PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 61.7175 | ok
394 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210707.PNT | 2QAI:AI210707.PNT | 20XAC12CT007 | BFP TURBINE B #2 BEARING PAD TEMP 1 | RTD | 0 | 200 | C | [6 empty] | 66.1603 | ok
395 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI210803.PNT | 2QAI:AI210803.PNT | 20XAC12CT008 | BFP TURBINE B #2 BEARING PAD TEMP 2 | RTD | 0 | 200 | C | [6 empty] | 75.6176 | ok
396 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-20 | OPC.AW2002.2QAI.AI212107.PNT | 2QAI:AI212107.PNT | 20XAC12CT009 | FRONT CYLINDER METAL WALL TEMP | TC | 0 | 600 | C | [6 empty] | 181.941 | ok
397 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2M_BFPREC.AO162602.OUT | 2M_BFPREC:AO162602.OUT | 20LAH10AA101XB11 | M-BFP MINI FLOW RECIRCULATING VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
398 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2MAI.AI161606.PNT | 2MAI:AI161606.PNT | 20LAH10AA101XB12 | M-BFP MINI FLOW RECIRCULATING VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 100.0684 | no
399 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2M_FLOW.MBFPAIN.PNT | 2M_FLOW:MBFPAIN.PNT | 20LAH10CF201 | M-BFP INLET WATER FLOW | AI | 0 | 410 | t/h | [6 empty] | 0 | ok
400 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2OAI.AI193501.PNT | 2OAI:AI193501.PNT | 20LAH10CP201 | M-BFP INLET PRESS | AI | 0 | 2 | MPa |  | 0.95 | 1.1 |  |  |  | 0.62262 | ok
401 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI213103.PNT | 2QAI:AI213103.PNT | 20LAH10CP202 | M-BFP OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 0.63574 | ok
402 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2M_FWCNTL.AOUTC.OUT | 2M_FWCNTL:AOUTC.OUT | 20LAJ10AA101XB11 | M-BFP HYDRAULIC CUOPLE ACTUATOR CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 50 | ok
403 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2MAI.AI161702.PNT | 2MAI:AI161702.PNT | 20LAJ10AA101XB12 | M-BFP HYDRAULIC CUOPLE ACTUATOR POSITION | AI | 0 | 100 | % | [6 empty] | 52.4727 | ok
404 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-08 | OPC.AW2002.2OAI.AI191302.PNT | 2OAI:AI191302.PNT | 20LAJ10AP001XB13 | M-BFP GROUP CURRENT | AI | 0 | 600 | A |  |  |  | 363 |  |  | -0.30469 | no
405 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI191405.PNT | 2OAI:AI191405.PNT | 20LAJ10AP003XB13 | M-BFP HYDRAULIC CUOPLE OIL PUMP CURRENT | AI | 0 | 25 | A | [6 empty] | 15.4316 | ok
406 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI191404.PNT | 2OAI:AI191404.PNT | 20LAJ10CS002 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min | [8 empty] | TIDAK DIPAKAI
407 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2QAI.AI213406.PNT | 2QAI:AI213406.PNT | 20LAJ10CS201 | M-BFP OUTLET WATER END ROTATIONAL SPEED | AI | 0 | 6000 | r/min | [6 empty] | 4.7852 | ok
408 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192603.PNT | 2OAI:AI192603.PNT | 20LAJ10CT003 | M-BFP INLET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 30.5267 | ok
409 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192604.PNT | 2OAI:AI192604.PNT | 20LAJ10CT004 | M-BFP OUTET WATER END RADIAL BEARING TEMP(TOP) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 30.9294 | ok
410 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192605.PNT | 2OAI:AI192605.PNT | 20LAJ10CT005 | M-BFP THRUST BEARING TEMP(MAIN THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 31.0723 | ok
411 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192606.PNT | 2OAI:AI192606.PNT | 20LAJ10CT006 | M-BFP THRUST BEARING TEMP(AUXILIARY THRUST PAD) | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 31.3321 | ok
412 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192607.PNT | 2OAI:AI192607.PNT | 20LAJ10CT007 | M-BFP INLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 27.7726 | ok
413 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192701.PNT | 2OAI:AI192701.PNT | 20LAJ10CT008 | M-BFP OUTLET WATER END MECHANICAL SEAL CIRCULATING WATER TEMP | RTD | 0 | 200 | C |  |  |  | 80 | 90 |  | 26.8892 | ok
414 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192702.PNT | 2OAI:AI192702.PNT | 20LAJ10CT009 | M-BFP HYDRAULIC COUPLER B1 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 30.6306 | ok
415 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192703.PNT | 2OAI:AI192703.PNT | 20LAJ10CT010 | M-BFP HYDRAULIC COUPLER B2 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 30.6306 | ok
416 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192704.PNT | 2OAI:AI192704.PNT | 20LAJ10CT011 | M-BFP HYDRAULIC COUPLER B3 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 30.9553 | ok
417 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192705.PNT | 2OAI:AI192705.PNT | 20LAJ10CT012 | M-BFP HYDRAULIC COUPLER B4 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 25.6291 | ok
418 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192706.PNT | 2OAI:AI192706.PNT | 20LAJ10CT013 | M-BFP HYDRAULIC COUPLER B5 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 31.3581 | ok
419 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192707.PNT | 2OAI:AI192707.PNT | 20LAJ10CT014 | M-BFP HYDRAULIC COUPLER B6 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 33.4626 | ok
420 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192801.PNT | 2OAI:AI192801.PNT | 20LAJ10CT015 | M-BFP HYDRAULIC COUPLER B7 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 31.2931 | ok
421 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192802.PNT | 2OAI:AI192802.PNT | 20LAJ10CT016 | M-BFP HYDRAULIC COUPLER B8 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 32.7481 | ok
422 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192803.PNT | 2OAI:AI192803.PNT | 20LAJ10CT017 | M-BFP HYDRAULIC COUPLER B9 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 31.6179 | ok
423 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192804.PNT | 2OAI:AI192804.PNT | 20LAJ10CT018 | M-BFP HYDRAULIC COUPLER B10 RADIAL BEARING TEMP | RTD | 0 | 180 | C |  |  |  | 90 | 95 |  | 31.5139 | ok
424 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192805.PNT | 2OAI:AI192805.PNT | 20LAJ10CT019 | M-BFP LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 180 | C |  |  |  | 55 | 60 |  | 31.8517 | ok
425 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192806.PNT | 2OAI:AI192806.PNT | 20LAJ10CT020 | M-BFP WORKING OIL COOLER INLET TEMP | RTD | 0 | 180 | C |  |  |  | 110 | 130 |  | 32.0855 | ok
426 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192807.PNT | 2OAI:AI192807.PNT | 20LAJ10CT021 | M-BFP WORKING OIL COOLER OUTLET TEMP | RTD | 0 | 180 | C |  |  |  | 75 | 85 |  | 31.2411 | ok
427 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193101.PNT | 2OAI:AI193101.PNT | 20LAJ10CT022 | M-BFP HYDRAULIC COUPLER MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | C |  |  |  | 85 | 90 |  | 29.9161 | ok
428 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193103.PNT | 2OAI:AI193103.PNT | 20LAJ10CT024 | M-BFP MOTOR STATOR WINDING TEMP 1 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.5526 | ok
429 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193104.PNT | 2OAI:AI193104.PNT | 20LAJ10CT025 | M-BFP MOTOR STATOR WINDING TEMP 2 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.8514 | ok
430 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193105.PNT | 2OAI:AI193105.PNT | 20LAJ10CT026 | M-BFP MOTOR STATOR WINDING TEMP 3 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.5786 | ok
431 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193201.PNT | 2OAI:AI193201.PNT | 20LAJ10CT027 | M-BFP MOTOR STATOR WINDING TEMP 4 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.7735 | ok
432 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193202.PNT | 2OAI:AI193202.PNT | 20LAJ10CT028 | M-BFP MOTOR STATOR WINDING TEMP 5 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.6306 | ok
433 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193203.PNT | 2OAI:AI193203.PNT | 20LAJ10CT029 | M-BFP MOTOR STATOR WINDING TEMP 6 | RTD | 0 | 200 | C |  |  |  | 115 | 120 |  | 30.5137 | ok
434 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI191402.PNT | 2OAI:AI191402.PNT | 20LAJ10CY201X | M-BFP FREE END BEARING VIBRATION (X DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.20109 | ok
435 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI191401.PNT | 2OAI:AI191401.PNT | 20LAJ10CY202Y | M-BFP FREE END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.066039 | ok
436 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2QAI.AI213501.PNT | 2QAI:AI213501.PNT | 20LAJ10CY203X | M-BFP DRIVE END BEARING VIBRATION (X DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.16256 | ok
437 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2QAI.AI213502.PNT | 2QAI:AI213502.PNT | 20LAJ10CY204Y | M-BFP DRIVE END BEARING VIBRATION (Y DIRECTION) | AI | 0 | 20 | mm/s |  |  |  | 7.1 | 11.2 |  | 0.018457 | ok
438 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192601.PNT | 2OAI:AI192601.PNT | 20LAJ10CT001 | BOOSTER PUMP FOR M-BFP FREE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 30.3448 | ok
439 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI192602.PNT | 2OAI:AI192602.PNT | 20LAJ10CT002 | BOOSTER PUMP FOR M-BFP DRIVE END RADIAL BEARING TEMP | RTD | 0 | 200 | C |  |  |  | 90 | 100 |  | 23.3817 | ok
440 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 5 | M-BFP #2 | F296S-J0201-21 | OPC.AW2002.2OAI.AI193102.PNT | 2OAI:AI193102.PNT | 20LAJ10CT023 | BOOSTER PUMP FOR M-BFP MOTOR RADIAL BEARING TEMP | RTD | 0 | 160 | C |  |  |  | 85 | 90 |  | 30.3708 | ok
441 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI212705.PNT | 2QAI:AI212705.PNT | 20LAB30CP201 | HP HEATER MAIN PIPE INLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.4243 | ok
442 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI211702.PNT | 2QAI:AI211702.PNT | 20LAB30CT001 | HP HEATER INLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 153.7922 | ok
443 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI212102.PNT | 2QAI:AI212102.PNT | 20LAB30CT002 | #3 HP HEATER OUTLET MAIN PIPE WATER TEMP | TC | 0 | 500 | C | [6 empty] | 190.6444 | ok
444 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.234.RO01 | 2PMS:234.RO01 | 20LAB30CT002C1 | #3 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | -6.9553 | ok
445 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.233.RO01 | 2PMS:233.RO01 | 20LAB30CT002C2 | #3 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 36.8447 | ok
446 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI160702.PNT | 2MAI:AI160702.PNT | 20LAD30CL201 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -13.9766 | ok
447 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP3LVL_1.SIGSEL1OUT.PNT | 2M_HP3LVL_1:SIGSEL1OUT.PNT | 20LAD30CL201C1 | #3 HP HEATER LEVEL AVG | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | 1.4297 | ok
448 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161102.PNT | 2MAI:AI161102.PNT | 20LAD30CL202 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -0.097656 | ok
449 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161202.PNT | 2MAI:AI161202.PNT | 20LAD30CL203 | #3 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | 5.6631 | ok
450 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI172101.PNT | 2NAI:AI172101.PNT | 20LBQ30AA001XB12 | #3 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.9219 | ok | REVISI TAG
451 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212306.PNT | 2QAI:AI212306.PNT | 20LBQ30CP201 | #3 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 1.9 | MPa | [6 empty] | 1.1198 | ok
452 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212406.PNT | 2QAI:AI212406.PNT | 20LBQ30CP202 | #3 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 1.9 | MPa | [6 empty] | 1.1146 | ok
453 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211303.PNT | 2QAI:AI211303.PNT | 20LBQ30CT001 | #3 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 427.2736 | ok
454 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211304.PNT | 2QAI:AI211304.PNT | 20LBQ30CT002 | #3 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 408.9779 | ok
455 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211404.PNT | 2QAI:AI211404.PNT | 20LBQ30CT003 | #3 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 421.1455 | ok
456 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211403.PNT | 2QAI:AI211403.PNT | 20LBQ30CT004 | #3 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 500 | C | [6 empty] | 455.2962 | ok
457 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP3LVL.AO162704.OUT | 2M_HP3LVL:AO162704.OUT | 20LCH30AA101XB11 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 53.2667 | ok
458 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161706.PNT | 2MAI:AI161706.PNT | 20LCH30AA101XB12 | #3 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 51.1758 | ok
459 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP3LVL.AO163102.OUT | 2M_HP3LVL:AO163102.OUT | 20LCH30AA102XB11 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
460 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI162104.PNT | 2MAI:AI162104.PNT | 20LCH30AA102XB12 | #3 HP HEATER EMERGENCY DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.6094 | ok
461 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2QAI.AI211705.PNT | 2QAI:AI211705.PNT | 20LCH30CT001 | #3 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 161.6206 | ok
462 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI211703.PNT | 2QAI:AI211703.PNT | 20LAB30CT003 | #2 HP HEATER OUTLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 220.5513 | ok
463 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.236.RO01 | 2PMS:236.RO01 | 20LAB30CT003C1 | #2 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | 0.33368 | ok
464 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.235.RO01 | 2PMS:235.RO01 | 20LAB30CT003C2 | #2 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 29.9144 | ok
465 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI160701.PNT | 2MAI:AI160701.PNT | 20LAD20CL201 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -11.0381 | ok
466 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP2LVL_1.SIGSEL1OUT.PNT | 2M_HP2LVL_1:SIGSEL1OUT.PNT | 20LAD20CL201C1 | #2 HP HEATER LEVEL SIGSEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -14.0928 | ok
467 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161101.PNT | 2MAI:AI161101.PNT | 20LAD20CL202 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -16.583 | ok
468 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161201.PNT | 2MAI:AI161201.PNT | 20LAD20CL203 | #2 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -13.6943 | ok
469 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI172103.PNT | 2NAI:AI172103.PNT | 20LBQ20AA001XB12 | #2 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 99.6504 | ok
470 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212305.PNT | 2QAI:AI212305.PNT | 20LBQ20CP201 | #2 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 4 | MPa | [6 empty] | 2.3802 | ok
471 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212405.PNT | 2QAI:AI212405.PNT | 20LBQ20CP202 | #2 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 4 | MPa | [6 empty] | 2.391 | ok
472 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211301.PNT | 2QAI:AI211301.PNT | 20LBQ20CT001 | #2 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 349.3282 | ok
473 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211302.PNT | 2QAI:AI211302.PNT | 20LBQ20CT002 | #2 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 299.4161 | ok
474 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211402.PNT | 2QAI:AI211402.PNT | 20LBQ20CT003 | #2 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 333.3295 | ok
475 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211401.PNT | 2QAI:AI211401.PNT | 20LBQ20CT004 | #2 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | C | [6 empty] | 355.8487 | ok
476 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP2LVL.AO163101.OUT | 2M_HP2LVL:AO163101.OUT | 20LCH20AA101XB11 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 32.3776 | ok
477 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI162102.PNT | 2MAI:AI162102.PNT | 20LCH20AA101XB12 | #2 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 35.0312 | ok
478 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP2LVL.AO162607.OUT | 2M_HP2LVL:AO162607.OUT | 20LCH20AA102XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
479 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161705.PNT | 2MAI:AI161705.PNT | 20LCH20AA102XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | -1.5332 | no
480 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP2LVL.AO162703.OUT | 2M_HP2LVL:AO162703.OUT | 20LCH20AA103XB11 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
481 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI162103.PNT | 2MAI:AI162103.PNT | 20LCH20AA103XB12 | #2 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 0.87109 | ok
482 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2QAI.AI212104.PNT | 2QAI:AI212104.PNT | 20LCH20CT001 | #2 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 193.4713 | ok
483 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI212103.PNT | 2QAI:AI212103.PNT | 20LAB30CT004 | #1 HP HEATER OUTLET WATER TEMP | TC | 0 | 500 | C | [6 empty] | 249.6372 | ok
484 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.238.RO01 | 2PMS:238.RO01 | 20LAB30CT004C1 | #1 HP DIFF. TEMP | TC | -50 | 200 | C | [6 empty] | -3.1492 | ok
485 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-08 | OPC.AW2002.2PMS.237.RO01 | 2PMS:237.RO01 | 20LAB30CT004C2 | #1 HP TEMP RISE | TC | -50 | 200 | C | [6 empty] | 29.086 | ok
486 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-08 | OPC.AW2002.2QAI.AI213105.PNT | 2QAI:AI213105.PNT | 20LAB40CP201 | HP HEATER OUTLET WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 11.4028 | ok
487 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI160407.PNT | 2MAI:AI160407.PNT | 20LAD10CL201 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -13.2627 | ok
488 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP1LVL_1.SIGSEL1OUT.PNT | 2M_HP1LVL_1:SIGSEL1OUT.PNT | 20LAD10CL201C1 | #1 HP HEATER LEVEL SIGSEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -13.8105 | ok
489 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI160507.PNT | 2MAI:AI160507.PNT | 20LAD10CL202 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -15.7861 | ok
490 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI160607.PNT | 2MAI:AI160607.PNT | 20LAD10CL203 | #1 HP HEATER LEVEL | AI | -100 | 400 | mm |  | -68 | -30 | 38 | 150 | 350 | -13.8105 | ok
491 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2NAI.AI172102.PNT | 2NAI:AI172102.PNT | 20LBQ10AA001XB12 | #1 EXTRACTION STEAM MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 100.209 | no
492 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212304.PNT | 2QAI:AI212304.PNT | 20LBQ10CP201 | #1 EXTRACTION STEAM PRESS (TURBINE SIDE) | AI | 0 | 6.6 | MPa | [6 empty] | 3.744 | ok
493 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI212404.PNT | 2QAI:AI212404.PNT | 20LBQ10CP202 | #1 EXTRACTION STEAM PRESS (HP HEATER SIDE) | AI | 0 | 6.6 | MPa | [6 empty] | 3.747 | ok
494 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211106.PNT | 2QAI:AI211106.PNT | 20LBQ10CT001 | #1 EXTRACTION STEAM TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 415.3978 | ok
495 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211107.PNT | 2QAI:AI211107.PNT | 20LBQ10CT002 | #1 EXTRACTION PIPE TOP TEMP | TC | 0 | 500 | C | [6 empty] | 339.6595 | ok
496 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211207.PNT | 2QAI:AI211207.PNT | 20LBQ10CT003 | #1 EXTRACTION PIPE BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 391.5994 | ok
497 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-05 | OPC.AW2002.2QAI.AI211206.PNT | 2QAI:AI211206.PNT | 20LBQ10CT004 | #1 EXTRACTION STEAM TEMP (HP HEATER SIDE) | TC | 0 | 600 | C | [6 empty] | 417.034 | ok
498 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP1LVL.AO162605.OUT | 2M_HP1LVL:AO162605.OUT | 20LCH10AA101XB11 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 75.4064 | ok
499 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161703.PNT | 2MAI:AI161703.PNT | 20LCH10AA101XB12 | #1 HP HEATER NORMAL DRAIN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 71.457 | ok
500 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP1LVL.AO162606.OUT | 2M_HP1LVL:AO162606.OUT | 20LCH10AA102XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
501 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI161704.PNT | 2MAI:AI161704.PNT | 20LCH10AA102XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok | OUT OFF RANGE
502 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2M_HP1LVL.AO162702.OUT | 2M_HP1LVL:AO162702.OUT | 20LCH10AA103XB11 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
503 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2MAI.AI162101.PNT | 2MAI:AI162101.PNT | 20LCH10AA103XB12 | #1 HP HEATER EMERGENCY DRAIN CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | -1.6973 | no
504 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 | F296S-J0201-09(1/2) | OPC.AW2002.2QAI.AI211704.PNT | 2QAI:AI211704.PNT | 20LCH10CT001 | #1 HP HEATER DRAIN WATER TEMP | TC | 0 | 500 | C | [6 empty] | 213.9654 | ok
505 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FWCNTL.AO163107.OUT | 2M_FWCNTL:AO163107.OUT | 20DCSMEHA01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | % | [6 empty] | 30.6151 | ok
506 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FWCNTL.AO163208.OUT | 2M_FWCNTL:AO163208.OUT | 20DCSMEHB01 | BOILER FEED WATER FLOW SIGNAL | AO | 0 | 100 | % | [6 empty] | 30.6151 | ok
507 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2JAI.AI125601.PNT | 2JAI:AI125601.PNT | 20LAB40AA002XB12 | BOILER FEED WATER MOTORIZED ORIFICE VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 98.1934 | ok
508 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FLOW.FW1AIN.PNT | 2M_FLOW:FW1AIN.PNT | 20LAB40CF201 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 553.3839 | ok
509 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FLOW.FW2AIN.PNT | 2M_FLOW:FW2AIN.PNT | 20LAB40CF202 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 553.8315 | ok
510 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FLOW.FW3AIN.PNT | 2M_FLOW:FW3AIN.PNT | 20LAB40CF203 | FEED WATER FLOW | AI | 0 | 1600 | t/h | [6 empty] | 554.0864 | ok
511 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI140605.PNT | 2LAI:AI140605.PNT | 20LAB40CP201C1 | FEED WATER OPERATE STATION FRONT PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.3892 | ok
512 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI140606.PNT | 2LAI:AI140606.PNT | 20LAB40CP202 | FEED WATER OPERATE STATION REAR PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.3701 | ok
513 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2MAI.AI163307.PNT | 2MAI:AI163307.PNT | 20LAB40CT001 | FEED WATER TEMPERATURE | TC | 0 | 300 | ℃ | [6 empty] | 249.6573 | ok
514 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2M_FWCNTL.AO162801.OUT | 2M_FWCNTL:AO162801.OUT | 20LAB41AA101XB11 | BOILER FEED WATER BYPASS CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
515 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 12 | FEEDWATER PIPE#2 | 50-F296S-J0201-08 | OPC.AW2002.2MAI.AI162306.PNT | 2MAI:AI162306.PNT | 20LAB41AA101XB12 | BOILER FEED WATER BYPASS CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 1.1934 | ok
516 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051603.PNT | 2EAI:AI051603.PNT | 20HFW11AA101XB12 | SAF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 0.95898 | ok
517 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2IAI.AI100507.PNT | 2IAI:AI100507.PNT | 20HFW11AN001XB13 | SAF A CURRENT | AI | 0 | 300 | A | [6 empty] | -0.84961 | no
518 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 1 | SAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_SAF.AO052503.OUT | 2E_SAF:AO052503.OUT | 20HFW11AA101XB11 | SAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
519 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051703.PNT | 2EAI:AI051703.PNT | 20HFW12AA101XB12 | SAF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 52.6387 | ok
520 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2IAI.AI100605.PNT | 2IAI:AI100605.PNT | 20HFW12AN001XB13 | SAF B CURRENT | AI | 0 | 300 | A | [6 empty] | 148.5762 | ok
521 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 2 | SAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_SAF.AO052603.OUT | 2E_SAF:AO052603.OUT | 20HFW12AA101XB11 | SAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 53 | ok
522 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051103.PNT | 2EAI:AI051103.PNT | 20HFW10CP201 | SAF OUTLET AIR PRESSURE | AI | 0 | 25 | KPa | [6 empty] | 12.5 | ok
523 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140306.PNT | 2LAI:AI140306.PNT | 20HFW10DP201 | DIFFERENTIAL PRESSURE BETWEEN SAF OUTLET AND PRIMARY HOT AIR MAIN PIPE | AI | 0 | 1.37 | KPa | [6 empty] | 3.2922 | ok
524 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141607.PNT | 2LAI:AI141607.PNT | 20HFW10CT001 | SAF OUTLET AIR TEMP. | TC | 0 | 100 | °C | [6 empty] | 26.4261 | ok
525 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051604.PNT | 2EAI:AI051604.PNT | 20HFW13AA101XB12 | SAF EXHAUST ASH VAVLE POSITION | AI | 0 | 100 | % | [6 empty] | 0.1875 | ok
526 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051104.PNT | 2EAI:AI051104.PNT | 20HFW13DP201 | SAF DIFFERENTIAL PRESSURE BETWEEN FILTER AND DISCHARGE ASH INLET | AI | 0 | 1.37 | KPa | [6 empty] | 0.0021406 | ok
527 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 3 | DUCTING SAF #2 | 50-F296S-J0201-02 | OPC.AW2002.2E_SAFASH.AO052504.OUT | 2E_SAFASH:AO052504.OUT | 20HFW13AA101XB11 | SAF EXHAUST ASH VAVLE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
528 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 4 | COAL FEEDER #2A | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELC.LLAG1.OUT | 2E_FUELC.LLAG1.OUT | 20HFB10GC001AI01 | ECF A INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 0 | ok
529 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 4 | COAL FEEDER #2A | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELF.AOUT1.OUT | 2E_FUELF:AOUT1.OUT | 20HFB10GC001AO01 | ECF A FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
530 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI071105.PNT | 2GAI:AI071105.PNT | 20HFC10AJ001XB13 | MSM A CURRENT | AI | 0 | 200 | A | [6 empty] | -0.25 | no
531 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070101.PNT | 2GAI:AI070101.PNT | 20HFC10CT001 | MSM A MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 38.5549 | ok
532 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070201.PNT | 2GAI:AI070201.PNT | 20HFC10CT002 | MSM A MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 33.8003 | ok
533 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070102.PNT | 2GAI:AI070102.PNT | 20HFC10CT003 | MSM A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 45.8168 | ok
534 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070202.PNT | 2GAI:AI070202.PNT | 20HFC10CT004 | MSM A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 45.44 | ok
535 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070103.PNT | 2GAI:AI070103.PNT | 20HFC10CT005 | MSM A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 47.0899 | ok
536 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070203.PNT | 2GAI:AI070203.PNT | 20HFC10CT006 | MSM A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 45.518 | ok
537 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070104.PNT | 2GAI:AI070104.PNT | 20HFC10CT007 | MSM A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 46.7261 | ok
538 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070204.PNT | 2GAI:AI070204.PNT | 20HFC10CT008 | MSM A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 47.1678 | ok
539 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070105.PNT | 2GAI:AI070105.PNT | 20HFC10CT009 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 35.9438 | ok
540 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070205.PNT | 2GAI:AI070205.PNT | 20HFC10CT010 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 35.8009 | ok
541 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070501.PNT | 2GAI:AI070501.PNT | 20HFC10CT011 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 35.8009 | ok
542 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070502.PNT | 2GAI:AI070502.PNT | 20HFC10CT012 | MSM A PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 35.4112 | ok
543 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070106.PNT | 2GAI:AI070106.PNT | 20HFC10CT013 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 34.9695 | ok
544 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070206.PNT | 2GAI:AI070206.PNT | 20HFC10CT014 | MSM A PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 36.7492 | ok
545 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070107.PNT | 2GAI:AI070107.PNT | 20HFC10CT015 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 51.7016 | ok
546 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050501.PNT | 2EAI:AI050501.PNT | 20HFC10CT016 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 52.0004 | ok
547 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050601.PNT | 2EAI:AI050601.PNT | 20HFC10CT017 | MSM A SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 51.5457 | ok
548 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070207.PNT | 2GAI:AI070207.PNT | 20HFC10CT018 | MSM A LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 35.2033 | ok
549 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070503.PNT | 2GAI:AI070503.PNT | 20HFC10CT019 | MSM A LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 31.2671 | ok
550 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141301.PNT | 2LAI:AI141301.PNT | 20HFC10CY001X | MSM A BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.0093437 | ok
551 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141302.PNT | 2LAI:AI141302.PNT | 20HFC10CY001Y | MSM A BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.039656 | ok
552 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070603.PNT | 2GAI:AI070603.PNT | 20HFC10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 0.21094 | ok
553 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI071106.PNT | 2GAI:AI071106.PNT | 20HFC10GC003AI01 | MSM A OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -10.0078 | no
554 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2GAI.AI070601.PNT | 2GAI:AI070601.PNT | 20HFE10DP201 | MSM A DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | -0.01377 | no
555 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_MAHCAD.AO052606.OUT | 2E_MAHCAD:AO052606.OUT | 20HFE41AA101XB11 | MSM A INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 50 | ok
556 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052102.PNT | 2EAI:AI052102.PNT | 20HFE41AA101XB12 | MSM A INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 59.627 | ok
557 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_MAHCAD.AO052505.OUT | 2E_MAHCAD:AO052505.OUT | 20HFE51AA101XB11 | MSM A INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
558 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051605.PNT | 2EAI:AI051605.PNT | 20HFE51AA101XB12 | MSM A INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | -0.24023 | no
559 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_MAPAD.AO052704.OUT | 2E_MAPAD:AO052704.OUT | 20HFE51AA102XB11 | MSM A INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
560 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052204.PNT | 2EAI:AI052204.PNT | 20HFE51AA102XB12 | MSM A INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.6582 | ok
561 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMA1AIN.PNT | 2E_AIRFLOW:MSMA1AIN.PNT | 20HFE51CF201 | MSM A INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 97.5945 | ok
562 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMA2AIN.PNT | 2E_AIRFLOW:MSMA2AIN.PNT | 20HFE51CF202 | MSM A INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 98.2945 | ok
563 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050703.PNT | 2EAI:AI050703.PNT | 20HFE51CP201 | MSM A INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 1.373 | ok
564 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 5 | MEDIUM SPEED MILL #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050107.PNT | 2EAI:AI050107.PNT | 20HFE51CT001 | MSM A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 51.4427 | ok
565 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140501.PNT | 2LAI:AI140501.PNT | 20HFF11CF201 | 1# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
566 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI071101.PNT | 2GAI:AI071101.PNT | 20HHA51CB201B | 1# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.24805 | ok
567 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCE.AO062504.OUT | 2F_CYCE:AO062504.OUT | 20HLA11AA011XB11 | 1# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20.0015 | ok
568 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061104.PNT | 2FAI:AI061104.PNT | 20HLA11AA011XB12 | 1# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.7617 | ok
569 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXEF.AO062505.OUT | 2F_AUXEF:AO062505.OUT | 20HLA11AA012XB11 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
570 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061105.PNT | 2FAI:AI061105.PNT | 20HLA11AA012XB12 | 1# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.7168 | ok
571 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2F_BUTFF.AO062506.OUT | 2F_BUTFF:AO062506.OUT | 20HLA11AA013XB11 | 1# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
572 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 6 | COAL BURNER LAYER E1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061106.PNT | 2FAI:AI061106.PNT | 20HLA11AA013XB12 | 1# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 10.1719 | ok
573 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140502.PNT | 2LAI:AI140502.PNT | 20HFF12CF201 | 2# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 18.0059 | ok
574 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI071102.PNT | 2GAI:AI071102.PNT | 20HHA52CB201B | 2# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.33594 | ok
575 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061303.PNT | 2FAI:AI061303.PNT | 20HLA21AA011XB12 | 2# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.7324 | ok
576 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061304.PNT | 2FAI:AI061304.PNT | 20HLA21AA012XB12 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.9355 | ok
577 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061305.PNT | 2FAI:AI061305.PNT | 20HLA21AA013XB12 | 2# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 11.3047 | ok
578 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCE.AO062703.OUT | 2F_CYCE:AO062703.OUT | 20HLA21AA011XB11 | 2# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20.0015 | ok
579 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXEF.AO062704.OUT | 2F_AUXEF:AO062704.OUT | 20HLA21AA012XB11 | 2# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
580 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 7 | COAL BURNER LAYER E2 | 50-F296S-J0201-03 | OPC.AW2002.2F_BUTFF.AO062705.OUT | 2F_BUTFF:AO062705.OUT | 20HLA21AA013XB11 | 2# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
581 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140503.PNT | 2LAI:AI140503.PNT | 20HFF13CF201 | 3# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
582 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI071103.PNT | 2GAI:AI071103.PNT | 20HHA53CB201B | 3# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.27148 | ok
583 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCE.AO063202.OUT | 2F_CYCE:AO063202.OUT | 20HLA31AA011XB11 | 3# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20.0015 | ok
584 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061502.PNT | 2FAI:AI061502.PNT | 20HLA31AA011XB12 | 3# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.4844 | ok
585 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXEF.AO063203.OUT | 2F_AUXEF:AO063203.OUT | 20HLA31AA012XB11 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
586 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061503.PNT | 2FAI:AI061503.PNT | 20HLA31AA012XB12 | 3# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.8652 | ok
587 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2F_BUTFF.AO063204.OUT | 2F_BUTFF:AO063204.OUT | 20HLA31AA013XB11 | 3# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
588 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 8 | COAL BURNER LAYER E3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061504.PNT | 2FAI:AI061504.PNT | 20HLA31AA013XB12 | 3# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.623 | ok
589 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140504.PNT | 2LAI:AI140504.PNT | 20HFF14CF201 | 4# CORNER E LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 15.4881 | ok
590 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI071104.PNT | 2GAI:AI071104.PNT | 20HHA54CB201B | 4# CORNER E LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.29492 | ok
591 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCE.AO063401.OUT | 2F_CYCE:AO063401.OUT | 20HLA41AA011XB11 | 4# CORNER E LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 20.0015 | ok
592 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061701.PNT | 2FAI:AI061701.PNT | 20HLA41AA011XB12 | 4# CORNER E LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 19.2246 | ok
593 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXEF.AO063402.OUT | 2F_AUXEF:AO063402.OUT | 20HLA41AA012XB11 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
594 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061702.PNT | 2FAI:AI061702.PNT | 20HLA41AA012XB12 | 4# CORNER EF LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.8281 | ok
595 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2F_BUTFF.AO063403.OUT | 2F_BUTFF:AO063403.OUT | 20HLA41AA013XB11 | 4# CORNER EFF LAYER BURNT AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
596 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 9 | COAL BURNER LAYER E4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061703.PNT | 2FAI:AI061703.PNT | 20HLA41AA013XB12 | 4# CORNER EFF LAYER BURNT AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.9316 | ok
597 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 11 | COAL FEEDER #2B | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELC.LLAG2.OUT | 2E_FUELC.LLAG2.OUT | 20HFB20GC001AI01 | ECF B INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 35.1025 | ok
598 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 11 | COAL FEEDER #2B | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELF.AOUT2.OUT | 2E_FUELF:AOUT2.OUT | 20HFB20GC001AO01 | ECF B FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 64.238 | ok
599 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070705.PNT | 2GAI:AI070705.PNT | 20HFC20AJ001XB13 | MSM B CURRENT | AI | 0 | 200 | A | [6 empty] | 38.5391 | ok
600 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070301.PNT | 2GAI:AI070301.PNT | 20HFC20CT001 | MSM B MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 56.6511 | ok
601 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070401.PNT | 2GAI:AI070401.PNT | 20HFC20CT002 | MSM B MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 41.1401 | ok
602 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070302.PNT | 2GAI:AI070302.PNT | 20HFC20CT003 | MSM B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 63.6401 | ok
603 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070402.PNT | 2GAI:AI070402.PNT | 20HFC20CT004 | MSM B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.6398 | ok
604 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070303.PNT | 2GAI:AI070303.PNT | 20HFC20CT005 | MSM B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.7437 | ok
605 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070403.PNT | 2GAI:AI070403.PNT | 20HFC20CT006 | MSM B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.2241 | ok
606 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070304.PNT | 2GAI:AI070304.PNT | 20HFC20CT007 | MSM B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.2761 | ok
607 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070404.PNT | 2GAI:AI070404.PNT | 20HFC20CT008 | MSM B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.38 | ok
608 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070305.PNT | 2GAI:AI070305.PNT | 20HFC20CT009 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.27 | ok
609 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070405.PNT | 2GAI:AI070405.PNT | 20HFC20CT010 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.4129 | ok
610 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070504.PNT | 2GAI:AI070504.PNT | 20HFC20CT011 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.1661 | ok
611 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070505.PNT | 2GAI:AI070505.PNT | 20HFC20CT012 | MSM B PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 40.3866 | ok
612 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070306.PNT | 2GAI:AI070306.PNT | 20HFC20CT013 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 49.5971 | ok
613 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070406.PNT | 2GAI:AI070406.PNT | 20HFC20CT014 | MSM B PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 58.9115 | ok
614 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070307.PNT | 2GAI:AI070307.PNT | 20HFC20CT015 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.1701 | ok
615 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050502.PNT | 2EAI:AI050502.PNT | 20HFC20CT016 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.0015 | ok
616 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050602.PNT | 2EAI:AI050602.PNT | 20HFC20CT017 | MSM B SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 54.9883 | ok
617 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070407.PNT | 2GAI:AI070407.PNT | 20HFC20CT018 | MSM B LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 39.0876 | ok
618 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070506.PNT | 2GAI:AI070506.PNT | 20HFC20CT019 | MSM B LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 32.0855 | ok
619 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141303.PNT | 2LAI:AI141303.PNT | 20HFC20CY001X | MSM B BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 1.3145 | ok
620 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141304.PNT | 2LAI:AI141304.PNT | 20HFC20CY001Y | MSM B BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.17255 | ok
621 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070604.PNT | 2GAI:AI070604.PNT | 20HFC20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 5.0997 | ok
622 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-34 | OPC.AW2002.2GAI.AI070706.PNT | 2GAI:AI070706.PNT | 20HFC20GC003AI01 | MSM B OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | 3.832 | ok
623 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2GAI.AI070602.PNT | 2GAI:AI070602.PNT | 20HFE20DP201 | MSM B DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 3.7205 | ok
624 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_MBHCAD.AO052607.OUT | 2E_MBHCAD:AO052607.OUT | 20HFE42AA101XB11 | MSM B INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 50.4042 | ok
625 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052103.PNT | 2EAI:AI052103.PNT | 20HFE42AA101XB12 | MSM B INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 50.4336 | ok
626 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_MBHCAD.AO052506.OUT | 2E_MBHCAD:AO052506.OUT | 20HFE52AA101XB11 | MSM B INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 60 | ok
627 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051606.PNT | 2EAI:AI051606.PNT | 20HFE52AA101XB12 | MSM B INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 59.5938 | ok
628 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_MBPAD.AO053102.OUT | 2E_MBPAD:AO053102.OUT | 20HFE52AA102XB11 | MSM B INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 95 | ok
629 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052205.PNT | 2EAI:AI052205.PNT | 20HFE52AA102XB12 | MSM B INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 93.2559 | ok
630 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMB1AIN.PNT | 2E_AIRFLOW:MSMB1AIN.PNT | 20HFE52CF201 | MSM B INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 81.9441 | ok
631 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMB2AIN.PNT | 2E_AIRFLOW:MSMB2AIN.PNT | 20HFE52CF202 | MSM B INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 82.6941 | ok
632 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050704.PNT | 2EAI:AI050704.PNT | 20HFE52CP201 | MSM B INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 5.6766 | ok
633 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 12 | MEDIUM SPEED MILL #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050205.PNT | 2EAI:AI050205.PNT | 20HFE52CT001 | MSM B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 234.3195 | ok
634 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140601.PNT | 2LAI:AI140601.PNT | 20HFF21CF201 | 1# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 22.5303 | ok
635 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI070701.PNT | 2GAI:AI070701.PNT | 20HHA41CB201B | 1# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 100.6934 | ok
636 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDD.AO062501.OUT | 2F_AUXDD:AO062501.OUT | 20HLA11AA008XB11 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 40 | ok
637 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061101.PNT | 2FAI:AI061101.PNT | 20HLA11AA008XB12 | 1# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 38.1289 | ok
638 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCD.AO062502.OUT | 2F_CYCD:AO062502.OUT | 20HLA11AA009XB11 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 70 | ok
639 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061102.PNT | 2FAI:AI061102.PNT | 20HLA11AA009XB12 | 1# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | 69.5586 | ok
640 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDE.AO062503.OUT | 2F_AUXDE:AO062503.OUT | 20HLA11AA010XB11 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
641 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 13 | COAL BURNER LAYER D1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061103.PNT | 2FAI:AI061103.PNT | 20HLA11AA010XB12 | 1# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.3027 | ok
642 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140602.PNT | 2LAI:AI140602.PNT | 20HFF22CF201 | 2# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
643 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI070702.PNT | 2GAI:AI070702.PNT | 20HHA42CB201B | 2# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.8145 | ok
644 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDD.AO062607.OUT | 2F_AUXDD:AO062607.OUT | 20HLA21AA008XB11 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 40 | ok
645 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061207.PNT | 2FAI:AI061207.PNT | 20HLA21AA008XB12 | 2# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 39.2734 | ok
646 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCD.AO062701.OUT | 2F_CYCD:AO062701.OUT | 20HLA21AA009XB11 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 70 | ok
647 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061301.PNT | 2FAI:AI061301.PNT | 20HLA21AA009XB12 | 2# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | 69.5547 | ok
648 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDE.AO062702.OUT | 2F_AUXDE:AO062702.OUT | 20HLA21AA010XB11 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
649 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 14 | COAL BURNER LAYER D2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061302.PNT | 2FAI:AI061302.PNT | 20HLA21AA010XB12 | 2# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.4082 | ok
650 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140603.PNT | 2LAI:AI140603.PNT | 20HFF23CF201 | 3# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
651 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI070703.PNT | 2GAI:AI070703.PNT | 20HHA43CB201B | 3# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.1543 | ok
652 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDD.AO063106.OUT | 2F_AUXDD:AO063106.OUT | 20HLA31AA008XB11 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 40 | ok
653 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061406.PNT | 2FAI:AI061406.PNT | 20HLA31AA008XB12 | 3# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 39.4121 | ok
654 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCD.AO063107.OUT | 2F_CYCD:AO063107.OUT | 20HLA31AA009XB11 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 70 | ok
655 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061407.PNT | 2FAI:AI061407.PNT | 20HLA31AA009XB12 | 3# CORNER D LAYER CYCLE AIR DAMPER CONTROL | AI | 0 | 100 | % | [6 empty] | 69.5215 | ok
656 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDE.AO063201.OUT | 2F_AUXDE:AO063201.OUT | 20HLA31AA010XB11 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
657 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 15 | COAL BURNER LAYER D3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061501.PNT | 2FAI:AI061501.PNT | 20HLA31AA010XB12 | 3# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.1152 | ok
658 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140604.PNT | 2LAI:AI140604.PNT | 20HFF24CF201 | 4# CORNER D LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
659 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-39 | OPC.AW2002.2GAI.AI070704.PNT | 2GAI:AI070704.PNT | 20HHA44CB201B | 4# CORNER D LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.4844 | ok
660 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDD.AO063305.OUT | 2F_AUXDD:AO063305.OUT | 20HLA41AA008XB11 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 40 | ok
661 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061605.PNT | 2FAI:AI061605.PNT | 20HLA41AA008XB12 | 4# CORNER DD LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 37.8242 | ok
662 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCD.AO063306.OUT | 2F_CYCD:AO063306.OUT | 20HLA41AA009XB11 | 4# CORNER D LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 70 | ok
663 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061606.PNT | 2FAI:AI061606.PNT | 20HLA41AA009XB12 | 4# CORNER D LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 69.3438 | ok
664 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXDE.AO063307.OUT | 2F_AUXDE:AO063307.OUT | 20HLA41AA010XB11 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
665 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 16 | COAL BURNER LAYER D4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061607.PNT | 2FAI:AI061607.PNT | 20HLA41AA010XB12 | 4# CORNER DE LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.0352 | ok
666 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 18 | COAL FEEDER #2C | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELC.LLAG3.OUT | 2E_FUELC.LLAG3.OUT | 20HFB30GC001AI01 | ECF C INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 40.473 | ok
667 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 18 | COAL FEEDER #2C | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELF.AOUT3.OUT | 2E_FUELF:AOUT3.OUT | 20HFB30GC001AO01 | ECF C FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 73.4645 | ok
668 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI091105.PNT | 2HAI:AI091105.PNT | 20HFC30AJ001XB13 | MSM C CURRENT | AI | 0 | 200 | A | [6 empty] | 45.9062 | ok
669 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090101.PNT | 2HAI:AI090101.PNT | 20HFC30CT001 | MSM C MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 50.5844 | ok
670 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090201.PNT | 2HAI:AI090201.PNT | 20HFC30CT002 | MSM C MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 37.2688 | ok
671 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090102.PNT | 2HAI:AI090102.PNT | 20HFC30CT003 | MSM C MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 64.7313 | ok
672 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090202.PNT | 2HAI:AI090202.PNT | 20HFC30CT004 | MSM C MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 59.548 | ok
673 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090103.PNT | 2HAI:AI090103.PNT | 20HFC30CT005 | MSM C MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 60.6652 | ok
674 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090203.PNT | 2HAI:AI090203.PNT | 20HFC30CT006 | MSM C MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 59.7689 | ok
675 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090104.PNT | 2HAI:AI090104.PNT | 20HFC30CT007 | MSM C MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 62.5229 | ok
676 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090204.PNT | 2HAI:AI090204.PNT | 20HFC30CT008 | MSM C MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 64.3156 | ok
677 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090105.PNT | 2HAI:AI090105.PNT | 20HFC30CT009 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 39.932 | ok
678 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090205.PNT | 2HAI:AI090205.PNT | 20HFC30CT010 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 40.8933 | ok
679 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090501.PNT | 2HAI:AI090501.PNT | 20HFC30CT011 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 40.0489 | ok
680 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090502.PNT | 2HAI:AI090502.PNT | 20HFC30CT012 | MSM C PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 40.9842 | ok
681 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090106.PNT | 2HAI:AI090106.PNT | 20HFC30CT013 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 49.1684 | ok
682 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090206.PNT | 2HAI:AI090206.PNT | 20HFC30CT014 | MSM C PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 57.0798 | ok
683 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090107.PNT | 2HAI:AI090107.PNT | 20HFC30CT015 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.2481 | ok
684 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050503.PNT | 2EAI:AI050503.PNT | 20HFC30CT016 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.1311 | ok
685 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050603.PNT | 2EAI:AI050603.PNT | 20HFC30CT017 | MSM C SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.0561 | ok
686 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090207.PNT | 2HAI:AI090207.PNT | 20HFC30CT018 | MSM C LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 38.6329 | ok
687 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090503.PNT | 2HAI:AI090503.PNT | 20HFC30CT019 | MSM C LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 28.9418 | ok
688 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141305.PNT | 2LAI:AI141305.PNT | 20HFC30CY001X | MSM C BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.66782 | ok
689 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141306.PNT | 2LAI:AI141306.PNT | 20HFC30CY001Y | MSM C BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.19031 | ok
690 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090603.PNT | 2HAI:AI090603.PNT | 20HFC30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 4.9836 | ok
691 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI091106.PNT | 2HAI:AI091106.PNT | 20HFC30GC003AI01 | MSM C OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -10.5117 | no
692 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2HAI.AI090601.PNT | 2HAI:AI090601.PNT | 20HFE30DP201 | MSM C DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 4.8036 | ok
693 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2E_MCHCAD.AO052701.OUT | 2E_MCHCAD:AO052701.OUT | 20HFE43AA101XB11 | MSM C INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 44.6342 | ok
694 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052201.PNT | 2EAI:AI052201.PNT | 20HFE43AA101XB12 | MSM C INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.8809 | ok
695 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2E_MCHCAD.AO052507.OUT | 2E_MCHCAD:AO052507.OUT | 20HFE53AA101XB11 | MSM C INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 42 | ok
696 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051607.PNT | 2EAI:AI051607.PNT | 20HFE53AA101XB12 | MSM C INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.3105 | ok
697 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2E_MCPAD.AO053103.OUT | 2E_MCPAD:AO053103.OUT | 20HFE53AA102XB11 | MSM C INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 96 | ok
698 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052206.PNT | 2EAI:AI052206.PNT | 20HFE53AA102XB12 | MSM C INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 94.5703 | ok
699 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMC1AIN.PNT | 2E_AIRFLOW:MSMC1AIN.PNT | 20HFE53CF201 | MSM C INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 81.9685 | ok
700 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMC2AIN.PNT | 2E_AIRFLOW:MSMC2AIN.PNT | 20HFE53CF202 | MSM C INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 82.6985 | ok
701 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050705.PNT | 2EAI:AI050705.PNT | 20HFE53CP201 | MSM C INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 6.0066 | ok
702 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 19 | MEDIUM SPEED MILL #2C | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050305.PNT | 2EAI:AI050305.PNT | 20HFE53CT001 | MSM C INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 230.8742 | ok
703 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140701.PNT | 2LAI:AI140701.PNT | 20HFF31CF201 | 1# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 17.9111 | ok
704 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI091101.PNT | 2HAI:AI091101.PNT | 20HHA31CB201B | 1# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.2969 | ok
705 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCC.AO062406.OUT | 2F_CYCC:AO062406.OUT | 20HLA11AA006XB11 | 1# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
706 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060706.PNT | 2FAI:AI060706.PNT | 20HLA11AA006XB12 | 1# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.0938 | ok
707 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXCC.AO062407.OUT | 2F_AUXCC:AO062407.OUT | 20HLA11AA007XB11 | 1#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 41 | ok
708 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 20 | COAL BURNER LAYER C1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060707.PNT | 2FAI:AI060707.PNT | 20HLA11AA007XB12 | 1# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 40.2285 | ok
709 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140702.PNT | 2LAI:AI140702.PNT | 20HFF32CF201 | 2# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 16.6457 | ok
710 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI091102.PNT | 2HAI:AI091102.PNT | 20HHA32CB201B | 2# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 100.7402 | ok
711 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCC.AO062605.OUT | 2F_CYCC:AO062605.OUT | 20HLA21AA006XB11 | 2# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
712 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061205.PNT | 2FAI:AI061205.PNT | 20HLA21AA006XB12 | 2# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.7129 | ok
713 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXCC.AO062606.OUT | 2F_AUXCC:AO062606.OUT | 20HLA21AA007XB11 | 2#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 41 | ok
714 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 21 | COAL BURNER LAYER C2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061206.PNT | 2FAI:AI061206.PNT | 20HLA21AA007XB12 | 2# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 41.4805 | ok
715 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140703.PNT | 2LAI:AI140703.PNT | 20HFF33CF201 | 3# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
716 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI091103.PNT | 2HAI:AI091103.PNT | 20HHA33CB201B | 3# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.2598 | ok
717 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCC.AO063104.OUT | 2F_CYCC:AO063104.OUT | 20HLA31AA006XB11 | 3# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
718 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061404.PNT | 2FAI:AI061404.PNT | 20HLA31AA006XB12 | 3# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 77.6523 | ok
719 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXCC.AO063105.OUT | 2F_AUXCC:AO063105.OUT | 20HLA31AA007XB11 | 3#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 41 | ok
720 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 22 | COAL BURNER LAYER C3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061405.PNT | 2FAI:AI061405.PNT | 20HLA31AA007XB12 | 3# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 40.332 | ok
721 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI140704.PNT | 2LAI:AI140704.PNT | 20HFF34CF201 | 4# CORNER C LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 2 | ok
722 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI091104.PNT | 2HAI:AI091104.PNT | 20HHA34CB201B | 4# CORNER C LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 101.0664 | ok
723 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCC.AO063303.OUT | 2F_CYCC:AO063303.OUT | 20HLA41AA006XB11 | 4# CORNER C LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
724 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061603.PNT | 2FAI:AI061603.PNT | 20HLA41AA006XB12 | 4# CORNER C LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.4629 | ok
725 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXCC.AO063304.OUT | 2F_AUXCC:AO063304.OUT | 20HLA41AA007XB11 | 4#CORNER CC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 41 | ok
726 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 23 | COAL BURNER LAYER C4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061604.PNT | 2FAI:AI061604.PNT | 20HLA41AA007XB12 | 4# CORNER CC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 40.5527 | ok
727 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 25 | COAL FEEDER #2D | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELC.LLAG4.OUT | 2E_FUELC.LLAG4.OUT | 20HFB40GC001AI01 | ECF D INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 0 | ok
728 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 25 | COAL FEEDER #2D | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELF.AOUT4.OUT | 2E_FUELF:AOUT4.OUT | 20HFB40GC001AO01 | ECF D FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
729 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090705.PNT | 2HAI:AI090705.PNT | 20HFC40AJ001XB13 | MSM D CURRENT | AI | 0 | 200 | A | [6 empty] | -0.15234 | no
730 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090301.PNT | 2HAI:AI090301.PNT | 20HFC40CT001 | MSM D MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 31.0593 | ok
731 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090401.PNT | 2HAI:AI090401.PNT | 20HFC40CT002 | MSM D MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 28.669 | ok
732 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090302.PNT | 2HAI:AI090302.PNT | 20HFC40CT003 | MSM D MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 35.0474 | ok
733 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090402.PNT | 2HAI:AI090402.PNT | 20HFC40CT004 | MSM D MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 35.606 | ok
734 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090303.PNT | 2HAI:AI090303.PNT | 20HFC40CT005 | MSM D MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 35.3462 | ok
735 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090403.PNT | 2HAI:AI090403.PNT | 20HFC40CT006 | MSM D MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 33.9172 | ok
736 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090304.PNT | 2HAI:AI090304.PNT | 20HFC40CT007 | MSM D MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 34.4369 | ok
737 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090404.PNT | 2HAI:AI090404.PNT | 20HFC40CT008 | MSM D MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 36.1387 | ok
738 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090305.PNT | 2HAI:AI090305.PNT | 20HFC40CT009 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 37.3858 | ok
739 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090405.PNT | 2HAI:AI090405.PNT | 20HFC40CT010 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 37.9833 | ok
740 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090504.PNT | 2HAI:AI090504.PNT | 20HFC40CT011 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 38.6589 | ok
741 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090505.PNT | 2HAI:AI090505.PNT | 20HFC40CT012 | MSM D PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 37.7885 | ok
742 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090306.PNT | 2HAI:AI090306.PNT | 20HFC40CT013 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 36.1516 | ok
743 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090406.PNT | 2HAI:AI090406.PNT | 20HFC40CT014 | MSM D PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 35.9178 | ok
744 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090307.PNT | 2HAI:AI090307.PNT | 20HFC40CT015 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.5212 | ok
745 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050504.PNT | 2EAI:AI050504.PNT | 20HFC40CT016 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.5861 | ok
746 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050604.PNT | 2EAI:AI050604.PNT | 20HFC40CT017 | MSM D SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 56.0795 | ok
747 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090407.PNT | 2HAI:AI090407.PNT | 20HFC40CT018 | MSM D LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 35.8529 | ok
748 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090506.PNT | 2HAI:AI090506.PNT | 20HFC40CT019 | MSM D LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 29.919 | ok
749 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141401.PNT | 2LAI:AI141401.PNT | 20HFC40CY001X | MSM D BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.045094 | ok
750 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141402.PNT | 2LAI:AI141402.PNT | 20HFC40CY001Y | MSM D BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | -0.0049687 | no
751 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090604.PNT | 2HAI:AI090604.PNT | 20HFC40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 0.13135 | ok
752 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-34 | OPC.AW2002.2HAI.AI090706.PNT | 2HAI:AI090706.PNT | 20HFC40GC003AI01 | MSM D OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | 7.9219 | ok
753 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2HAI.AI090602.PNT | 2HAI:AI090602.PNT | 20HFE40DP201 | MSM D DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | -0.0073242 | no
754 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2E_MDHCAD.AO052702.OUT | 2E_MDHCAD:AO052702.OUT | 20HFE44AA101XB11 | MSM D INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 55 | ok
755 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052202.PNT | 2EAI:AI052202.PNT | 20HFE44AA101XB12 | MSM D INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 55.0078 | ok
756 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2E_MDHCAD.AO052604.OUT | 2E_MDHCAD:AO052604.OUT | 20HFE54AA101XB11 | MSM D INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
757 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051704.PNT | 2EAI:AI051704.PNT | 20HFE54AA101XB12 | MSM D INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 0.03125 | ok
758 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2E_MDPAD.AO053104.OUT | 2E_MDPAD:AO053104.OUT | 20HFE54AA102XB11 | MSM D INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
759 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052207.PNT | 2EAI:AI052207.PNT | 20HFE54AA102XB12 | MSM D INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.12305 | no
760 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMD1AIN.PNT | 2E_AIRFLOW:MSMD1AIN.PNT | 20HFE54CF201 | MSM D INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 84.7673 | ok
761 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSMD2AIN.PNT | 2E_AIRFLOW:MSMD2AIN.PNT | 20HFE54CF202 | MSM D INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 83.9773 | ok
762 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050706.PNT | 2EAI:AI050706.PNT | 20HFE54CP201 | MSM D INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 2.9188 | ok
763 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 26 | MEDIUM SPEED MILL #2D | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050401.PNT | 2EAI:AI050401.PNT | 20HFE54CT001 | MSM D INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 55.8677 | ok
764 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141101.PNT | 2LAI:AI141101.PNT | 20HFF41CF201 | 1# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
765 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI090701.PNT | 2HAI:AI090701.PNT | 20HHA21CB201B | 1# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.16406 | no
766 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCB.AO062404.OUT | 2F_CYCB:AO062404.OUT | 20HLA11AA004XB11 | 1# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
767 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060704.PNT | 2FAI:AI060704.PNT | 20HLA11AA004XB12 | 1# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.8379 | ok
768 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXBC.AO062405.OUT | 2F_AUXBC:AO062405.OUT | 20HLA11AA005XB11 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
769 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 27 | COAL BURNER LAYER B1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060705.PNT | 2FAI:AI060705.PNT | 20HLA11AA005XB12 | 1# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.2891 | ok
770 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141102.PNT | 2LAI:AI141102.PNT | 20HFF42CF201 | 2# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
771 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI090702.PNT | 2HAI:AI090702.PNT | 20HHA22CB201B | 2# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.15625 | no
772 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCB.AO062603.OUT | 2F_CYCB:AO062603.OUT | 20HLA21AA004XB11 | 2# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
773 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061203.PNT | 2FAI:AI061203.PNT | 20HLA21AA004XB12 | 2# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | -0.089844 | no
774 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXBC.AO062604.OUT | 2F_AUXBC:AO062604.OUT | 20HLA21AA005XB11 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
775 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 28 | COAL BURNER LAYER B2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061204.PNT | 2FAI:AI061204.PNT | 20HLA21AA005XB12 | 2# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.5781 | ok
776 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141103.PNT | 2LAI:AI141103.PNT | 20HFF43CF201 | 3# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
777 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI090703.PNT | 2HAI:AI090703.PNT | 20HHA23CB201B | 3# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.21289 | no
778 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCB.AO063102.OUT | 2F_CYCB:AO063102.OUT | 20HLA31AA004XB11 | 3# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
779 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061402.PNT | 2FAI:AI061402.PNT | 20HLA31AA004XB12 | 3# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.8984 | ok
780 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXBC.AO063103.OUT | 2F_AUXBC:AO063103.OUT | 20HLA31AA005XB11 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
781 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 29 | COAL BURNER LAYER B3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061403.PNT | 2FAI:AI061403.PNT | 20HLA31AA005XB12 | 3# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.7793 | ok
782 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141104.PNT | 2LAI:AI141104.PNT | 20HFF44CF201 | 4# CORNER B LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
783 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-39 | OPC.AW2002.2HAI.AI090704.PNT | 2HAI:AI090704.PNT | 20HHA24CB201B | 4# CORNER B LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.1875 | no
784 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCB.AO063301.OUT | 2F_CYCB:AO063301.OUT | 20HLA41AA004XB11 | 4# CORNER B LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 10 | ok
785 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061601.PNT | 2FAI:AI061601.PNT | 20HLA41AA004XB12 | 4# CORNER B LAYER CYCLE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 9.6113 | ok
786 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXBC.AO063302.OUT | 2F_AUXBC:AO063302.OUT | 20HLA41AA005XB11 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
787 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 30 | COAL BURNER LAYER B4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061602.PNT | 2FAI:AI061602.PNT | 20HLA41AA005XB12 | 4# CORNER BC LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.5391 | ok
788 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 32 | COAL FEEDER #2E | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELC.LLAG5.OUT | 2E_FUELC.LLAG5.OUT | 20HFB50GC001AI01 | ECF E INSTANTANEOUS FEED RATE | AI | 0 | 55 | t/h | [6 empty] | 40.6647 | ok
789 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 32 | COAL FEEDER #2E | 50-F296S-J0201-03 | OPC.AW2002.2E_FUELF.AOUT5.OUT | 2E_FUELF:AOUT5.OUT | 20HFB50GC001AO01 | ECF E FEED RATE COMMAND | AO | 0 | 100 | % | [6 empty] | 74.0414 | ok
790 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100505.PNT | 2IAI:AI100505.PNT | 20HFC50AJ001XB13 | MSM E CURRENT | AI | 0 | 200 | A | [6 empty] | 41.3398 | ok
791 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100101.PNT | 2IAI:AI100101.PNT | 20HFC50CT001 | MSM E MOTOR FRONT BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 59.1583 | ok
792 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100201.PNT | 2IAI:AI100201.PNT | 20HFC50CT002 | MSM E MOTOR REAR BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 85 | 95 |  | 43.4784 | ok
793 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100102.PNT | 2IAI:AI100102.PNT | 20HFC50CT003 | MSM E MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 64.2507 | ok
794 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100202.PNT | 2IAI:AI100202.PNT | 20HFC50CT004 | MSM E MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 63.6791 | ok
795 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100103.PNT | 2IAI:AI100103.PNT | 20HFC50CT005 | MSM E MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 64.7833 | ok
796 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100203.PNT | 2IAI:AI100203.PNT | 20HFC50CT006 | MSM E MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.1603 | ok
797 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100104.PNT | 2IAI:AI100104.PNT | 20HFC50CT007 | MSM E MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 66.7059 | ok
798 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100204.PNT | 2IAI:AI100204.PNT | 20HFC50CT008 | MSM E MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 135 | 145 |  | 65.8355 | ok
799 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100105.PNT | 2IAI:AI100105.PNT | 20HFC50CT009 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.7377 | ok
800 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100205.PNT | 2IAI:AI100205.PNT | 20HFC50CT010 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 41.309 | ok
801 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100301.PNT | 2IAI:AI100301.PNT | 20HFC50CT011 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 42.0624 | ok
802 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100302.PNT | 2IAI:AI100302.PNT | 20HFC50CT012 | MSM E PLANETARY GEAR BOX BEARING TEMPERATURE 4 | RTD | 0 | 100 | ℃ |  |  |  | 75 | 80 |  | 42.0495 | ok
803 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100106.PNT | 2IAI:AI100106.PNT | 20HFC50CT013 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 52.7668 | ok
804 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100206.PNT | 2IAI:AI100206.PNT | 20HFC50CT014 | MSM E PLANETARY GEAR BOX DRIVE SHAFT BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 85 | 90 |  | 61.8084 | ok
805 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100107.PNT | 2IAI:AI100107.PNT | 20HFC50CT015 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.5988 | ok
806 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050505.PNT | 2EAI:AI050505.PNT | 20HFC50CT016 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.781 | ok
807 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2EAI.AI050605.PNT | 2EAI:AI050605.PNT | 20HFC50CT017 | MSM E SEPARATOR OUTLET MIXTURE TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  | 53 | 55 | 61 | 71 |  | 55.1182 | ok
808 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100207.PNT | 2IAI:AI100207.PNT | 20HFC50CT018 | MSM E LUBE OIL STATION OIL TANK OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 25 | 40 |  |  | 39.4903 | ok
809 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100303.PNT | 2IAI:AI100303.PNT | 20HFC50CT019 | MSM E LUBE OIL PUMP OUTLET OIL TEMPERATURE | RTD | 0 | 100 | ℃ |  |  | 30 |  |  |  | 33.7484 | ok
810 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141403.PNT | 2LAI:AI141403.PNT | 20HFC50CY001X | MSM E BEARING VIBRATING（X DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 1.2785 | ok
811 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2LAI.AI141404.PNT | 2LAI:AI141404.PNT | 20HFC50CY001Y | MSM E BEARING VIBRATING（Y DIRECTION） | AI | 0 | 20 | µm | [6 empty] | 0.21157 | ok
812 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100402.PNT | 2IAI:AI100402.PNT | 20HFC50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN INTLET AND OUTLET | AI | 0 | 5 | kPa | [6 empty] | 5.0896 | ok
813 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-34 | OPC.AW2002.2IAI.AI100506.PNT | 2IAI:AI100506.PNT | 20HFC50GC003AI01 | MSM E OUTLET CO CONTENT | AI | 0 | 20 | µm | [6 empty] | -7.3125 | no
814 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2E_MEHCAD.AO052703.OUT | 2E_MEHCAD:AO052703.OUT | 20HFE45AA101XB11 | MSM E INLET COLD AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 35.6876 | ok
815 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052203.PNT | 2EAI:AI052203.PNT | 20HFE45AA101XB12 | MSM E INLET COLD AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 35.7324 | ok
816 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2IAI.AI100401.PNT | 2IAI:AI100401.PNT | 20HFE50DP201 | MSM E DIFFERENTIAL PRESSURE BETWEEN SEALING AIR AND PRIMARY AIR | AI | 0 | 5 | KPa |  |  | 2.5 |  |  |  | 4.6657 | ok
817 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2E_MEHCAD.AO052605.OUT | 2E_MEHCAD:AO052605.OUT | 20HFE55AA101XB11 | MSM E INLET HOT AIR CONTROL DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
818 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052101.PNT | 2EAI:AI052101.PNT | 20HFE55AA101XB12 | MSM E INLET HOT AIR CONTROL DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.7656 | ok
819 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2E_MEPAD.AO053105.OUT | 2E_MEPAD:AO053105.OUT | 20HFE55AA102XB11 | MSM E INLET MIXED AIR CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 82 | ok
820 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052301.PNT | 2EAI:AI052301.PNT | 20HFE55AA102XB12 | MSM E INLET MIXED AIR CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 81.3281 | ok
821 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSME1AIN.PNT | 2E_AIRFLOW:MSME1AIN.PNT | 20HFE55CF201 | MSM E INLET PRIMARY AIR FLOW 1 | AI | 0 | 1200 | t/h | [6 empty] | 91.6055 | ok
822 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2E_AIRFLOW.MSME2AIN.PNT | 2E_AIRFLOW:MSME2AIN.PNT | 20HFE55CF202 | MSM E INLET PRIMARY AIR FLOW 2 | AI | 0 | 1200 | t/h | [6 empty] | 90.8355 | ok
823 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050707.PNT | 2EAI:AI050707.PNT | 20HFE55CP201 | MSM E INLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 5.3293 | ok
824 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 33 | MEDIUM SPEED MILL #2E | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050402.PNT | 2EAI:AI050402.PNT | 20HFE55CT001 | MSM E INLET PRIMARY AIR TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 263.1873 | ok
825 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141201.PNT | 2LAI:AI141201.PNT | 20HFF51CF201 | 1# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 10.4129 | ok
826 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063601.OUT | 2F_RHTEM:AO063601.OUT | 20HHA10KV001XB11 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
827 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW2002.2FAI.AI062202.PNT | 2FAI:AI062202.PNT | 20HHA10KV001XB12 | LOWER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 59.1504 | ok
828 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063602.OUT | 2F_RHTEM:AO063602.OUT | 20HHA10KV002XB11 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
829 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-33 | OPC.AW2002.2FAI.AI062203.PNT | 2FAI:AI062203.PNT | 20HHA10KV002XB12 | UPPER LAYER #1 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 58.6191 | ok
830 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-39 | OPC.AW2002.2IAI.AI100501.PNT | 2IAI:AI100501.PNT | 20HHA11CB201B | 1# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 97.4668 | ok
831 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAA.AO062401.OUT | 2F_AUXAA:AO062401.OUT | 20HLA11AA001XB11 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
832 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060701.PNT | 2FAI:AI060701.PNT | 20HLA11AA001XB12 | 1# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.3398 | ok
833 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCA.AO062402.OUT | 2F_CYCA:AO062402.OUT | 20HLA11AA002XB11 | 1# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
834 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060702.PNT | 2FAI:AI060702.PNT | 20HLA11AA002XB12 | 1# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.3711 | ok
835 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAB.AO062403.OUT | 2F_AUXAB:AO062403.OUT | 20HLA11AA003XB11 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
836 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 34 | COAL BURNER LAYER A1 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI060703.PNT | 2FAI:AI060703.PNT | 20HLA11AA003XB12 | 1# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.8008 | ok
837 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141202.PNT | 2LAI:AI141202.PNT | 20HFF52CF201 | 2# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 20.7035 | ok
838 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW2002.2IAI.AI100502.PNT | 2IAI:AI100502.PNT | 20HHA12CB201B | 2# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.2383 | ok
839 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063603.OUT | 2F_RHTEM:AO063603.OUT | 20HHA20KV001XB11 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
840 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW2002.2FAI.AI062204.PNT | 2FAI:AI062204.PNT | 20HHA20KV001XB12 | LOWER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 59.1523 | ok
841 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063604.OUT | 2F_RHTEM:AO063604.OUT | 20HHA20KV002XB11 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
842 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-39 | OPC.AW2002.2FAI.AI062205.PNT | 2FAI:AI062205.PNT | 20HHA20KV002XB12 | UPPER LAYER #2 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 58.7988 | ok
843 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAA.AO062507.OUT | 2F_AUXAA:AO062507.OUT | 20HLA21AA001XB11 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
844 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061107.PNT | 2FAI:AI061107.PNT | 20HLA21AA001XB12 | 2# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.6914 | ok
845 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCA.AO062601.OUT | 2F_CYCA:AO062601.OUT | 20HLA21AA002XB11 | 2# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
846 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061201.PNT | 2FAI:AI061201.PNT | 20HLA21AA002XB12 | 2# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 21.8398 | ok
847 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAB.AO062602.OUT | 2F_AUXAB:AO062602.OUT | 20HLA21AA003XB11 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
848 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 35 | COAL BURNER LAYER A2 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061202.PNT | 2FAI:AI061202.PNT | 20HLA21AA003XB12 | 2# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.5117 | ok
849 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141203.PNT | 2LAI:AI141203.PNT | 20HFF53CF201 | 3# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 13.8216 | ok
850 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW2002.2IAI.AI100503.PNT | 2IAI:AI100503.PNT | 20HHA13CB201B | 3# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 99.4434 | ok
851 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063605.OUT | 2F_RHTEM:AO063605.OUT | 20HHA30KV001XB11 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
852 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW2002.2FAI.AI062301.PNT | 2FAI:AI062301.PNT | 20HHA30KV001XB12 | LOWER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 59.0605 | ok
853 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063701.OUT | 2F_RHTEM:AO063701.OUT | 20HHA30KV002XB11 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
854 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-39 | OPC.AW2002.2FAI.AI062302.PNT | 2FAI:AI062302.PNT | 20HHA30KV002XB12 | UPPER LAYER #3 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 60.0078 | ok
855 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAA.AO062706.OUT | 2F_AUXAA:AO062706.OUT | 20HLA31AA001XB11 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
856 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061306.PNT | 2FAI:AI061306.PNT | 20HLA31AA001XB12 | 3# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 45.6094 | ok
857 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCA.AO062707.OUT | 2F_CYCA:AO062707.OUT | 20HLA31AA002XB11 | 3# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
858 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061307.PNT | 2FAI:AI061307.PNT | 20HLA31AA002XB12 | 3# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 79.1855 | ok
859 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAB.AO063101.OUT | 2F_AUXAB:AO063101.OUT | 20HLA31AA003XB11 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
860 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 36 | COAL BURNER LAYER A3 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061401.PNT | 2FAI:AI061401.PNT | 20HLA31AA003XB12 | 3# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 44.3398 | ok
861 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2LAI.AI141204.PNT | 2LAI:AI141204.PNT | 20HFF54CF201 | 4# CORNER A LAYER BURNER INLET PULVERIZED COAL FLOW | AI | 0 | 30 | t/h | [6 empty] | 10.32 | ok
862 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW2002.2IAI.AI100504.PNT | 2IAI:AI100504.PNT | 20HHA14CB201B | 4# CORNER A LAYER COAL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 98.2383 | ok
863 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063702.OUT | 2F_RHTEM:AO063702.OUT | 20HHA40KV001XB11 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
864 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW2002.2FAI.AI062303.PNT | 2FAI:AI062303.PNT | 20HHA40KV001XB12 | LOWER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 59.3848 | ok
865 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-33 | OPC.AW2002.2F_RHTEM.AO063703.OUT | 2F_RHTEM:AO063703.OUT | 20HHA40KV002XB11 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY COMMAND | AO | 0 | 100 | % | [6 empty] | 59 | ok
866 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-39 | OPC.AW2002.2FAI.AI062304.PNT | 2FAI:AI062304.PNT | 20HHA40KV002XB12 | UPPER LAYER #4 CORNER SWAY BURNER OBLIQUITY POSITION | AI | 0 | 100 | % | [6 empty] | 59.0723 | ok
867 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAA.AO063205.OUT | 2F_AUXAA:AO063205.OUT | 20HLA41AA001XB11 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
868 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061505.PNT | 2FAI:AI061505.PNT | 20HLA41AA001XB12 | 4# CORNER AA LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 45.0977 | ok
869 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2F_CYCA.AO063206.OUT | 2F_CYCA:AO063206.OUT | 20HLA41AA002XB11 | 4# CORNER A LAYER CYCLE AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 80 | ok
870 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061506.PNT | 2FAI:AI061506.PNT | 20HLA41AA002XB12 | 4# CORNER A LAYER CYCE AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 80.3066 | ok
871 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2F_AUXAB.AO063207.OUT | 2F_AUXAB:AO063207.OUT | 20HLA41AA003XB11 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 45 | ok
872 | 2 | UJPCT #2 | 5 | PULVERIZER SYSTEM#2 | 37 | COAL BURNER LAYER A4 | 50-F296S-J0201-03 | OPC.AW2002.2FAI.AI061507.PNT | 2FAI:AI061507.PNT | 20HLA41AA003XB12 | 4# CORNER AB LAYER AUXILIARY AIR DAMPER POSITION | AI | 0 | 100 | % | [6 empty] | 45.4238 | ok
873 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140106.PNT | 2LAI:AI140106.PNT | 20HNA10CP201 | A SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa | [6 empty] | -212.8711 | ok
874 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140206.PNT | 2LAI:AI140206.PNT | 20HNA20CP201 | B SIDE ECONOMIZER OUTLET FLUE GAS PRESSURE | AI | -3000 | 0 | Pa | [6 empty] | -319.1602 | ok
875 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141504.PNT | 2LAI:AI141504.PNT | 20HNA10CT001 | A SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 352.653 | ok
876 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 1 | ECONOMIZER #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141604.PNT | 2LAI:AI141604.PNT | 20HNA20CT001 | B SIDE ECONOMIZER OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 366.1064 | ok
877 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2M_DRUMLVL.LT160708.PNT | 2M_DRUMLVL:LT160708.PNT | 20HAG10CL201 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | -24.3732 | ok
878 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2M_DRUMLVL.LT161108.PNT | 2M_DRUMLVL:LT161108.PNT | 20HAG10CL202 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | 2.3286 | ok
879 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2M_DRUMLVL.LT161208.PNT | 2M_DRUMLVL:LT161208.PNT | 20HAG10CL203 | DRUM LEVEL | AI | -300 | 300 | mm | -300 | -250 | -100 | 100 | 250 | 300 | -3.0194 | ok
880 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2MAI.AI160707.PNT | 2MAI:AI160707.PNT | 20HAG10CP201 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 10.9224 | ok
881 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2MAI.AI161107.PNT | 2MAI:AI161107.PNT | 20HAG10CP202 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 16.5 | ok
882 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 2 | STEAM DRUM #2 | 50-F296S-J0201-04 | OPC.AW2002.2MAI.AI161207.PNT | 2MAI:AI161207.PNT | 20HAG10CP203 | DRUM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 10.9351 | ok
883 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154101.PNT | 2LAI:AI154101.PNT | 20HAG10CT001 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 319.605 | ok
884 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154102.PNT | 2LAI:AI154102.PNT | 20HAG10CT002 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 319.367 | ok
885 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154103.PNT | 2LAI:AI154103.PNT | 20HAG10CT003 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 317.7309 | ok
886 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154104.PNT | 2LAI:AI154104.PNT | 20HAG10CT004 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 319.1291 | ok
887 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154105.PNT | 2LAI:AI154105.PNT | 20HAG10CT005 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 315.946 | ok
888 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154106.PNT | 2LAI:AI154106.PNT | 20HAG10CT006 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 0 | no | OUT OFF RANGE
889 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154107.PNT | 2LAI:AI154107.PNT | 20HAG10CT007 | WALL TEMPERATURE OF BOILER DRUM WALL | TC | 0 | 600 | ℃ | [6 empty] | 313.5959 | ok
890 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154201.PNT | 2LAI:AI154201.PNT | 20HAG10CT008 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 315.2916 | ok
891 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154202.PNT | 2LAI:AI154202.PNT | 20HAG10CT009 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 315.0238 | ok
892 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154203.PNT | 2LAI:AI154203.PNT | 20HAG10CT010 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 314.5776 | ok
893 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154204.PNT | 2LAI:AI154204.PNT | 20HAG10CT011 | WALL TEMPERATURE OF CENTRALIZED DOWNCOMER | TC | 0 | 600 | ℃ | [6 empty] | 314.2801 | ok
894 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154205.PNT | 2LAI:AI154205.PNT | 20HAG10CT012 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 5th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 320.2892 | ok
895 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 3 | WALL TUBE #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154206.PNT | 2LAI:AI154206.PNT | 20HAG10CT013 | WALL TEMPERATURE OF SATURATED STEAM FROM LEFT 12th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 320.0512 | ok
896 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140305.PNT | 2LAI:AI140305.PNT | 20H10CP205 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -240.3008 | ok
897 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051707.PNT | 2EAI:AI051707.PNT | 20H10CQ201 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 3.6721 | ok
898 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI052105.PNT | 2EAI:AI052105.PNT | 20H10CQ202 | A SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 4.0279 | ok
899 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142208.PNT | 2LAI:AI142208.PNT | 20H10CT009 | A SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 376.0036 | ok
900 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140405.PNT | 2LAI:AI140405.PNT | 20H20CP205 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -281.4922 | ok
901 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI052304.PNT | 2EAI:AI052304.PNT | 20H20CQ201 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 3.3802 | ok
902 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI052401.PNT | 2EAI:AI052401.PNT | 20H20CQ202 | B SIDE LOW TEMPERATURE SUPERHEATER OUTLET FLUE GAS OXYGEN CONTENT | AI | 0 | 10 | % | [6 empty] | 3.7175 | ok
903 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154207.PNT | 2LAI:AI154207.PNT | 20HAH10CT001 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 476.7775 | ok
904 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154301.PNT | 2LAI:AI154301.PNT | 20HAH10CT002 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 478.1881 | ok
905 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154302.PNT | 2LAI:AI154302.PNT | 20HAH10CT003 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 487.1613 | ok
906 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154303.PNT | 2LAI:AI154303.PNT | 20HAH10CT004 | WALL TEMPERATURE OF BOILER LARGER PLATEN SUPERHEATER OUTLET HEADER | TC | 0 | 600 | ℃ | [6 empty] | 474.893 | ok
907 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154304.PNT | 2LAI:AI154304.PNT | 20HAH10CT005 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 4th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 516.3116 | ok
908 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154305.PNT | 2LAI:AI154305.PNT | 20HAH10CT006 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 7th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 524.7846 | ok
909 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154306.PNT | 2LAI:AI154306.PNT | 20HAH10CT007 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 10th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 532.7036 | ok
910 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154307.PNT | 2LAI:AI154307.PNT | 20HAH10CT008 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 12th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 522.637 | ok
911 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154401.PNT | 2LAI:AI154401.PNT | 20HAH10CT009 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FEOM LEFT 15th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 532.53 | ok
912 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154402.PNT | 2LAI:AI154402.PNT | 20HAH10CT010 | WALL TEMPERATURE OF REAR PLATEN SUPERHEATER OUTLET FROM LEFT 18th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 524.6453 | ok
913 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154403.PNT | 2LAI:AI154403.PNT | 20HAH10CT011 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 5th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 527.7861 | ok
914 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154404.PNT | 2LAI:AI154404.PNT | 20HAH10CT012 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 20th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 539.5319 | ok
915 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154405.PNT | 2LAI:AI154405.PNT | 20HAH10CT013 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 35th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 537.2666 | ok
916 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154406.PNT | 2LAI:AI154406.PNT | 20HAH10CT014 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 50th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 540.6499 | ok
917 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154407.PNT | 2LAI:AI154407.PNT | 20HAH10CT015 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 65th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 544.4156 | ok
918 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154501.PNT | 2LAI:AI154501.PNT | 20HAH10CT016 | WALL TEMPERATURE OF HIGH TEMPERATURE SUPERHEATER OUTLET FROM LEFT 80th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 545.1434 | ok
919 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154502.PNT | 2LAI:AI154502.PNT | 20HAH10CT017 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 4th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 475.5353 | ok
920 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154503.PNT | 2LAI:AI154503.PNT | 20HAH10CT018 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 46th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 465.2383 | ok
921 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154504.PNT | 2LAI:AI154504.PNT | 20HAH10CT019 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 67th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 468.3568 | ok
922 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154505.PNT | 2LAI:AI154505.PNT | 20HAH10CT020 | WALL TEMPERATURE OF LOW TEMPERATURE SUPERHEATER OUTLET FROM LEFT 109th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 612 | ok
923 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141701.PNT | 2LAI:AI141701.PNT | 20HAH11CT001 | SUPERHEATER 1st STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 487.9164 | ok
924 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060201.PNT | 2FAI:AI060201.PNT | 20HAH11CT002 | SUPERHEATER 1st STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 450.1593 | ok
925 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060301.PNT | 2FAI:AI060301.PNT | 20HAH11CT003 | SUPERHEATER 1st STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 446.644 | ok
926 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141702.PNT | 2LAI:AI141702.PNT | 20HAH21CT001 | SUPERHEATER 2nd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 479.3552 | ok
927 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060202.PNT | 2FAI:AI060202.PNT | 20HAH21CT002 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 423.3861 | ok
928 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060302.PNT | 2FAI:AI060302.PNT | 20HAH21CT003 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 422.7861 | ok
929 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141704.PNT | 2LAI:AI141704.PNT | 20HAH21CT004 | SUPERHEATER 3rd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 522.9852 | ok
930 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060204.PNT | 2FAI:AI060204.PNT | 20HAH21CT005 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 494.3613 | ok
931 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060303.PNT | 2FAI:AI060303.PNT | 20HAH21CT006 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 494.0326 | ok
932 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141703.PNT | 2LAI:AI141703.PNT | 20HAH22CT001 | SUPERHEATER 2nd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 473.8242 | ok
933 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060401.PNT | 2FAI:AI060401.PNT | 20HAH22CT002 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 441.9147 | ok
934 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060203.PNT | 2FAI:AI060203.PNT | 20HAH22CT003 | SUPERHEATER 2nd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 438.3494 | ok
935 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141705.PNT | 2LAI:AI141705.PNT | 20HAH22CT004 | SUPERHEATER 3rd STAGE DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 524.015 | ok
936 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060402.PNT | 2FAI:AI060402.PNT | 20HAH22CT005 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 497.3283 | ok
937 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060205.PNT | 2FAI:AI060205.PNT | 20HAH22CT006 | SUPERHEATER 3rd STAGE DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | ℃ | [6 empty] | 496.1264 | ok
938 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI140507.PNT | 2LAI:AI140507.PNT | 20LAE40CP201 | SUPERHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 11.5005 | ok
939 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI142104.PNT | 2LAI:AI142104.PNT | 20LAE40CT001 | SUPERHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃ | [6 empty] | 152.4422 | ok
940 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_SH1.AO063502.OUT | 2F_SH1:AO063502.OUT | 20LAE41AA101XB11 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 31.2916 | ok
941 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI061706.PNT | 2FAI:AI061706.PNT | 20LAE41AA101XB12 | 1st STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 31.6465 | ok
942 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.1SHCALCA.RO01 | 2F_FLOW:1SHCALCA.RO01 | 20LAE41CF201 | 1st STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 23.5352 | ok
943 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_SH2A.AO063406.OUT | 2F_SH2A:AO063406.OUT | 20LAE42AA101XB11 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 42.9826 | ok
944 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI062102.PNT | 2FAI:AI062102.PNT | 20LAE42AA101XB12 | A SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 42.7305 | ok
945 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.2SHACALCA.RO01 | 2F_FLOW:2SHACALCA.RO01 | 20LAE42CF201 | A SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 16.2286 | ok
946 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_SH2B.AO063503.OUT | 2F_SH2B:AO063503.OUT | 20LAE43AA101XB11 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 29.1795 | ok
947 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI061707.PNT | 2FAI:AI061707.PNT | 20LAE43AA101XB12 | B SIDE 2nd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 29.1172 | ok
948 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.2SHBCALCA.RO01 | 2F_FLOW:2SHBCALCA.RO01 | 20LAE43CF201 | B SIDE 2nd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 10.3113 | ok
949 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_SH3A.AO063407.OUT | 2F_SH3A:AO063407.OUT | 20LAE44AA101XB11 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 28.2283 | ok
950 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI062103.PNT | 2FAI:AI062103.PNT | 20LAE44AA101XB12 | A SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 28.7227 | ok
951 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.3SHACALCA.RO01 | 2F_FLOW:3SHACALCA.RO01 | 20LAE44CF201 | A SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 7.8869 | ok
952 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_SH3B.AO063504.OUT | 2F_SH3B:AO063504.OUT | 20LAE45AA101XB11 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 30.3817 | ok
953 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI062104.PNT | 2FAI:AI062104.PNT | 20LAE45AA101XB12 | B SIDE 3rd STAGE SUPERHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 30.2188 | ok
954 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.3SHBCALCA.RO01 | 2F_FLOW:3SHBCALCA.RO01 | 20LAE45CF201 | B SIDE 3rd STAGE SUPERHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 8.5134 | ok
955 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI140307.PNT | 2LAI:AI140307.PNT | 20LBA10CP201 | SUPERHEATED STEAM PRESSURE | AI | 0 | 20 | MPa |  |  | 0 | 17.41 |  |  | 10.1704 | ok
956 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160401.PNT | 2MAI:AI160401.PNT | 20LBA10CP202 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 9.9956 | ok
957 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160501.PNT | 2MAI:AI160501.PNT | 20LBA10CP203 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 9.9941 | ok
958 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160601.PNT | 2MAI:AI160601.PNT | 20LBA10CP204 | SUPERHEATED STEAM PRESSURE | AI | 0 | 25 | MPa | [6 empty] | 10.0068 | ok
959 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060206.PNT | 2FAI:AI060206.PNT | 20LBA10CT001 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 538.1967 | ok
960 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060304.PNT | 2FAI:AI060304.PNT | 20LBA10CT002 | SUPERHATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 538.9863 | ok
961 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2M_MSTFLOW_1.SIGSEL1OUT.PNT | 2M_MSTFLOW_1:SIGSEL1OUT.PNT | 20LBA10CP101C1 | MAIN STEAM PRESSURE SIGSEL | AI | 0 | 20 | MPa | [6 empty] | 9.9966 | ok
962 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2M_MSTFLOW.SWCH2OUT.PNT | 2M_MSTFLOW:SWCH2OUT.PNT | 20LBA10CF101C1 | MAIN STEAM FLOW | AI | 0 | 1000 | t/h | [6 empty] | 589.7016 | ok
963 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2F_SH3A_2.SIGSEL1OUT.PNT | 2F_SH3A_2:SIGSEL1OUT.PNT | 20LBA10CT001C1 | MAIN STEAM TEMPERATURE SIGSEL | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 538.6062 | ok
964 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154605.PNT | 2LAI:AI154605.PNT | 20HAJ10CT001 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 3th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 485.3688 | ok
965 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154606.PNT | 2LAI:AI154606.PNT | 20HAJ10CT002 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 9th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 510.6113 | ok
966 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154607.PNT | 2LAI:AI154607.PNT | 20HAJ10CT003 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 16th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 523.7621 | ok
967 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154701.PNT | 2LAI:AI154701.PNT | 20HAJ10CT004 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 22th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 548.2863 | ok
968 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154702.PNT | 2LAI:AI154702.PNT | 20HAJ10CT005 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 28th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 562.6139 | ok
969 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154703.PNT | 2LAI:AI154703.PNT | 20HAJ10CT006 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 37th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 548.404 | ok
970 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154704.PNT | 2LAI:AI154704.PNT | 20HAJ10CT007 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 43th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 537.6951 | ok
971 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154705.PNT | 2LAI:AI154705.PNT | 20HAJ10CT008 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 49th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 523.0732 | ok
972 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154706.PNT | 2LAI:AI154706.PNT | 20HAJ10CT009 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 56th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 570.2632 | ok
973 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154707.PNT | 2LAI:AI154707.PNT | 20HAJ10CT010 | WALL TEMPERATURE OF BOILER HIGH TEMPERATURE REHEATER OUTLET FROM LEFT 62th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 545.7268 | ok
974 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141708.PNT | 2LAI:AI141708.PNT | 20HAJ21CT001 | REHEATER DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 390.6912 | ok
975 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060307.PNT | 2FAI:AI060307.PNT | 20HAJ21CT002 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 248.0628 | ok
976 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060404.PNT | 2FAI:AI060404.PNT | 20HAJ21CT003 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 251.7602 | ok
977 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI142101.PNT | 2LAI:AI142101.PNT | 20HAJ22CT001 | REHEATER DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 371.9747 | ok
978 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060405.PNT | 2FAI:AI060405.PNT | 20HAJ22CT002 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 235.9288 | ok
979 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060406.PNT | 2FAI:AI060406.PNT | 20HAJ22CT003 | REHEATER DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 600 | °C | [6 empty] | 244.5531 | ok
980 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154506.PNT | 2LAI:AI154506.PNT | 20HAK10CT001 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 3th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 448.1989 | ok
981 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154507.PNT | 2LAI:AI154507.PNT | 20HAK10CT002 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 8th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 466.0914 | ok
982 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154601.PNT | 2LAI:AI154601.PNT | 20HAK10CT003 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 13th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 490.7233 | ok
983 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154602.PNT | 2LAI:AI154602.PNT | 20HAK10CT004 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 17th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 497.0781 | ok
984 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154603.PNT | 2LAI:AI154603.PNT | 20HAK10CT005 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 22th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 493.5771 | ok
985 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-16 | OPC.AW2002.2LAI.AI154604.PNT | 2LAI:AI154604.PNT | 20HAK10CT006 | WALL TEMPERATURE OF BOILER INTERMEDIATE TEMPERATURE REHEATER OUTLET FROM LEFT 28th TUBE | TC | 0 | 600 | ℃ | [6 empty] | 502.1089 | ok
986 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI140506.PNT | 2LAI:AI140506.PNT | 20LAF60CP201 | REHEATED STEAM DESUPERHEATING WATER PRESSURE | AI | 0 | 12 | MPa | [6 empty] | 6.0499 | ok
987 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2LAI.AI142103.PNT | 2LAI:AI142103.PNT | 20LAF60CT001 | REHEATED STEAM DESUPERHEATING WATER TEMPERATURE | TC | 0 | 200 | ℃ | [6 empty] | 151.6034 | ok
988 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_RHEMG.AO063404.OUT | 2F_RHEMG:AO063404.OUT | 20LAF61AA101XB11 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
989 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI061704.PNT | 2FAI:AI061704.PNT | 20LAF61AA101XB12 | REHEATED STEAM EMERGENCY SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.26562 | no
990 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.RHCALCA.RO01 | 2F_FLOW:RHCALCA.RO01 | 20LAF61CF201 | REHEATER EMERGENCY DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 9.1036 | ok
991 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_RHA.AO063405.OUT | 2F_RHA:AO063405.OUT | 20LAF62AA101XB11 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 23.8496 | ok
992 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI061705.PNT | 2FAI:AI061705.PNT | 20LAF62AA101XB12 | A SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 24.0547 | ok
993 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.RHACALCA.RO01 | 2F_FLOW:RHACALCA.RO01 | 20LAF62CF201 | A SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 19.6748 | ok
994 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_RHB.AO063501.OUT | 2F_RHB:AO063501.OUT | 20LAF63AA101XB11 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 17.6088 | ok
995 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2FAI.AI062101.PNT | 2FAI:AI062101.PNT | 20LAF63AA101XB12 | B SIDE REHEATED STEAM SPRAYING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 17.7305 | ok
996 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-08 | OPC.AW2002.2F_FLOW.RHBCALCA.RO01 | 2F_FLOW:RHBCALCA.RO01 | 20LAF63CF201 | B SIDE REHEATED STEAM DESUPERHEATING WATER FLOW | AI | 0 | 100 | t/h | [6 empty] | 15.9809 | ok
997 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI140505.PNT | 2LAI:AI140505.PNT | 20LBB10CP201 | REHEATED STEAM PRESSURE | AI | 0 | 6 | MPa |  |  | 0 |  |  |  | 2.2876 | ok
998 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI142102.PNT | 2LAI:AI142102.PNT | 20LBB10CT001 | REHEATED STEAM TEMPERATURE | TC | 0 | 600 | ℃ |  |  | 520 | 545 |  |  | 541.3677 | ok
999 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI140406.PNT | 2LAI:AI140406.PNT | 20LBC21CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa | [6 empty] | 1.4352 | ok
1000 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141706.PNT | 2LAI:AI141706.PNT | 20LBC21CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 358.2362 | ok
1001 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060207.PNT | 2FAI:AI060207.PNT | 20LBC21CT002 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 334.9453 | ok
1002 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060305.PNT | 2FAI:AI060305.PNT | 20LBC21CT003 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 335.684 | ok
1003 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI140407.PNT | 2LAI:AI140407.PNT | 20LBC22CP201 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM PRESSURE | AI | 0 | 6 | MPa | [6 empty] | 1.4371 | ok
1004 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2LAI.AI141707.PNT | 2LAI:AI141707.PNT | 20LBC22CT001 | REHEATER EMERGENCY DESUPERHEATER INLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 358.2957 | ok
1005 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060403.PNT | 2FAI:AI060403.PNT | 20LBC22CT002 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 333.9593 | ok
1006 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2FAI.AI060306.PNT | 2FAI:AI060306.PNT | 20LBC22CT003 | REHEATER EMERGENCY DESUPERHEATER OUTLET STEAM TEMPERATURE | TC | 0 | 400 | ℃ | [6 empty] | 333.8744 | ok
1007 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2PMS.RSFLOW.RO01 | 2PMS:RSFLOW.RO01 | 20LBB10CF101C1 | RH STEAM OUTLET FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | 574.1434 | ok
1008 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 5 | REHEATER #2 | 50-F296S-J0201-04 | OPC.AW2002.2PMS.RSFLOW.RO02 | 2PMS:RSFLOW.RO02 | 20LBB10CF101C2 | RH STM FLOW | AI | 0 | 1000 | t/h |  |  | 0 |  |  |  | 529.3841 | ok
1009 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOT BLOWER #2 | K0601-02 | OPC.AW2002.2EAI.AI052106.PNT | 2EAI:AI052106.PNT | 20HCB10AA101XB12 | BOILER SOOTBLOWER STEAM PRESSURE POSITION | AI | 0 | 100 | % | [6 empty] | 1.707 | ok
1010 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOT BLOWER #2 | K0601-02 | OPC.AW2002.2EAI.AI051405.PNT | 2EAI:AI051405.PNT | 20HCB10CP201 | BOILER SOOTBLOWER STEAM PRESSURE | AI | 0 | 20 | MPa | [6 empty] | 0.026758 | ok
1011 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 6 | SOOT BLOWER #2 | K0601-02 | OPC.AW2002.2E_BLCV.AO053106.OUT | 2E_BLCV:AO053106.OUT | 20HCB10AA101XB11 | BOILER SOOTBLOWER STEAM PRESSURE CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1012 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051402.PNT | 2EAI:AI051402.PNT | 20H10CP201 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -40.5703 | ok
1013 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051306.PNT | 2EAI:AI051306.PNT | 20H10CP202 | A SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -46.3008 | ok
1014 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140303.PNT | 2LAI:AI140303.PNT | 20H10CP203 | A SIDE FURNACE PRESSURE | AI | -2000 | 2000 | Pa | [6 empty] | 34.6351 | ok
1015 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140304.PNT | 2LAI:AI140304.PNT | 20H10CP204 | A SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa | [6 empty] | -54.9453 | ok
1016 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142201.PNT | 2LAI:AI142201.PNT | 20H10CT002 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 833.8675 | ok
1017 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142202.PNT | 2LAI:AI142202.PNT | 20H10CT003 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 739.9613 | ok
1018 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142203.PNT | 2LAI:AI142203.PNT | 20H10CT004 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 614.2543 | ok
1019 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142204.PNT | 2LAI:AI142204.PNT | 20H10CT005 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 578.9501 | ok
1020 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142205.PNT | 2LAI:AI142205.PNT | 20H10CT006 | A SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 1000 | ℃ | [6 empty] | 577.6556 | ok
1021 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142206.PNT | 2LAI:AI142206.PNT | 20H10CT007 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 526.9059 | ok
1022 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142207.PNT | 2LAI:AI142207.PNT | 20H10CT008 | A SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 521.0807 | ok
1023 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051307.PNT | 2EAI:AI051307.PNT | 20H10DP201 | A SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 468.6562 | ok
1024 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051401.PNT | 2EAI:AI051401.PNT | 20H10DP202 | A SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 486.5 | ok
1025 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2JAI.AI112703.PNT | 2JAI:AI112703.PNT | 20H10GC001AI01 | A SIDE PROBE POSITION SIGNAL | AI | 0 | 100 | % | [6 empty] | 100.627 | no
1026 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2JAI.AI112704.PNT | 2JAI:AI112704.PNT | 20H10GC001AI02 | A SIDE PROBE TEMPERATURE SIGNAL | AI | 0 | 800 | C |  |  |  | 540 | 560 |  | 48 | ok
1027 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051207.PNT | 2EAI:AI051207.PNT | 20H20CP201 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -48.5156 | ok
1028 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051502.PNT | 2EAI:AI051502.PNT | 20H20CP202 | B SIDE FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -48.0586 | ok
1029 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140403.PNT | 2LAI:AI140403.PNT | 20H20CP203 | B SIDE FURNACE PRESSURE | AI | -2000 | 2000 | Pa | [6 empty] | 49.375 | ok
1030 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI140404.PNT | 2LAI:AI140404.PNT | 20H20CP204 | B SIDE FURNACE CAVITY CHAMFER PRESSURE | AI | -300 | 0 | Pa | [6 empty] | 89.8047 | no
1031 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142301.PNT | 2LAI:AI142301.PNT | 20H20CT002 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 748.8388 | ok
1032 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142302.PNT | 2LAI:AI142302.PNT | 20H20CT003 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 828.1177 | ok
1033 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142303.PNT | 2LAI:AI142303.PNT | 20H20CT004 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 676.8876 | ok
1034 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142304.PNT | 2LAI:AI142304.PNT | 20H20CT005 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 613.5167 | ok
1035 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142305.PNT | 2LAI:AI142305.PNT | 20H20CT006 | B SIDE FURNACE HORIZONTAL GAS DUCT GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 612.075 | ok
1036 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142306.PNT | 2LAI:AI142306.PNT | 20H20CT007 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 533.5233 | ok
1037 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142307.PNT | 2LAI:AI142307.PNT | 20H20CT008 | B SIDE FURNACE CAVITY CHAMFER GAS TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 533.4888 | ok
1038 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2LAI.AI142308.PNT | 2LAI:AI142308.PNT | 20H20CT009 | B SIDE FURNACE LOW TEMPERATURE SUPERHEATER OUTLET TEMPERATURE | TC | 0 | 700 | ℃ | [6 empty] | 378.8275 | ok
1039 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051403.PNT | 2EAI:AI051403.PNT | 20H20DP201 | B SIDE DIFFERENTIAL PRESSURE 1 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 440.375 | ok
1040 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2EAI.AI051501.PNT | 2EAI:AI051501.PNT | 20H20DP202 | B SIDE DIFFERENTIAL PRESSURE 2 BETWEEN AIR BOX AND FURNACE | AI | 0 | 1600 | Pa | [6 empty] | 459.875 | ok
1041 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2JAI.AI112705.PNT | 2JAI:AI112705.PNT | 20H20GC001AI01 | B SIDE PROBE POSITION SIGNAL | AI | 0 | 100 | % | [6 empty] | 84.8828 | ok
1042 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2JAI.AI112706.PNT | 2JAI:AI112706.PNT | 20H20GC001AI02 | B SIDE PROBE TEMPERATURE SIGNAL | AI | 0 | 800 | C |  |  |  | 540 | 560 |  | 34.9375 | ok
1043 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051105.PNT | 2EAI:AI051105.PNT | 20HLA10CF201 | FURNACE A-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | 70.7506 | ok
1044 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051202.PNT | 2EAI:AI051202.PNT | 20HLA10CF202 | FURNACE A-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h | [6 empty] | 72.664 | ok
1045 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051106.PNT | 2EAI:AI051106.PNT | 20HLA20CF201 | FURNACE B-SIDE BELLOWS AIR FLOW 1 | AI | 0 | 263 | t/h | [6 empty] | 50.6121 | ok
1046 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051203.PNT | 2EAI:AI051203.PNT | 20HLA20CF202 | FURNACE B-SIDE BELLOWS AIR FLOW 2 | AI | 0 | 263 | t/h | [6 empty] | 51.055 | ok
1047 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_PAF.AO052502.OUT | 2E_PAF:AO052502.OUT | 20HFE10AA101XB11 | PAF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 44.0712 | ok
1048 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051602.PNT | 2EAI:AI051602.PNT | 20HFE10AA101XB12 | PAF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 43.6484 | ok
1049 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2JAI.AI111102.PNT | 2JAI:AI111102.PNT | 20HFE10AN001XB13 | PAF A CURRENT | AI | 0 | 300 | A | [6 empty] | 150.3398 | ok
1050 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140103.PNT | 2LAI:AI140103.PNT | 20HFE10CP201 | PAF A OUTLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.3406 | ok
1051 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141502.PNT | 2LAI:AI141502.PNT | 20HFE10CT001 | PAF A INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 25.0316 | ok
1052 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111407.PNT | 2JAI:AI111407.PNT | 20HFE10CT006 | PAF A MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 60.2885 | ok
1053 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111507.PNT | 2JAI:AI111507.PNT | 20HFE10CT007 | PAF A MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 59.2882 | ok
1054 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111603.PNT | 2JAI:AI111603.PNT | 20HFE10CT008 | PAF A MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 58.9634 | ok
1055 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111701.PNT | 2JAI:AI111701.PNT | 20HFE10CT009 | PAF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 61.5876 | ok
1056 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI112101.PNT | 2JAI:AI112101.PNT | 20HFE10CT010 | PAF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 65.7316 | ok
1057 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111702.PNT | 2JAI:AI111702.PNT | 20HFE10CT011 | PAF A NON DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 61.7045 | ok
1058 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI112102.PNT | 2JAI:AI112102.PNT | 20HFE10CT012 | PAF A DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 45.1672 | ok
1059 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111205.PNT | 2JAI:AI111205.PNT | 20HFE10CY001X | PAF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.2188 | ok
1060 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111301.PNT | 2JAI:AI111301.PNT | 20HFE10CY001Y | PAF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.79808 | ok
1061 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111206.PNT | 2JAI:AI111206.PNT | 20HFE10CY002X | PAF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.3225 | ok
1062 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 1 | PAF #2A | 50-F296S-J0201-36 | OPC.AW2002.2JAI.AI111302.PNT | 2JAI:AI111302.PNT | 20HFE10CY002Y | PAF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.94601 | ok
1063 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140101.PNT | 2LAI:AI140101.PNT | 20HLA10CP201 | FDF A OUTLET AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.62344 | ok
1064 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141501.PNT | 2LAI:AI141501.PNT | 20HLA10CT001 | FDF A INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 24.3427 | ok
1065 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_FDF.AO052501.OUT | 2E_FDF:AO052501.OUT | 20HLB10AA101XB11 | FDF A INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 12 | ok
1066 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051601.PNT | 2EAI:AI051601.PNT | 20HLB10AA101XB12 | FDF A INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 11.8613 | ok
1067 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2JAI.AI111101.PNT | 2JAI:AI111101.PNT | 20HLB10AN001XB13 | FDF A CURRENT | AI | 0 | 200 | A | [6 empty] | 16.6211 | ok
1068 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111401.PNT | 2JAI:AI111401.PNT | 20HLB10CT001 | FDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 45.492 | ok
1069 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111501.PNT | 2JAI:AI111501.PNT | 20HLB10CT002 | FDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 44.3618 | ok
1070 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111402.PNT | 2JAI:AI111402.PNT | 20HLB10CT003 | FDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 44.1929 | ok
1071 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111502.PNT | 2JAI:AI111502.PNT | 20HLB10CT004 | FDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 43.1407 | ok
1072 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111403.PNT | 2JAI:AI111403.PNT | 20HLB10CT005 | FDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 44.076 | ok
1073 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111503.PNT | 2JAI:AI111503.PNT | 20HLB10CT006 | FDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 44.4657 | ok
1074 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111404.PNT | 2JAI:AI111404.PNT | 20HLB10CT007 | FDF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 58.6257 | ok
1075 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111504.PNT | 2JAI:AI111504.PNT | 20HLB10CT008 | FDF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 53.0137 | ok
1076 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111405.PNT | 2JAI:AI111405.PNT | 20HLB10CT009 | FDF A NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 40.6075 | ok
1077 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111505.PNT | 2JAI:AI111505.PNT | 20HLB10CT010 | FDF A NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 39.906 | ok
1078 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111601.PNT | 2JAI:AI111601.PNT | 20HLB10CT011 | FDF A NON DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 40.7114 | ok
1079 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111406.PNT | 2JAI:AI111406.PNT | 20HLB10CT012 | FDF A DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 48.5059 | ok
1080 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111506.PNT | 2JAI:AI111506.PNT | 20HLB10CT013 | FDF A DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 47.1938 | ok
1081 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111602.PNT | 2JAI:AI111602.PNT | 20HLB10CT014 | FDF A DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 48.5708 | ok
1082 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111106.PNT | 2JAI:AI111106.PNT | 20HLB10CY001X | FDF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.2773 | ok
1083 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111203.PNT | 2JAI:AI111203.PNT | 20HLB10CY001Y | FDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.9516 | ok
1084 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111107.PNT | 2JAI:AI111107.PNT | 20HLB10CY002X | FDF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.4456 | ok
1085 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 2 | FDF #2A | 50-F296S-J0201-35 | OPC.AW2002.2JAI.AI111204.PNT | 2JAI:AI111204.PNT | 20HLB10CY002Y | FDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.91377 | ok
1086 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140104.PNT | 2LAI:AI140104.PNT | 20HFE10CP202 | APH A INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.6105 | ok
1087 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140105.PNT | 2LAI:AI140105.PNT | 20HFE10CP203 | APH A OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 9.6074 | ok
1088 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050105.PNT | 2EAI:AI050105.PNT | 20HFE10CT002 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.4307 | ok
1089 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050203.PNT | 2EAI:AI050203.PNT | 20HFE10CT003 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.824 | ok
1090 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050303.PNT | 2EAI:AI050303.PNT | 20HFE10CT004 | APH A INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 41.5832 | ok
1091 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141503.PNT | 2LAI:AI141503.PNT | 20HFE10CT005 | APH A OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 322.1911 | ok
1092 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140102.PNT | 2LAI:AI140102.PNT | 20HLA10CP202 | APH A INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.63789 | ok
1093 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050701.PNT | 2EAI:AI050701.PNT | 20HLA10CP203 | APH A OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.50527 | ok
1094 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050101.PNT | 2EAI:AI050101.PNT | 20HLA10CT002 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 27.135 | ok
1095 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050201.PNT | 2EAI:AI050201.PNT | 20HLA10CT003 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 27.8552 | ok
1096 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050301.PNT | 2EAI:AI050301.PNT | 20HLA10CT004 | APH A INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 27.2006 | ok
1097 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050102.PNT | 2EAI:AI050102.PNT | 20HLA10CT005 | APH A OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 328.0268 | ok
1098 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAI.AI111104.PNT | 2JAI:AI111104.PNT | 20HLD11GC001AI01 | AIR PREHEATER A MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 8.5996 | ok
1099 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAI.AI111201.PNT | 2JAI:AI111201.PNT | 20HLD11GC001AI02 | AIR PREHEATER A AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 0.23047 | ok
1100 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAI.AI111105.PNT | 2JAI:AI111105.PNT | 20HLD11GC001AI03 | AIR PREHEATER A MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 988.3201 | ok
1101 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAI.AI111202.PNT | 2JAI:AI111202.PNT | 20HLD11GC001AI04 | AIR PREHEATER A AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 14.2279 | ok
1102 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAH.AO112601.OUT | 2JAH:AO112601.OUT | 20HLD11GC001AO01 | AIR PREHEATER A MAIN MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | 0 | ok
1103 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-38 | OPC.AW2002.2JAH.AO112602.OUT | 2JAH:AO112602.OUT | 20HLD11GC001AO02 | AIR PREHEATER A AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | 0 | ok
1104 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140107.PNT | 2LAI:AI140107.PNT | 20HNA10CP202 | APH A OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa | [6 empty] | -1428.6426 | ok
1105 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050206.PNT | 2EAI:AI050206.PNT | 20HNA10CT002 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 182.161 | ok
1106 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050306.PNT | 2EAI:AI050306.PNT | 20HNA10CT003 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 173.7453 | ok
1107 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050403.PNT | 2EAI:AI050403.PNT | 20HNA10CT004 | APH A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 163.8408 | ok
1108 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141507.PNT | 2LAI:AI141507.PNT | 20LCN10CT001 | STEAM AIR HEATER DRAIN WATER TEMP. | TC | 0 | 400 | ℃ | [6 empty] | 27.9125 | ok
1109 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | F296S-J0201-06 | OPC.AW2002.2M_GLDSED.AO162403.OUT | 2M_GLDSED:AO162403.OUT | 20LBG41AA101XB11 | AUXILIARY STEAM TO SECONDARY AIR HEATER CONTRL VALVE CONTROL SIGNAL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1110 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | F296S-J0201-06 | OPC.AW2002.2MAI.AI161403.PNT | 2MAI:AI161403.PNT | 20LBG41AA101XB12 | AUXILIARY STEAM TO SECONDARY AIR HEATER CONTRL VALVE POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0 | ok | TIDAK DIOPERASIKAN
1111 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | F296S-J0201-06 | OPC.AW2002.2M_GLDPRI.AO162404.OUT | 2M_GLDPRI:AO162404.OUT | 20LBG42AA101XB11 | AUXILIARY STEAM TO PRIMARY AIR HEATER CONTRL VALVE CONTROL SIGNAL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1112 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 4 | AIR HEATER #2A | F296S-J0201-06 | OPC.AW2002.2MAI.AI161404.PNT | 2MAI:AI161404.PNT | 20LBG42AA101XB12 | AUXILIARY STEAM TO PRIMARY AIR HEATER CONTRL VALVE POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0 | ok | TIDAK DIOPERASIKAN
1113 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050702.PNT | 2EAI:AI050702.PNT | 20HFE50CP201 | PRIMARY HOT AIR HEADER PRESSURE 1 | AI | 0 | 20 | KPa | [6 empty] | 9.1164 | ok
1114 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051102.PNT | 2EAI:AI051102.PNT | 20HFE50CP202 | PRIMARY HOT AIR HEADER PRESSURE 2 | AI | 0 | 20 | KPa | [6 empty] | 9.0938 | ok
1115 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 5 | DUCTING HOT AIR #2 | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051201.PNT | 2EAI:AI051201.PNT | 20HFE50CP203 | PRIMARY HOT AIR HEADER PRESSURE 3 | AI | 0 | 20 | KPa | [6 empty] | 9.0281 | ok
1116 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2E_PAF.AO053205.OUT | 2E_PAF:AO053205.OUT | 20HFE20AA101XB11 | PAF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 43.5712 | ok
1117 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051702.PNT | 2EAI:AI051702.PNT | 20HFE20AA101XB12 | PAF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 43.6875 | ok
1118 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2KAI.AI131102.PNT | 2KAI:AI131102.PNT | 20HFE20AN001XB13 | PAF B CURRENT | AI | 0 | 300 | A | [6 empty] | 150.1875 | ok
1119 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140203.PNT | 2LAI:AI140203.PNT | 20HFE20CP201 | PAF B OUTLET AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 1.9965 | ok
1120 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141602.PNT | 2LAI:AI141602.PNT | 20HFE20CT001 | PAF B INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 23.411 | ok
1121 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2KAI.AI131407.PNT | 2KAI:AI131407.PNT | 20HFE20CT006 | PAF B MOTOR STATOR U TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 61.8344 | ok
1122 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2KAI.AI131507.PNT | 2KAI:AI131507.PNT | 20HFE20CT007 | PAF B MOTOR STATOR V TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 61.2628 | ok
1123 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2KAI.AI131603.PNT | 2KAI:AI131603.PNT | 20HFE20CT008 | PAF B MOTOR STATOR W TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 60.7951 | ok
1124 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-03 | OPC.AW2002.2KAI.AI131701.PNT | 2KAI:AI131701.PNT | 20HFE20CT009 | PAF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 55.5598 | ok
1125 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-08 | OPC.AW2002.2KAI.AI132101.PNT | 2KAI:AI132101.PNT | 20HFE20CT010 | PAF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 70 | 95 |  | 45.544 | ok
1126 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-08 | OPC.AW2002.2KAI.AI131702.PNT | 2KAI:AI131702.PNT | 20HFE20CT011 | PAF B NON DRIVED END BEARING TEMPERATURE | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 52.3901 | ok
1127 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-K1003-02 | OPC.AW2002.2KAI.AI132102.PNT | 2KAI:AI132102.PNT | 20HFE20CT012 | PAF B DRIVED END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 85 |  | 49.2204 | ok
1128 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2KAI.AI131205.PNT | 2KAI:AI131205.PNT | 20HFE20CY001X | PAF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.9302 | ok
1129 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2KAI.AI131301.PNT | 2KAI:AI131301.PNT | 20HFE20CY001Y | PAF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.59284 | ok
1130 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2KAI.AI131206.PNT | 2KAI:AI131206.PNT | 20HFE20CY002X | PAF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.9078 | ok
1131 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 6 | PAF #2B | 50-F296S-J0201-02 | OPC.AW2002.2KAI.AI131302.PNT | 2KAI:AI131302.PNT | 20HFE20CY002Y | PAF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.63907 | ok
1132 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140201.PNT | 2LAI:AI140201.PNT | 20HLA20CP201 | FDF B OUTLET AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.67813 | ok
1133 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141601.PNT | 2LAI:AI141601.PNT | 20HLA20CT001 | FDF B INLET AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 23.3484 | ok
1134 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_FDF.AO052601.OUT | 2E_FDF:AO052601.OUT | 20HLB20AA101XB11 | FDF B INLET VANE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 11 | ok
1135 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051701.PNT | 2EAI:AI051701.PNT | 20HLB20AA101XB12 | FDF B INLET VANE POSITION | AI | 0 | 100 | % | [6 empty] | 11.2168 | ok
1136 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2KAI.AI131101.PNT | 2KAI:AI131101.PNT | 20HLB20AN001XB13 | FDF B CURRENT | AI | 0 | 200 | A | [6 empty] | 19.9023 | ok
1137 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131401.PNT | 2KAI:AI131401.PNT | 20HLB20CT001 | FDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.9481 | ok
1138 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131501.PNT | 2KAI:AI131501.PNT | 20HLB20CT002 | FDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.5844 | ok
1139 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131402.PNT | 2KAI:AI131402.PNT | 20HLB20CT003 | FDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 51.0131 | ok
1140 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131502.PNT | 2KAI:AI131502.PNT | 20HLB20CT004 | FDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.8572 | ok
1141 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131403.PNT | 2KAI:AI131403.PNT | 20HLB20CT005 | FDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.7013 | ok
1142 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131503.PNT | 2KAI:AI131503.PNT | 20HLB20CT006 | FDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 51.2599 | ok
1143 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131404.PNT | 2KAI:AI131404.PNT | 20HLB20CT007 | FDF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 45.7518 | ok
1144 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131504.PNT | 2KAI:AI131504.PNT | 20HLB20CT008 | FDF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 80 | 95 |  | 62.328 | ok
1145 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131405.PNT | 2KAI:AI131405.PNT | 20HLB20CT009 | FDF B NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 41.4129 | ok
1146 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131505.PNT | 2KAI:AI131505.PNT | 20HLB20CT010 | FDF B NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 39.3474 | ok
1147 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131601.PNT | 2KAI:AI131601.PNT | 20HLB20CT011 | FDF B NON DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 41.4259 | ok
1148 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131406.PNT | 2KAI:AI131406.PNT | 20HLB20CT012 | FDF B DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 36.4764 | ok
1149 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131506.PNT | 2KAI:AI131506.PNT | 20HLB20CT013 | FDF B DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 35.658 | ok
1150 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131602.PNT | 2KAI:AI131602.PNT | 20HLB20CT014 | FDF B DRIVED END BEARING TEMPERATURE 3 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 36.1906 | ok
1151 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131106.PNT | 2KAI:AI131106.PNT | 20HLB20CY001X | FDF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.67774 | ok
1152 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131203.PNT | 2KAI:AI131203.PNT | 20HLB20CY001Y | FDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.18049 | ok
1153 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131107.PNT | 2KAI:AI131107.PNT | 20HLB20CY002X | FDF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 1.2287 | ok
1154 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 7 | FDF #2B | 50-F296S-J0201-35 | OPC.AW2002.2KAI.AI131204.PNT | 2KAI:AI131204.PNT | 20HLB20CY002Y | FDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 4.6 |  |  | 0.39358 | ok
1155 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140204.PNT | 2LAI:AI140204.PNT | 20HFE20CP202 | APH B INLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 10.5312 | ok
1156 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140205.PNT | 2LAI:AI140205.PNT | 20HFE20CP203 | APH B OUTLET PRIMARY AIR PRESSURE | AI | 0 | 20 | KPa | [6 empty] | 9.3336 | ok
1157 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050106.PNT | 2EAI:AI050106.PNT | 20HFE20CT002 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 40.1585 | ok
1158 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050204.PNT | 2EAI:AI050204.PNT | 20HFE20CT003 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 39.3719 | ok
1159 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050304.PNT | 2EAI:AI050304.PNT | 20HFE20CT004 | APH B INLET PRIMARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 39.1328 | ok
1160 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141603.PNT | 2LAI:AI141603.PNT | 20HFE20CT005 | APH B OUTLET PRIMARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 316.7248 | ok
1161 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140202.PNT | 2LAI:AI140202.PNT | 20HLA20CP202 | APH B INLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.59961 | ok
1162 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051101.PNT | 2EAI:AI051101.PNT | 20HLA20CP203 | APH B OUTLET SECONDARY AIR PRESSURE | AI | 0 | 5 | KPa | [6 empty] | 0.47588 | ok
1163 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050103.PNT | 2EAI:AI050103.PNT | 20HLA20CT002 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 26.0703 | ok
1164 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050202.PNT | 2EAI:AI050202.PNT | 20HLA20CT003 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 26.3521 | ok
1165 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050302.PNT | 2EAI:AI050302.PNT | 20HLA20CT004 | APH B INLET SECONDARY AIR TEMPERATURE | TC | 0 | 100 | ℃ | [6 empty] | 26.1673 | ok
1166 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050104.PNT | 2EAI:AI050104.PNT | 20HLA20CT005 | APH B OUTLET SECONDARY AIR TEMPERATURE | TC | 0 | 360 | ℃ | [6 empty] | 332.3402 | ok
1167 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2KAI.AI131104.PNT | 2KAI:AI131104.PNT | 20HLD12GC001AI01 | AIR PREHEATER B MAIN MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | 13.4537 | ok
1168 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2KAI.AI131201.PNT | 2KAI:AI131201.PNT | 20HLD12GC001AI02 | AIR PREHEATER B AUXILIARY MOTOR CURRENT OUTPUT | AI | 0 | 50 | A | [6 empty] | -0.0091797 | no
1169 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2KAI.AI131105.PNT | 2KAI:AI131105.PNT | 20HLD12GC001AI03 | AIR PREHEATER B MAIN MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 986.0845 | ok
1170 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2KAI.AI131202.PNT | 2KAI:AI131202.PNT | 20HLD12GC001AI04 | AIR PREHEATER B AUXILIARY MOTOR ROTATIONAL SPEED OUTPUT | AI | 0 | 1000 | rpm | [6 empty] | 11.8977 | ok
1171 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2JAH.AO112603.OUT | 2JAH:AO112603.OUT | 20HLD12GC001AO01 | AIR PREHEATER B MAIN MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | 0 | ok
1172 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-38 | OPC.AW2002.2JAH.AO112604.OUT | 2JAH:AO112604.OUT | 20HLD12GC001AO02 | AIR PREHEATER B AUXILIARY MOTOR ROTATIONAL SPEED PRESET | AO | 0 | 100 | % | [6 empty] | 0 | ok
1173 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140207.PNT | 2LAI:AI140207.PNT | 20HNA20CP202 | APH B OUTLET FLUE GAS PRESSURE | AI | -3500 | 0 | Pa | [6 empty] | -1387.2168 | ok
1174 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050207.PNT | 2EAI:AI050207.PNT | 20HNA20CT002 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 159.297 | ok
1175 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050307.PNT | 2EAI:AI050307.PNT | 20HNA20CT003 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 163.8045 | ok
1176 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 8 | AIR HEATER #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI050404.PNT | 2EAI:AI050404.PNT | 20HNA20CT004 | APH B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 170.7994 | ok
1177 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140301.PNT | 2LAI:AI140301.PNT | 20HNA11CP201 | ESP A OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa | [6 empty] | -1812.0117 | ok
1178 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141505.PNT | 2LAI:AI141505.PNT | 20HNA11CT001 | ESP A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 165.0077 | ok
1179 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140302.PNT | 2LAI:AI140302.PNT | 20HNA12CP201 | IDF A OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa | [6 empty] | 331.875 | ok
1180 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141506.PNT | 2LAI:AI141506.PNT | 20HNA12CT001 | IDF A OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 168.1764 | ok
1181 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2E_IDF.AO052705.OUT | 2E_IDF:AO052705.OUT | 20HNC11AA101XB11 | IDF A INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 36.5253 | ok
1182 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI051705.PNT | 2EAI:AI051705.PNT | 20HNC11AA101XB12 | IDF A INLET STATIONARY BLADE POSITION | AI | 0 | 100 | % | [6 empty] | 36.7754 | ok
1183 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111103.PNT | 2JAI:AI111103.PNT | 20HNC11AN001XB13 | IDF A CURRENT | AI | 0 | 400 | A | [6 empty] | 115.0078 | ok
1184 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111305.PNT | 2JAI:AI111305.PNT | 20HNC11AN002XB13 | IDF A #1 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | 0.021094 | ok
1185 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111306.PNT | 2JAI:AI111306.PNT | 20HNC11AN003XB13 | IDF A #2 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | 12.4523 | ok
1186 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111703.PNT | 2JAI:AI111703.PNT | 20HNC11CT001 | IDF A MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.5056 | ok
1187 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI112103.PNT | 2JAI:AI112103.PNT | 20HNC11CT002 | IDF A MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.4666 | ok
1188 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111704.PNT | 2JAI:AI111704.PNT | 20HNC11CT003 | IDF A MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.9862 | ok
1189 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI112104.PNT | 2JAI:AI112104.PNT | 20HNC11CT004 | IDF A MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 48.0382 | ok
1190 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111705.PNT | 2JAI:AI111705.PNT | 20HNC11CT005 | IDF A MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.3497 | ok
1191 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI112105.PNT | 2JAI:AI112105.PNT | 20HNC11CT006 | IDF A MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 47.0379 | ok
1192 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111706.PNT | 2JAI:AI111706.PNT | 20HNC11CT007 | IDF A MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 42.5171 | ok
1193 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI112106.PNT | 2JAI:AI112106.PNT | 20HNC11CT008 | IDF A MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 36.3855 | ok
1194 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111707.PNT | 2JAI:AI111707.PNT | 20HNC11CT009 | IDF A DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 56.5846 | ok
1195 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI112107.PNT | 2JAI:AI112107.PNT | 20HNC11CT010 | IDF A DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 55.9626 | ok
1196 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111604.PNT | 2JAI:AI111604.PNT | 20HNC11CT011 | IDF A MIDDLE BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 57.4169 | ok
1197 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111605.PNT | 2JAI:AI111605.PNT | 20HNC11CT012 | IDF A MIDDLE BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 55.9366 | ok
1198 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111606.PNT | 2JAI:AI111606.PNT | 20HNC11CT013 | IDF A NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 55.5339 | ok
1199 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111607.PNT | 2JAI:AI111607.PNT | 20HNC11CT014 | IDF A NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 56.1444 | ok
1200 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111207.PNT | 2JAI:AI111207.PNT | 20HNC11CY001X | IDF A DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 3.5327 | ok
1201 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111303.PNT | 2JAI:AI111303.PNT | 20HNC11CY001Y | IDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.0453 | ok
1202 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111208.PNT | 2JAI:AI111208.PNT | 20HNC11CY002X | IDF A NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.3067 | ok
1203 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 10 | IDF #2A | 50-F296S-J0201-37 | OPC.AW2002.2JAI.AI111304.PNT | 2JAI:AI111304.PNT | 20HNC11CY002Y | IDF A DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 2.7954 | ok
1204 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140401.PNT | 2LAI:AI140401.PNT | 20HNA21CP201 | ESP B OUTLET FLUE GAS PRESSURE | AI | -5000 | 0 | Pa | [6 empty] | -1153.6133 | ok
1205 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141605.PNT | 2LAI:AI141605.PNT | 20HNA21CT001 | ESP B OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 156.5035 | ok
1206 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI140402.PNT | 2LAI:AI140402.PNT | 20HNA22CP201 | IDF B OUTLET FLUE GAS PRESSURE | AI | 0 | 600 | Pa | [6 empty] | 350.884 | ok
1207 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141606.PNT | 2LAI:AI141606.PNT | 20HNA22CT001 | IDFB OUTLET FLUE GAS TEMPERATURE | TC | 0 | 350 | ℃ | [6 empty] | 164.2077 | ok
1208 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2E_IDF.AO053101.OUT | 2E_IDF:AO053101.OUT | 20HNC21AA101XB11 | IDF B INLET STATIONARY BLADE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 35.6357 | ok
1209 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-02 | OPC.AW2002.2EAI.AI052302.PNT | 2EAI:AI052302.PNT | 20HNC21AA101XB12 | IDF B INLET STATIONARY BLADE POSITION | AI | 0 | 100 | % | [6 empty] | 35.9844 | ok
1210 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131103.PNT | 2KAI:AI131103.PNT | 20HNC21AN001XB13 | IDF B CURRENT | AI | 0 | 400 | A | [6 empty] | 109.3359 | ok
1211 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131305.PNT | 2KAI:AI131305.PNT | 20HNC21AN002XB13 | IDF B #1 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | -0.074219 | no
1212 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131306.PNT | 2KAI:AI131306.PNT | 20HNC21AN003XB13 | IDF B #2 COOLING FAN MOTOR CURRENT | AI | 0 | 40 | A | [6 empty] | 9.525 | ok
1213 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131703.PNT | 2KAI:AI131703.PNT | 20HNC21CT001 | IDF B MOTOR STATOR COIL U TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.0388 | ok
1214 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI132103.PNT | 2KAI:AI132103.PNT | 20HNC21CT002 | IDF B MOTOR STATOR COIL U TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 49.8569 | ok
1215 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131704.PNT | 2KAI:AI131704.PNT | 20HNC21CT003 | IDF B MOTOR STATOR COIL V TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.1687 | ok
1216 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI132104.PNT | 2KAI:AI132104.PNT | 20HNC21CT004 | IDF B MOTOR STATOR COIL V TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 50.4025 | ok
1217 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131705.PNT | 2KAI:AI131705.PNT | 20HNC21CT005 | IDF B MOTOR STATOR COIL W TEMPERATURE 1 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 49.5321 | ok
1218 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI132105.PNT | 2KAI:AI132105.PNT | 20HNC21CT006 | IDF B MOTOR STATOR COIL W TEMPERATURE 2 | RTD | 0 | 150 | ℃ |  |  |  | 125 | 135 |  | 49.2463 | ok
1219 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131706.PNT | 2KAI:AI131706.PNT | 20HNC21CT007 | IDF B MOTOR DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 43.7253 | ok
1220 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI132106.PNT | 2KAI:AI132106.PNT | 20HNC21CT008 | IDF B MOTOR NON DRIVING END BEARING TEMPERATURE | RTD | 0 | 100 | ℃ |  |  |  | 75 | 95 |  | 32.9429 | ok
1221 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131707.PNT | 2KAI:AI131707.PNT | 20HNC21CT009 | IDF B DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 58.5861 | ok
1222 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI132107.PNT | 2KAI:AI132107.PNT | 20HNC21CT010 | IDF B DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 58.0671 | ok
1223 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131604.PNT | 2KAI:AI131604.PNT | 20HNC21CT011 | IDF B MIDDLE BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 62.341 | ok
1224 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131605.PNT | 2KAI:AI131605.PNT | 20HNC21CT012 | IDF B MIDDLE BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 60.6649 | ok
1225 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131606.PNT | 2KAI:AI131606.PNT | 20HNC21CT013 | IDF B NON DRIVED END BEARING TEMPERATURE 1 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 60.8861 | ok
1226 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131607.PNT | 2KAI:AI131607.PNT | 20HNC21CT014 | IDF B NON DRIVED END BEARING TEMPERATURE 2 | RTD | 0 | 100 | ℃ |  |  |  | 90 | 95 |  | 60.964 | ok
1227 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131207.PNT | 2KAI:AI131207.PNT | 20HNC21CY001X | IDF B DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.031797 | ok
1228 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131303.PNT | 2KAI:AI131303.PNT | 20HNC21CY001Y | IDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.088125 | ok
1229 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131208.PNT | 2KAI:AI131208.PNT | 20HNC21CY002X | IDF B NON DRIVED END BEARING VIBRATING ON X DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 0.037734 | ok
1230 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 12 | IDF #2B | 50-F296S-J0201-37 | OPC.AW2002.2KAI.AI131304.PNT | 2KAI:AI131304.PNT | 20HNC21CY002Y | IDF B DRIVED END BEARING VIBRATING ON Y DIRECTION | AI | 0 | 20 | mm/s |  |  |  | 6.3 |  |  | 1.4133 | ok
1231 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142701.PNT | 2LAI:AI142701.PNT | 20HNEAI001 | DUST CONCENTRATION | AI | 10 | 1000 | mg/m3 | [6 empty] | 648.6328 | ok
1232 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142702.PNT | 2LAI:AI142702.PNT | 20HNEAI002 | SO2 CONCENTRATION | AI | 0 | 1000 | mg/m3 | [6 empty] | 144.2578 | ok
1233 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142703.PNT | 2LAI:AI142703.PNT | 20HNEAI003 | NOX CONCENTRATION | AI | 0 | 1000 | mg/m3 | [6 empty] | 103.2656 | ok
1234 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142704.PNT | 2LAI:AI142704.PNT | 20HNEAI004 | O2 CONCENTRATION | AI | 0 | 25 | % | [6 empty] | 2.4598 | ok
1235 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142705.PNT | 2LAI:AI142705.PNT | 20HNEAI005 | FLUE GAS FLOW | AI | 0 | 45 | m/s | [6 empty] | 8.3258 | ok
1236 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI141405.PNT | 2LAI:AI141405.PNT | 20HNEAI006 | FLUE GAS TEMPERATURE | RTD | 0 | 200 | ℃ | [6 empty] | 56.5273 | ok | REVISI TAG
1237 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142706.PNT | 2LAI:AI142706.PNT | 20HNEAI007 | FLUE GAS PRESSURE | AI | -5 | 5 | kPa | [6 empty] | 609.2227 | ok
1238 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142707.PNT | 2LAI:AI142707.PNT | 20HNEAI008 | FLUE GAS HUMIDITY | AI | 0 | 100 | % | [6 empty] | 181.7012 | ok
1239 | 2 | UJPCT #2 | 7 | AIR & FLUE GAS SYSTEM #2 | 13 | CEMS #2 | 50-F296S-J0201-02 | OPC.AW2002.2LAI.AI142708.PNT | 2LAI:AI142708.PNT | 20HNEAI009 | CO CONCENTRATION | AI | 0 | 500 | mg/m3 | [8 empty] | TIDAK DIPAKAI
1240 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-19 | OPC.AW2002.2QAI.AI213404.PNT | 2QAI:AI213404.PNT | 20MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.023895 | ok
1241 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2PAI.AI203602.PNT | 2PAI:AI203602.PNT | 20MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 1000 | mm |  |  | 300 | 600 |  |  | 367.6289 | ok
1242 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2RAI.AI231204.PNT | 2RAI:AI231204.PNT | 20MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 2 | MPa | [6 empty] | 0.38125 | ok
1243 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230305.PNT | 2RAI:AI230305.PNT | 20MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C | [6 empty] | 51.9094 | ok
1244 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230405.PNT | 2RAI:AI230405.PNT | 20MKW10CT003 | GENERATOR H2 SIDE RETURN OIL TEMP(EXCITER SIDE) | RTD | 0 | 100 | C | [6 empty] | 60.7172 | ok
1245 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2PAI.AI202205.PNT | 2PAI:AI202205.PNT | 20MKW20AP101XB13 | GENERATOR H2 SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 15 | A |  |  |  | 8.8 |  |  | -0.0076172 | no
1246 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 1 | GENERATOR SEAL OIL - H2 SIDE #2A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230307.PNT | 2RAI:AI230307.PNT | 20MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 30.6046 | ok
1247 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2PAI.AI202801.PNT | 2PAI:AI202801.PNT | 20MKW20AP102XB13 | GENERATOR H2 SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 15 | A |  |  |  | 8.8 |  |  | 5.9268 | ok
1248 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 3 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW2002.2PAI.AI202107.PNT | 2PAI:AI202107.PNT | 20MKW10AP101XB13 | GENERATOR AIR SIDE SEAL OIL PUMP A CURRENT | AI | 0 | 25 | A |  |  |  | 15.4 |  |  | -0.041992 | no
1249 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 3 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230404.PNT | 2RAI:AI230404.PNT | 20MKW10CT001 | GENERATOR AIR SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 40.2048 | ok
1250 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 3 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230306.PNT | 2RAI:AI230306.PNT | 20MKW10CT004 | GENERATOR TURBINE SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 55.0532 | ok
1251 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 3 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP A | F296S-J0201-25 | OPC.AW2002.2RAI.AI230406.PNT | 2RAI:AI230406.PNT | 20MKW10CT005 | GENERATOR EXCITER SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 51.0261 | ok
1252 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 4 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW2002.2PAI.AI202203.PNT | 2PAI:AI202203.PNT | 20MKW10AP102XB13 | GENERATOR AIR SIDE SEAL OIL PUMP B CURRENT | AI | 0 | 25 | A |  |  |  | 15.4 |  |  | 12.1089 | ok
1253 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 5 | GENERATOR SEAL OIL #2 - AIR SIDE DC EMERGENCY PUMP | F296S-J0201-25 | OPC.AW2002.2PAI.AI202204.PNT | 2PAI:AI202204.PNT | 20MKW10AP103XB13 | GENERATOR AIR SIDE DC EMERGENCY SEAL OIL PUMP CURRENT | AI | 0 | 50 | A |  |  |  | 41.1 |  |  | -0.30566 | no
1254 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2M_GESTAT.AO162608.OUT | 2M_GESTAT:AO162608.OUT | 20MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1255 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2MAI.AI162304.PNT | 2MAI:AI162304.PNT | 20MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.25781 | ok
1256 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2PAI.AI202201.PNT | 2PAI:AI202201.PNT | 20MKF10AP001XB13 | GENERATOR STATOR COOLING WATER PUMP A CURRENT | AI | 0 | 75 | A |  |  |  | 42.2 |  |  | 0.0014648 | ok
1257 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2R_FLOW.GENAIN.PNT | 2R_FLOW:GENAIN.PNT | 20MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 50 | t/h |  |  | 5 | 45 |  |  | 50.4966 | no
1258 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2RAI.AI231501.PNT | 2RAI:AI231501.PNT | 20MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2 |  |  | 1.3152 | ok
1259 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2RAI.AI231402.PNT | 2RAI:AI231402.PNT | 20MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5 |  |  | 12.6789 | no
1260 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2MAI.AI160101.PNT | 2MAI:AI160101.PNT | 20MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | C |  |  |  | 48 |  |  | 43.7512 | ok
1262 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2RAI.AI231103.PNT | 2RAI:AI231103.PNT | 20MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.1945 | ok
1263 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2RAI.AI231203.PNT | 2RAI:AI231203.PNT | 20MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.045176 | ok
1264 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-24 | OPC.AW2002.2RAI.AI230304.PNT | 2RAI:AI230304.PNT | 20MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | C |  |  |  | 80 |  |  | 47.5445 | ok
1265 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 6 | GENERATOR STATOR COOLING #2A | F296S-J0201-14 | OPC.AW2002.2RAI.AI230206.PNT | 2RAI:AI230206.PNT | 20PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 44.5827 | ok
1266 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2PAI.AI202202.PNT | 2PAI:AI202202.PNT | 20MKF10AP002XB13 | GENERATOR STATOR COOLING WATER PUMP B CURRENT | AI | 0 | 75 | A |  |  |  | 42.2 |  |  | 35.1504 | ok
1267 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_6 | 2ATC:2BD117AIN.PNT_6 | 20MKA00CT0143 | GENERATOR TURBINE SIDE BABBIT TEMP | RTD | 0 | 120 | C | [6 empty] | 92.1029 | ok
1268 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_5 | 2ATC:2BD115AIN.PNT_5 | 20MKA00CT0144 | GENERATOR TURBINE SIDE BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 62.6398 | ok
1269 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_7 | 2ATC:2BD104AIN.PNT_7 | 20TSIDEH16 | SHAFT NO.5 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 50.75 | ok
1270 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_8 | 2ATC:2BD104AIN.PNT_8 | 20TSIDEH17 | SHAFT NO.5 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 27.2891 | ok
1271 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 8 | BEARING GENERATOR NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_7 | 2ATC:2BD105AIN.PNT_7 | 20TSIDEH24 | BEARING COVER NO.5 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 21.1475 | ok
1272 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_7 | 2ATC:2BD117AIN.PNT_7 | 20MKA00CT0146 | GENERATOR COLECTOR SIDE BABBIT TEMP | RTD | 0 | 120 | C | [6 empty] | 81.0348 | ok
1273 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_6 | 2ATC:2BD115AIN.PNT_6 | 20MKA00CT0147 | GENERATOR COLECTOR SIDE BEARING RETURN OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 57.6514 | ok
1274 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_1 | 2ATC:2BD105AIN.PNT_1 | 20TSIDEH18 | SHAFT NO.6 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 43.0703 | ok
1275 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_2 | 2ATC:2BD105AIN.PNT_2 | 20TSIDEH19 | SHAFT NO.6 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 51.6328 | ok
1276 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 9 | BEARING GENERATOR NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_8 | 2ATC:2BD105AIN.PNT_8 | 20TSIDEH25 | BEARING COVER NO.6 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 17.8369 | ok
1277 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224601.PNT | 2QAI:AI224601.PNT | 20MKA00CT001 | GENERATOR STATOR COIL OUTLET WATER TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7253 | ok
1278 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224602.PNT | 2QAI:AI224602.PNT | 20MKA00CT002 | GENERATOR STATOR COIL OUTLET WATER TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.647 | ok
1279 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224603.PNT | 2QAI:AI224603.PNT | 20MKA00CT003 | GENERATOR STATOR COIL OUTLET WATER TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.0241 | ok
1280 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224604.PNT | 2QAI:AI224604.PNT | 20MKA00CT004 | GENERATOR STATOR COIL OUTLET WATER TEMP 4 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.634 | ok
1281 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224605.PNT | 2QAI:AI224605.PNT | 20MKA00CT005 | GENERATOR STATOR COIL OUTLET WATER TEMP 5 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.0495 | ok
1282 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224606.PNT | 2QAI:AI224606.PNT | 20MKA00CT006 | GENERATOR STATOR COIL OUTLET WATER TEMP 6 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7642 | ok
1283 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224607.PNT | 2QAI:AI224607.PNT | 20MKA00CT007 | GENERATOR STATOR COIL OUTLET WATER TEMP 7 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.7766 | ok
1284 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224608.PNT | 2QAI:AI224608.PNT | 20MKA00CT008 | GENERATOR STATOR COIL OUTLET WATER TEMP 8 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.4654 | ok
1285 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224701.PNT | 2QAI:AI224701.PNT | 20MKA00CT009 | GENERATOR STATOR COIL OUTLET WATER TEMP 9 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.2576 | ok
1286 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224702.PNT | 2QAI:AI224702.PNT | 20MKA00CT010 | GENERATOR STATOR COIL OUTLET WATER TEMP 10 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.5561 | ok
1287 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224703.PNT | 2QAI:AI224703.PNT | 20MKA00CT011 | GENERATOR STATOR COIL OUTLET WATER TEMP 11 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.2963 | ok
1288 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224704.PNT | 2QAI:AI224704.PNT | 20MKA00CT012 | GENERATOR STATOR COIL OUTLET WATER TEMP 12 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5824 | ok
1289 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224705.PNT | 2QAI:AI224705.PNT | 20MKA00CT013 | GENERATOR STATOR COIL OUTLET WATER TEMP 13 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.2576 | ok
1290 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224706.PNT | 2QAI:AI224706.PNT | 20MKA00CT014 | GENERATOR STATOR COIL OUTLET WATER TEMP 14 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.3353 | ok
1291 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224707.PNT | 2QAI:AI224707.PNT | 20MKA00CT015 | GENERATOR STATOR COIL OUTLET WATER TEMP 15 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.9328 | ok
1292 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224708.PNT | 2QAI:AI224708.PNT | 20MKA00CT016 | GENERATOR STATOR COIL OUTLET WATER TEMP 16 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.4392 | ok
1293 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225101.PNT | 2QAI:AI225101.PNT | 20MKA00CT017 | GENERATOR STATOR COIL OUTLET WATER TEMP 17 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.6987 | ok
1294 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225102.PNT | 2QAI:AI225102.PNT | 20MKA00CT018 | GENERATOR STATOR COIL OUTLET WATER TEMP 18 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.8936 | ok
1295 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225103.PNT | 2QAI:AI225103.PNT | 20MKA00CT019 | GENERATOR STATOR COIL OUTLET WATER TEMP 19 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.647 | ok
1296 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225104.PNT | 2QAI:AI225104.PNT | 20MKA00CT020 | GENERATOR STATOR COIL OUTLET WATER TEMP 20 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.8679 | ok
1297 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225105.PNT | 2QAI:AI225105.PNT | 20MKA00CT021 | GENERATOR STATOR COIL OUTLET WATER TEMP 21 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.0887 | ok
1298 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225106.PNT | 2QAI:AI225106.PNT | 20MKA00CT022 | GENERATOR STATOR COIL OUTLET WATER TEMP 22 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.5174 | ok
1299 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225107.PNT | 2QAI:AI225107.PNT | 20MKA00CT023 | GENERATOR STATOR COIL OUTLET WATER TEMP 23 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.5821 | ok
1300 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225108.PNT | 2QAI:AI225108.PNT | 20MKA00CT024 | GENERATOR STATOR COIL OUTLET WATER TEMP 24 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.6211 | ok
1301 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225201.PNT | 2QAI:AI225201.PNT | 20MKA00CT025 | GENERATOR STATOR COIL OUTLET WATER TEMP 25 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 41.8936 | ok
1302 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225202.PNT | 2QAI:AI225202.PNT | 20MKA00CT026 | GENERATOR STATOR COIL OUTLET WATER TEMP 26 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.8289 | ok
1303 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225203.PNT | 2QAI:AI225203.PNT | 20MKA00CT027 | GENERATOR STATOR COIL OUTLET WATER TEMP 27 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.0365 | ok
1304 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225204.PNT | 2QAI:AI225204.PNT | 20MKA00CT028 | GENERATOR STATOR COIL OUTLET WATER TEMP 28 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.6211 | ok
1305 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225205.PNT | 2QAI:AI225205.PNT | 20MKA00CT029 | GENERATOR STATOR COIL OUTLET WATER TEMP 29 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.7899 | ok
1306 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225206.PNT | 2QAI:AI225206.PNT | 20MKA00CT030 | GENERATOR STATOR COIL OUTLET WATER TEMP 30 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.2319 | ok
1307 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225207.PNT | 2QAI:AI225207.PNT | 20MKA00CT031 | GENERATOR STATOR COIL OUTLET WATER TEMP 31 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7383 | ok
1308 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225208.PNT | 2QAI:AI225208.PNT | 20MKA00CT032 | GENERATOR STATOR COIL OUTLET WATER TEMP 32 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.05 | ok
1309 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225301.PNT | 2QAI:AI225301.PNT | 20MKA00CT033 | GENERATOR STATOR COIL OUTLET WATER TEMP 33 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.9978 | ok
1310 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225302.PNT | 2QAI:AI225302.PNT | 20MKA00CT034 | GENERATOR STATOR COIL OUTLET WATER TEMP 34 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.7512 | ok
1311 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225303.PNT | 2QAI:AI225303.PNT | 20MKA00CT035 | GENERATOR STATOR COIL OUTLET WATER TEMP 35 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.154 | ok
1312 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225304.PNT | 2QAI:AI225304.PNT | 20MKA00CT036 | GENERATOR STATOR COIL OUTLET WATER TEMP 36 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.8941 | ok
1313 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225305.PNT | 2QAI:AI225305.PNT | 20MKA00CT037 | GENERATOR STATOR COIL OUTLET WATER TEMP 37 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6603 | ok
1314 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225306.PNT | 2QAI:AI225306.PNT | 20MKA00CT038 | GENERATOR STATOR COIL OUTLET WATER TEMP 38 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.764 | ok
1315 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225307.PNT | 2QAI:AI225307.PNT | 20MKA00CT039 | GENERATOR STATOR COIL OUTLET WATER TEMP 39 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.0241 | ok
1316 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225308.PNT | 2QAI:AI225308.PNT | 20MKA00CT040 | GENERATOR STATOR COIL OUTLET WATER TEMP 40 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.0111 | ok
1317 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225401.PNT | 2QAI:AI225401.PNT | 20MKA00CT041 | GENERATOR STATOR COIL OUTLET WATER TEMP 41 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9591 | ok
1318 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225402.PNT | 2QAI:AI225402.PNT | 20MKA00CT042 | GENERATOR STATOR COIL OUTLET WATER TEMP 42 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.4525 | ok
1319 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225403.PNT | 2QAI:AI225403.PNT | 20MKA00CT043 | GENERATOR STATOR COIL OUTLET WATER TEMP 43 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.0235 | ok
1320 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225404.PNT | 2QAI:AI225404.PNT | 20MKA00CT044 | GENERATOR STATOR COIL OUTLET WATER TEMP 44 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.6733 | ok
1321 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225405.PNT | 2QAI:AI225405.PNT | 20MKA00CT045 | GENERATOR STATOR COIL OUTLET WATER TEMP 45 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.9331 | ok
1322 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225406.PNT | 2QAI:AI225406.PNT | 20MKA00CT046 | GENERATOR STATOR COIL OUTLET WATER TEMP 46 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.764 | ok
1323 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225407.PNT | 2QAI:AI225407.PNT | 20MKA00CT047 | GENERATOR STATOR COIL OUTLET WATER TEMP 47 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4008 | ok
1324 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225408.PNT | 2QAI:AI225408.PNT | 20MKA00CT048 | GENERATOR STATOR COIL OUTLET WATER TEMP 48 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.102 | ok
1325 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225501.PNT | 2QAI:AI225501.PNT | 20MKA00CT049 | GENERATOR STATOR COIL OUTLET WATER TEMP 49 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1927 | ok
1326 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225502.PNT | 2QAI:AI225502.PNT | 20MKA00CT050 | GENERATOR STATOR COIL OUTLET WATER TEMP 50 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1796 | ok
1327 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225503.PNT | 2QAI:AI225503.PNT | 20MKA00CT051 | GENERATOR STATOR COIL OUTLET WATER TEMP 51 | RTD | 0 | 100 | C | [6 empty] | 43.6733 | ok
1328 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225504.PNT | 2QAI:AI225504.PNT | 20MKA00CT052 | GENERATOR STATOR COIL OUTLET WATER TEMP 52 | RTD | 0 | 100 | C | [6 empty] | 41.0622 | ok
1329 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225505.PNT | 2QAI:AI225505.PNT | 20MKA00CT053 | GENERATOR STATOR COIL OUTLET WATER TEMP 53 | RTD | 0 | 100 | C | [6 empty] | 42.673 | ok
1330 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225506.PNT | 2QAI:AI225506.PNT | 20MKA00CT054 | GENERATOR STATOR COIL OUTLET WATER TEMP 54 | RTD | 0 | 100 | C | [6 empty] | 44.3618 | ok
1331 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225601.PNT | 2QAI:AI225601.PNT | 20MKA00CT055 | GENERATOR STATOR BARS TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.8947 | ok
1332 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225602.PNT | 2QAI:AI225602.PNT | 20MKA00CT056 | GENERATOR STATOR BARS TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.9597 | ok
1333 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225603.PNT | 2QAI:AI225603.PNT | 20MKA00CT057 | GENERATOR STATOR BARS TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.466 | ok
1334 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225604.PNT | 2QAI:AI225604.PNT | 20MKA00CT058 | GENERATOR STATOR BARS TEMP 4 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.9334 | ok
1335 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225605.PNT | 2QAI:AI225605.PNT | 20MKA00CT059 | GENERATOR STATOR BARS TEMP 5 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.6349 | ok
1336 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225606.PNT | 2QAI:AI225606.PNT | 20MKA00CT060 | GENERATOR STATOR BARS TEMP 6 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.0893 | ok
1337 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225607.PNT | 2QAI:AI225607.PNT | 20MKA00CT061 | GENERATOR STATOR BARS TEMP 7 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2062 | ok
1338 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225608.PNT | 2QAI:AI225608.PNT | 20MKA00CT062 | GENERATOR STATOR BARS TEMP 8 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.5699 | ok
1339 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225701.PNT | 2QAI:AI225701.PNT | 20MKA00CT063 | GENERATOR STATOR BARS TEMP 9 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1672 | ok
1340 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225702.PNT | 2QAI:AI225702.PNT | 20MKA00CT064 | GENERATOR STATOR BARS TEMP 10 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.453 | ok
1341 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225703.PNT | 2QAI:AI225703.PNT | 20MKA00CT065 | GENERATOR STATOR BARS TEMP 11 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1672 | ok
1342 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225704.PNT | 2QAI:AI225704.PNT | 20MKA00CT066 | GENERATOR STATOR BARS TEMP 12 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.8947 | ok
1343 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225705.PNT | 2QAI:AI225705.PNT | 20MKA00CT067 | GENERATOR STATOR BARS TEMP 13 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2712 | ok
1344 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225706.PNT | 2QAI:AI225706.PNT | 20MKA00CT068 | GENERATOR STATOR BARS TEMP 14 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1802 | ok
1345 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225707.PNT | 2QAI:AI225707.PNT | 20MKA00CT069 | GENERATOR STATOR BARS TEMP 15 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.6476 | ok
1346 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI225708.PNT | 2QAI:AI225708.PNT | 20MKA00CT070 | GENERATOR STATOR BARS TEMP 16 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.9984 | ok
1347 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226101.PNT | 2QAI:AI226101.PNT | 20MKA00CT071 | GENERATOR STATOR BARS TEMP 17 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.8814 | ok
1348 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226102.PNT | 2QAI:AI226102.PNT | 20MKA00CT072 | GENERATOR STATOR BARS TEMP 18 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.9857 | ok
1349 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226103.PNT | 2QAI:AI226103.PNT | 20MKA00CT073 | GENERATOR STATOR BARS TEMP 19 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.7905 | ok
1350 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226104.PNT | 2QAI:AI226104.PNT | 20MKA00CT074 | GENERATOR STATOR BARS TEMP 20 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2452 | ok
1351 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226105.PNT | 2QAI:AI226105.PNT | 20MKA00CT075 | GENERATOR STATOR BARS TEMP 21 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 46.5832 | ok
1352 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226106.PNT | 2QAI:AI226106.PNT | 20MKA00CT076 | GENERATOR STATOR BARS TEMP 22 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.0373 | ok
1353 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226107.PNT | 2QAI:AI226107.PNT | 20MKA00CT077 | GENERATOR STATOR BARS TEMP 23 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.9204 | ok
1354 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226108.PNT | 2QAI:AI226108.PNT | 20MKA00CT078 | GENERATOR STATOR BARS TEMP 24 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.4141 | ok
1355 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226201.PNT | 2QAI:AI226201.PNT | 20MKA00CT079 | GENERATOR STATOR BARS TEMP 25 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.466 | ok
1356 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226202.PNT | 2QAI:AI226202.PNT | 20MKA00CT080 | GENERATOR STATOR BARS TEMP 26 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.4268 | ok
1357 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226203.PNT | 2QAI:AI226203.PNT | 20MKA00CT081 | GENERATOR STATOR BARS TEMP 27 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.4141 | ok
1358 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226204.PNT | 2QAI:AI226204.PNT | 20MKA00CT082 | GENERATOR STATOR BARS TEMP 28 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 46.3494 | ok
1359 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226205.PNT | 2QAI:AI226205.PNT | 20MKA00CT083 | GENERATOR STATOR BARS TEMP 29 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.7388 | ok
1360 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226206.PNT | 2QAI:AI226206.PNT | 20MKA00CT084 | GENERATOR STATOR BARS TEMP 30 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 46.0766 | ok
1361 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226207.PNT | 2QAI:AI226207.PNT | 20MKA00CT085 | GENERATOR STATOR BARS TEMP 31 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.8947 | ok
1362 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226208.PNT | 2QAI:AI226208.PNT | 20MKA00CT086 | GENERATOR STATOR BARS TEMP 32 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2062 | ok
1363 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226301.PNT | 2QAI:AI226301.PNT | 20MKA00CT087 | GENERATOR STATOR BARS TEMP 33 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.7388 | ok
1364 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226302.PNT | 2QAI:AI226302.PNT | 20MKA00CT088 | GENERATOR STATOR BARS TEMP 34 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.8425 | ok
1365 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226303.PNT | 2QAI:AI226303.PNT | 20MKA00CT089 | GENERATOR STATOR BARS TEMP 35 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.0114 | ok
1366 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226304.PNT | 2QAI:AI226304.PNT | 20MKA00CT090 | GENERATOR STATOR BARS TEMP 36 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.8295 | ok
1367 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226305.PNT | 2QAI:AI226305.PNT | 20MKA00CT091 | GENERATOR STATOR BARS TEMP 37 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.6999 | ok
1368 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226306.PNT | 2QAI:AI226306.PNT | 20MKA00CT092 | GENERATOR STATOR BARS TEMP 38 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.505 | ok
1369 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226307.PNT | 2QAI:AI226307.PNT | 20MKA00CT093 | GENERATOR STATOR BARS TEMP 39 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.9207 | ok
1370 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226308.PNT | 2QAI:AI226308.PNT | 20MKA00CT094 | GENERATOR STATOR BARS TEMP 40 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.8298 | ok
1371 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226401.PNT | 2QAI:AI226401.PNT | 20MKA00CT095 | GENERATOR STATOR BARS TEMP 41 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2322 | ok
1372 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226402.PNT | 2QAI:AI226402.PNT | 20MKA00CT096 | GENERATOR STATOR BARS TEMP 42 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1802 | ok
1373 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226403.PNT | 2QAI:AI226403.PNT | 20MKA00CT097 | GENERATOR STATOR BARS TEMP 43 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.8035 | ok
1374 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226404.PNT | 2QAI:AI226404.PNT | 20MKA00CT098 | GENERATOR STATOR BARS TEMP 44 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1413 | ok
1375 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226405.PNT | 2QAI:AI226405.PNT | 20MKA00CT099 | GENERATOR STATOR BARS TEMP 45 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.453 | ok
1376 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226406.PNT | 2QAI:AI226406.PNT | 20MKA00CT100 | GENERATOR STATOR BARS TEMP 46 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.7908 | ok
1377 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226407.PNT | 2QAI:AI226407.PNT | 20MKA00CT101 | GENERATOR STATOR BARS TEMP 47 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 44.5437 | ok
1378 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226408.PNT | 2QAI:AI226408.PNT | 20MKA00CT102 | GENERATOR STATOR BARS TEMP 48 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.544 | ok
1379 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226501.PNT | 2QAI:AI226501.PNT | 20MKA00CT103 | GENERATOR STATOR BARS TEMP 49 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2062 | ok
1380 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226502.PNT | 2QAI:AI226502.PNT | 20MKA00CT104 | GENERATOR STATOR BARS TEMP 50 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 54.1309 | ok
1381 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226503.PNT | 2QAI:AI226503.PNT | 20MKA00CT105 | GENERATOR STATOR BARS TEMP 51 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1543 | ok
1382 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226504.PNT | 2QAI:AI226504.PNT | 20MKA00CT106 | GENERATOR STATOR BARS TEMP 52 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.2062 | ok
1383 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226505.PNT | 2QAI:AI226505.PNT | 20MKA00CT107 | GENERATOR STATOR BARS TEMP 53 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.479 | ok
1384 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226506.PNT | 2QAI:AI226506.PNT | 20MKA00CT108 | GENERATOR STATOR BARS TEMP 54 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 45.1283 | ok
1385 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226601.PNT | 2QAI:AI226601.PNT | 20MKA00CT109 | GENERATOR STATOR CORE TEMP 1 | RTD | 0 | 100 | C | [6 empty] | 41.0102 | ok
1386 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226602.PNT | 2QAI:AI226602.PNT | 20MKA00CT110 | GENERATOR STATOR CORE TEMP 2 | RTD | 0 | 100 | C | [6 empty] | 41.5688 | ok
1387 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226603.PNT | 2QAI:AI226603.PNT | 20MKA00CT111 | GENERATOR STATOR CORE TEMP 3 | RTD | 0 | 100 | C | [6 empty] | 44.4008 | ok
1388 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226604.PNT | 2QAI:AI226604.PNT | 20MKA00CT112 | GENERATOR STATOR CORE TEMP 4 | RTD | 0 | 100 | C | [6 empty] | 46.7651 | ok
1389 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226605.PNT | 2QAI:AI226605.PNT | 20MKA00CT113 | GENERATOR STATOR CORE TEMP 5 | RTD | 0 | 100 | C | [6 empty] | 54.7025 | ok
1390 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226606.PNT | 2QAI:AI226606.PNT | 20MKA00CT114 | GENERATOR STATOR CORE TEMP 6 | RTD | 0 | 100 | C | [6 empty] | 57.9112 | ok
1391 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226607.PNT | 2QAI:AI226607.PNT | 20MKA00CT115 | GENERATOR STATOR CORE TEMP 7 | RTD | 0 | 100 | C | [6 empty] | 53.5073 | ok
1392 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226608.PNT | 2QAI:AI226608.PNT | 20MKA00CT116 | GENERATOR STATOR CORE TEMP 8 | RTD | 0 | 100 | C | [6 empty] | 57.1967 | ok
1393 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226701.PNT | 2QAI:AI226701.PNT | 20MKA00CT117 | GENERATOR STATOR CORE TEMP 9 | RTD | 0 | 100 | C | [6 empty] | 57.1317 | ok
1394 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226702.PNT | 2QAI:AI226702.PNT | 20MKA00CT118 | GENERATOR STATOR CORE TEMP 10 | RTD | 0 | 100 | C | [6 empty] | 53.7671 | ok
1395 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226703.PNT | 2QAI:AI226703.PNT | 20MKA00CT119 | GENERATOR STATOR CORE TEMP 11 | RTD | 0 | 100 | C | [6 empty] | 57.5864 | ok
1396 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226704.PNT | 2QAI:AI226704.PNT | 20MKA00CT120 | GENERATOR STATOR CORE TEMP 12 | RTD | 0 | 100 | C | [6 empty] | 54.8324 | ok
1397 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226705.PNT | 2QAI:AI226705.PNT | 20MKA00CT121 | GENERATOR STATOR CORE TEMP 13 | RTD | 0 | 100 | C | [6 empty] | 39.906 | ok
1398 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226706.PNT | 2QAI:AI226706.PNT | 20MKA00CT122 | GENERATOR STATOR CORE TEMP 14 | RTD | 0 | 100 | C | [6 empty] | 40.6335 | ok
1399 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226707.PNT | 2QAI:AI226707.PNT | 20MKA00CT123 | GENERATOR STATOR CORE TEMP 15 | RTD | 0 | 100 | C | [6 empty] | 39.7891 | ok
1400 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI226708.PNT | 2QAI:AI226708.PNT | 20MKA00CT124 | GENERATOR STATOR CORE TEMP 16 | RTD | 0 | 100 | C | [6 empty] | 41.1661 | ok
1401 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227101.PNT | 2QAI:AI227101.PNT | 20MKA00CT125 | GENERATOR STATOR CORE TEMP 17 | RTD | 0 | 100 | C | [6 empty] | 40.4386 | ok
1402 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227102.PNT | 2QAI:AI227102.PNT | 20MKA00CT126 | GENERATOR STATOR CORE TEMP 18 | RTD | 0 | 100 | C | [6 empty] | 41.8806 | ok
1403 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227105.PNT | 2QAI:AI227105.PNT | 20MKA00CT127 | GENERATOR COLD/HOT H2 TEMP 1 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 32.4753 | ok
1404 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227106.PNT | 2QAI:AI227106.PNT | 20MKA00CT128 | GENERATOR COLD/HOT H2 TEMP 2 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 32.0206 | ok
1405 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227107.PNT | 2QAI:AI227107.PNT | 20MKA00CT129 | GENERATOR COLD/HOT H2 TEMP 3 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 44.5956 | ok
1406 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227201.PNT | 2QAI:AI227201.PNT | 20MKA00CT130 | GENERATOR COLD/HOT H2 TEMP 4 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 34.307 | ok
1407 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227202.PNT | 2QAI:AI227202.PNT | 20MKA00CT131 | GENERATOR COLD/HOT H2 TEMP 5 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 43.6083 | ok
1408 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227203.PNT | 2QAI:AI227203.PNT | 20MKA00CT132 | GENERATOR COLD/HOT H2 TEMP 6 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 35.1903 | ok
1409 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227204.PNT | 2QAI:AI227204.PNT | 20MKA00CT133 | GENERATOR COLD/HOT H2 TEMP 7 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 43.1796 | ok
1410 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227205.PNT | 2QAI:AI227205.PNT | 20MKA00CT134 | GENERATOR COLD/HOT H2 TEMP 8 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 34.7746 | ok
1411 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227206.PNT | 2QAI:AI227206.PNT | 20MKA00CT135 | GENERATOR COLD/HOT H2 TEMP 9 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 46.5443 | ok
1412 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227301.PNT | 2QAI:AI227301.PNT | 20MKA00CT136 | GENERATOR COLD/HOT H2 TEMP 10 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 35.0474 | ok
1413 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227302.PNT | 2QAI:AI227302.PNT | 20MKA00CT137 | GENERATOR COLD/HOT H2 TEMP 11 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 43.8552 | ok
1414 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227303.PNT | 2QAI:AI227303.PNT | 20MKA00CT138 | GENERATOR COLD/HOT H2 TEMP 12 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 32.7741 | ok
1415 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227304.PNT | 2QAI:AI227304.PNT | 20MKA00CT139 | GENERATOR COLD/HOT H2 TEMP 13 | RTD | 0 | 100 | C |  |  |  | 70 |  |  | 33.4236 | ok
1416 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227305.PNT | 2QAI:AI227305.PNT | 20MKA00CT140 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 1 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.8549 | ok
1417 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227306.PNT | 2QAI:AI227306.PNT | 20MKA00CT141 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 2 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 43.1537 | ok
1418 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227307.PNT | 2QAI:AI227307.PNT | 20MKA00CT142 | GENERATOR STATOR WINDING LEADS OUTLET WATER TEMP 3 | RTD | 0 | 100 | C |  |  |  | 90 | 100 |  | 42.9069 | ok
1419 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224304.PNT | 2QAI:AI224304.PNT | 20MKA00CT160 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 100 | C | [6 empty] | 33.6482 | ok
1420 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224305.PNT | 2QAI:AI224305.PNT | 20MKA00CT161 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 100 | C | [6 empty] | 37.1937 | ok
1421 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224306.PNT | 2QAI:AI224306.PNT | 20MKA00CT162 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 100 | C | [6 empty] | 32.2391 | ok
1422 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224307.PNT | 2QAI:AI224307.PNT | 20MKA00CT163 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 4 | TC | 0 | 100 | C | [6 empty] | 34.5563 | ok
1423 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224308.PNT | 2QAI:AI224308.PNT | 20MKA00CT164 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 5 | TC | 0 | 100 | C | [6 empty] | 37.4712 | ok
1424 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224401.PNT | 2QAI:AI224401.PNT | 20MKA00CT165 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 6 | TC | 0 | 100 | C | [6 empty] | 40.137 | ok
1425 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224402.PNT | 2QAI:AI224402.PNT | 20MKA00CT166 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 7 | TC | 0 | 600 | C | [6 empty] | 35.0976 | ok
1426 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224403.PNT | 2QAI:AI224403.PNT | 20MKA00CT167 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 8 | TC | 0 | 100 | C | [6 empty] | 37.8075 | ok
1427 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224404.PNT | 2QAI:AI224404.PNT | 20MKA00CT168 | GENERATOR COLECTOR SIDE PARTS OF CORE END TEMP 9 | TC | 0 | 100 | C | [6 empty] | 33.532 | ok
1428 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224405.PNT | 2QAI:AI224405.PNT | 20MKA00CT169 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 1 | TC | 0 | 100 | C | [6 empty] | 33.9704 | ok
1429 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224406.PNT | 2QAI:AI224406.PNT | 20MKA00CT170 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 2 | TC | 0 | 100 | C | [6 empty] | 38.9874 | ok
1430 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI224407.PNT | 2QAI:AI224407.PNT | 20MKA00CT171 | GENERATOR TURBINE SIDE PARTS OF CORE END TEMP 3 | TC | 0 | 100 | C | [6 empty] | 37.3537 | ok
1431 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2E_CSDMD.AO052608.OUT | 2E_CSDMD:AO052608.OUT | 20DCSDEHAO01 | CCS DEMAND 1 | AO | 0 | 100 | % | [6 empty] | 88.9838 | ok
1432 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2E_CSDMD.AO052707.OUT | 2E_CSDMD:AO052707.OUT | 20DCSDEHAO02 | CCS DEMAND 2 | AO | 0 | 100 | % | [6 empty] | 88.9838 | ok
1433 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2EAI.AI052407.PNT | 2EAI:AI052407.PNT | 20DEHDCSAI02 | GENERATOR LOAD | AI | 0 | 519.6 | MW | [6 empty] | 193.8351 | ok
1434 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD106AIN.PNT_3 | 2VALVE:2AD106AIN.PNT_3 | 20DCSDEHAI01 | CCS DEMAND 1 | AI | 0 | 100 | % | [6 empty] | -91.1328 | no
1435 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD107AIN.PNT_3 | 2VALVE:2AD107AIN.PNT_3 | 20DCSDEHAI02 | CCS DEMAND 2 | AI | 0 | 100 | % | [6 empty] | 89.0391 | ok
1436 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD11206AOUT.OUT | 2VALVE:2AD11206AOUT.OUT | 20DEHDCSAO02 | GENERATOR LOAD | AO | 0 | 519.6 | MW | [6 empty] | 194.0713 | ok
1437 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD106AIN.PNT_1 | 2VALVE:2AD106AIN.PNT_1 | 20DQDEH01 | GENERATOR LOAD 1 | AI | 0 | 519.6 | MW | [6 empty] | 194.1328 | ok
1438 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD107AIN.PNT_1 | 2VALVE:2AD107AIN.PNT_1 | 20DQDEH02 | GENERATOR LOAD 2 | AI | 0 | 519.6 | MW | [6 empty] | 195.4951 | ok
1439 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 11 | GENERATOR #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD108AIN.PNT_1 | 2VALVE:2AD108AIN.PNT_1 | 20DQDEH03 | GENERATOR LOAD 3 | AI | 0 | 519.6 | MW | [6 empty] | 193.5234 | ok
1440 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242101.PNT | 2SAI:AI242101.PNT | 20MKA01-04 | GT HV SIDE CURRENT Ia | AI | 0 | 2500 | A | [6 empty] | 691.8457 | ok
1441 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242102.PNT | 2SAI:AI242102.PNT | 20MKA01-05 | GT HV SIDE CURRENT Ib | AI | 0 | 2500 | A | [6 empty] | 717.8711 | ok
1442 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242103.PNT | 2SAI:AI242103.PNT | 20MKA01-06 | GT HV SIDE CURRENT Ic | AI | 0 | 2500 | A | [6 empty] | 715.5273 | ok
1443 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242104.PNT | 2SAI:AI242104.PNT | 20MKA01-07 | GEN. CURRENT Ia | AI | 0 | 15000 | A | [6 empty] | 5563.4766 | ok
1444 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242105.PNT | 2SAI:AI242105.PNT | 20MKA01-08 | GEN. CURRENT Ib | AI | 0 | 15000 | A | [6 empty] | 5545.3125 | ok
1445 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242106.PNT | 2SAI:AI242106.PNT | 20MKA01-09 | GEN. CURRENT Ic | AI | 0 | 15000 | A | [6 empty] | 5799.6094 | ok
1446 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242107.PNT | 2SAI:AI242107.PNT | 20MKA01-10 | GEN. NEGATIVE-SEQUENCE CURRENT | AI | 0 | 15000 | A | [6 empty] | 224.707 | ok
1447 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242201.PNT | 2SAI:AI242201.PNT | 20MKA01-11 | GEN. NEUTRAL POINT CURRENT | AI | 0 | 5 | A | [6 empty] | 0.041309 | ok
1448 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242202.PNT | 2SAI:AI242202.PNT | 20MKA01-12 | EXCITING TR. HV SIDE CURRENT Ia | AI | 0 | 300 | A | [6 empty] | 45.3164 | ok
1449 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242203.PNT | 2SAI:AI242203.PNT | 20MKA01-13 | EXCITING TR. HV SIDE CURRENT Ib | AI | 0 | 300 | A | [6 empty] | 45.4219 | ok
1450 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242204.PNT | 2SAI:AI242204.PNT | 20MKA01-14 | EXCITING TR. HV SIDE CURRENT Ic | AI | 0 | 300 | A | [6 empty] | 45.4805 | ok
1451 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242205.PNT | 2SAI:AI242205.PNT | 20MKA01-15 | GEN. A-C VOLTAGE | AI | 0 | 24 | kV | [6 empty] | 19.7902 | ok
1452 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242206.PNT | 2SAI:AI242206.PNT | 20MKA01-16 | GEN. OUTLET ZERO-SEQUENCE VOLTAGE | AI | 0 | 100 | V | [6 empty] | 4.1797 | ok
1453 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242301.PNT | 2SAI:AI242301.PNT | 20MKA01-17 | GT REACTIVE POWER | AI | -500 | 500 | MVAR | [6 empty] | 0.9375 | ok
1454 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242302.PNT | 2SAI:AI242302.PNT | 20MKA01-18 | GEN. REACTIVE POWER | AI | -400 | 400 | MVAR | [6 empty] | -168.8594 | ok
1455 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242303.PNT | 2SAI:AI242303.PNT | 20MKA01-19 | GT ACTIVE POWER | AI | 0 | 450 | MW | [6 empty] | 183.0026 | ok
1456 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242304.PNT | 2SAI:AI242304.PNT | 20MKA01-20 | GEN. ACTIVE POWER | AI | 0 | 450 | MW | [6 empty] | 194.9062 | ok
1457 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242305.PNT | 2SAI:AI242305.PNT | 20MKA01-21 | GEN. POWER FACTOR | AI | -1 | 1 | pF | [6 empty] | 12.1431 | no
1458 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242306.PNT | 2SAI:AI242306.PNT | 20MKA01-22 | GEN. FREQUENCY | AI | 0 | 60 | Hz | [6 empty] | 50.0748 | ok
1459 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-05 | OPC.AW2002.2SAI.AI242307.PNT | 2SAI:AI242307.PNT | 20MKA01-23 | EXCITING TR. ACTIVE POWER | AI | 0 | 6 | MW | [6 empty] | 0.27193 | ok
1460 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-14 | OPC.AW2002.2SAI.AI242401.PNT | 2SAI:AI242401.PNT | 20MKA01-24 | FIELD CURRENT | AI | 0 | 3000 | A | [6 empty] | 1198.1836 | ok
1461 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-14 | OPC.AW2002.2SAI.AI242402.PNT | 2SAI:AI242402.PNT | 20MKA01-25 | FIELD VOLTAGE | AI | 0 | 1000 | V | [6 empty] | 208.9844 | ok
1462 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242403.PNT | 2SAI:AI242403.PNT | 20MKA01-26 | GT OIL TEMPERATURE 1 | AI | 0 | 150 | C | [6 empty] | 45.7969 | ok
1463 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242404.PNT | 2SAI:AI242404.PNT | 20MKA01-27 | GT OIL TEMPERATURE 2 | AI | 0 | 150 | C | [6 empty] | 40.9062 | ok
1464 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242405.PNT | 2SAI:AI242405.PNT | 20MKA01-28 | GT HV WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 44.0531 | ok
1465 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242406.PNT | 2SAI:AI242406.PNT | 20MKA01-29 | GT LV WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 57.4906 | ok
1466 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-12 | OPC.AW2002.2SAI.AI242407.PNT | 2SAI:AI242407.PNT | 20MKA01-30 | GT OLTC CHANGING POSITION | AI | 0 | 150 | C | [6 empty] | 8.8606 | ok
1467 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242501.PNT | 2SAI:AI242501.PNT | 20MKA01-209 | ET A PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 60.4102 | ok
1468 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242502.PNT | 2SAI:AI242502.PNT | 20MKA01-210 | ET B PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 62.8828 | ok
1469 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 12 | GENERATOR TRANSFORMER #2 | F296S-D0606-11 | OPC.AW2002.2SAI.AI242503.PNT | 2SAI:AI242503.PNT | 20MKA01-211 | ET C PHASE TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 58.1641 | ok
1470 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231404.PNT | 2RAI:AI231404.PNT | 20MKG00GH001AI01 | GENERATOR H2 LEAKAGE RATE 1 | AI | 0.1 | 2 | % | [6 empty] | 0.0055469 | no
1471 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231504.PNT | 2RAI:AI231504.PNT | 20MKG00GH001AI02 | GENERATOR H2 LEAKAGE RATE 2 | AI | 0.1 | 2 | % | [6 empty] | 0.0034766 | no
1472 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231405.PNT | 2RAI:AI231405.PNT | 20MKG00GH001AI03 | GENERATOR H2 LEAKAGE RATE 3 | AI | 0.1 | 2 | % | [6 empty] | 0.00078125 | no
1473 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231505.PNT | 2RAI:AI231505.PNT | 20MKG00GH001AI04 | GENERATOR H2 LEAKAGE RATE 4 | AI | 0.1 | 2 | % | [6 empty] | 0 | no
1474 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231406.PNT | 2RAI:AI231406.PNT | 20MKG00GH001AI05 | GENERATOR H2 LEAKAGE RATE 5 | AI | 0.1 | 2 | % | [6 empty] | 0.00042969 | no
1475 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231506.PNT | 2RAI:AI231506.PNT | 20MKG00GH001AI06 | GENERATOR H2 LEAKAGE RATE 6 | AI | 0.1 | 2 | % | [6 empty] | 0.0017969 | no
1476 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231407.PNT | 2RAI:AI231407.PNT | 20MKG00GH001AI07 | GENERATOR H2 LEAKAGE RATE 7 | AI | 0.1 | 2 | % | [6 empty] | 0.0019531 | no
1477 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231507.PNT | 2RAI:AI231507.PNT | 20MKG00GH001AI08 | GENERATOR H2 LEAKAGE RATE 8 | AI | 0.1 | 2 | % | [6 empty] | 0.0015234 | no
1478 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231105.PNT | 2RAI:AI231105.PNT | 20MKG10CP201 | GENERATOR INLET HYDROGEN PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.29051 | ok
1479 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI230407.PNT | 2RAI:AI230407.PNT | 20MKG10CT001 | GENERATOR INLET HYDROGEN TEMP | RTD | 0 | 100 | C | [6 empty] | 27.7726 | ok
1480 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI230501.PNT | 2RAI:AI230501.PNT | 20MKG11CT001 | GENERATOR EXHAUST HYDROGEN TEMP | RTD | 0 | 100 | C | [6 empty] | 27.201 | ok
1481 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231403.PNT | 2RAI:AI231403.PNT | 20MKG30CQ201 | GENERATOR TURBINE SIDE HYDROGEN HUMIDITY | AI | -40 | 10 | g/m3 | [6 empty] | 9.9502 | ok
1482 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231503.PNT | 2RAI:AI231503.PNT | 20MKG30CQ202 | GENERATOR COLLECTOR SIDE HYDROGEN HUMIDITY | AI | -40 | 10 | g/m3 | [6 empty] | -40.1123 | no
1483 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-26 | OPC.AW2002.2RAI.AI231502.PNT | 2RAI:AI231502.PNT | 20MKG50CQ201 | GENERATOR HYDROGEN PURITY | AI | 0 | 100 | % |  |  | 95 |  |  |  | 97.9676 | ok
1484 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230207.PNT | 2RAI:AI230207.PNT | 20PGA33CT001 | GENERATOR HYDROGEN COOLER MAIN PIPE INLET TEMP | RTD | 0 | 50 | C | [6 empty] | 29.6822 | ok
1485 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230301.PNT | 2RAI:AI230301.PNT | 20PGA33CT002 | GENERATOR HYDROGEN COOLER NO.1 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 30.7345 | ok
1486 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230401.PNT | 2RAI:AI230401.PNT | 20PGA33CT003 | GENERATOR HYDROGEN COOLER NO.2 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 32.4753 | ok
1487 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230302.PNT | 2RAI:AI230302.PNT | 20PGA33CT004 | GENERATOR HYDROGEN COOLER NO.3 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 32.1245 | ok
1488 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230402.PNT | 2RAI:AI230402.PNT | 20PGA33CT005 | GENERATOR HYDROGEN COOLER NO.4 OUTLET WATER TEMP | RTD | 0 | 50 | C | [6 empty] | 30.5656 | ok
1489 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 13 | GENERATOR H2 SYSTEM #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230303.PNT | 2RAI:AI230303.PNT | 20PGA33CT006 | TURBINE HOUSER COOLING RETURN WATER TEMP 3 | RTD | 0 | 50 | C | [6 empty] | 31.6309 | ok
1490 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 14 | STEADY BEARING GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227308.PNT | 2QAI:AI227308.PNT | 20MKA00CT149 | GENERATOR STEADY BEARING TEMP | RTD | 0 | 100 | C | [6 empty] | 62.4579 | ok
1491 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 14 | STEADY BEARING GENERATOR #2 | F296S-J0201-44 | OPC.AW2002.2QAI.AI227207.PNT | 2QAI:AI227207.PNT | 20MKA00CT150 | GENERATOR STEADY BEARING RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 47.7134 | ok
1492 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-04 | OPC.AW2002.2SAI.AI242504.PNT | 2SAI:AI242504.PNT | 20BBT01-01 | UAT HV A PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 377.7344 | ok
1493 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-04 | OPC.AW2002.2SAI.AI242505.PNT | 2SAI:AI242505.PNT | 20BBT01-02 | UAT HV B PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 381.3672 | ok
1494 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-04 | OPC.AW2002.2SAI.AI242506.PNT | 2SAI:AI242506.PNT | 20BBT01-03 | UAT HV C PHASE CURRENT MEASUREMENT | AI | 0 | 2000 | A | [6 empty] | 372.3047 | ok
1495 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-04 | OPC.AW2002.2SAI.AI242507.PNT | 2SAI:AI242507.PNT | 20BBT01-04 | UAT ACTIVE-POWER MEASUREMENT | AI | 0 | 40 | MW | [6 empty] | 10.4551 | ok
1496 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-05 | OPC.AW2002.2SAI.AI254601.PNT | 2SAI:AI254601.PNT | 20BBT01-06 | UAT WINDING TEMPERATURE | AI | 0 | 150 | C | [6 empty] | 51.7156 | ok
1497 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-05 | OPC.AW2002.2SAI.AI254602.PNT | 2SAI:AI254602.PNT | 20BBT01-07 | UAT OIL TEMPERATURE 1 | AI | 0 | 150 | C | [6 empty] | 44.5844 | ok
1498 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 | F296S-D0608-05 | OPC.AW2002.2SAI.AI254603.PNT | 2SAI:AI254603.PNT | 20BBT01-08 | UAT OIL TEMPERATURE 2 | AI | 0 | 150 | C | [6 empty] | 41.1313 | ok
1499 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0608-06 | OPC.AW2002.2SAI.AI254604.PNT | 2SAI:AI254604.PNT | 20BBA02-05 | 20BBA02 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 623.3203 | ok
1500 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0607-07 | OPC.AW2002.2SAI.AI254702.PNT | 2SAI:AI254702.PNT | 20BBA04-01 | CURRENT MEASUREMENT OF SST LV SIDE | AI | 0 | 3000 | A | [6 empty] | -6.3281 | no
1501 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0608-09 | OPC.AW2002.2SAI.AI254606.PNT | 2SAI:AI254606.PNT | 20BBA07-01 | VOLTAGE MEASUREMENT | AI | 0 | 7 | kV | [6 empty] | 6.201 | ok
1502 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0610-06 | OPC.AW2002.2SAI.AI254704.PNT | 2SAI:AI254704.PNT | 20BBA11-05 | 20BBA11 BREAKER CURRENT MESUREMENT | AI | 0 | 300 | A | [6 empty] | 18.2637 | ok
1503 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0610-06 | OPC.AW2002.2SAI.AI254705.PNT | 2SAI:AI254705.PNT | 20BBA11-10 | 20BFD01 BREAKER CURRENT MEASUREMENT | AI | 0 | 4000 | A | [6 empty] | 226.3281 | ok
1504 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0608-07 | OPC.AW2002.2SAI.AI254605.PNT | 2SAI:AI254605.PNT | 20BBB02-05 | 20BBB02 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 570.9961 | ok
1505 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0607-07 | OPC.AW2002.2SAI.AI254703.PNT | 2SAI:AI254703.PNT | 20BBB04-01 | CURRENT MEASUREMENT OF SST LV SIDE | AI | 0 | 3000 | A | [6 empty] | 0.23438 | ok
1506 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0608-13 | OPC.AW2002.2SAI.AI254701.PNT | 2SAI:AI254701.PNT | 20BBB06-05 | 20BBB06 BREAKER CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 78.5645 | ok
1507 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0608-10 | OPC.AW2002.2SAI.AI254607.PNT | 2SAI:AI254607.PNT | 20BBB07-01 | VOLTAGE MEASUREMENT | AI | 0 | 7 | kV | [6 empty] | 6.2628 | ok
1508 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0610-07 | OPC.AW2002.2SAI.AI254706.PNT | 2SAI:AI254706.PNT | 20BBB11-05 | 20BBB11 BREAKER CURRENT MESUREMENT | AI | 0 | 300 | A | [6 empty] | 26.502 | ok
1509 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 2 | MEDIUM VOLTAGE SYSTEM #2 | F296S-D0610-07 | OPC.AW2002.2SAI.AI254707.PNT | 2SAI:AI254707.PNT | 20BBB11-10 | 20BFE01 BREAKER CURRENT MEASUREMENT | AI | 0 | 4000 | A | [6 empty] | 338.75 | ok
1510 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-08 | OPC.AW2002.2TAI.AI261403.PNT | 2TAI:AI261403.PNT | 20BFA01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 387.459 | ok
1511 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261606.PNT | 2TAI:AI261606.PNT | 20BFA02A-05 | 20BFA02A BREAKER CURRENT MEASUREMENT | AI | 0 | 800 | A | [6 empty] | 8.6621 | ok
1512 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261702.PNT | 2TAI:AI261702.PNT | 20BFA02B-05 | 20BFA02B BREAKER CURRENT MEASUREMENT | AI | 0 | 600 | A | [6 empty] | 65.5078 | ok
1513 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261704.PNT | 2TAI:AI261704.PNT | 20BFA03A-05 | 20BFA03A BREAKER CURRENT MEASUREMENT | AI | 0 | 400 | A | [6 empty] | 14.4922 | ok
1514 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-03 | OPC.AW2002.2TAI.AI261501.PNT | 2TAI:AI261501.PNT | 20BFA03B-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 112.1191 | ok
1515 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-07 | OPC.AW2002.2TAI.AI261401.PNT | 2TAI:AI261401.PNT | 20BFA07-06 | 20BFA07 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 4.3359 | ok
1516 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-08 | OPC.AW2002.2TAI.AI261404.PNT | 2TAI:AI261404.PNT | 20BFB01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 385.9375 | ok
1517 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261701.PNT | 2TAI:AI261701.PNT | 20BFB02A-05 | 20BFB02A BREAKER CURRENT MEASUREMENT | AI | 0 | 800 | A | [6 empty] | 0.2832 | ok
1518 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261703.PNT | 2TAI:AI261703.PNT | 20BFB02B-05 | 20BFB02B BREAKER CURRENT MEASUREMENT | AI | 0 | 600 | A | [6 empty] | 0.17578 | ok
1519 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261705.PNT | 2TAI:AI261705.PNT | 20BFB03A-05 | 20BFB03A BREAKER CURRENT MEASUREMENT | AI | 0 | 400 | A | [6 empty] | 26.1523 | ok
1520 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-08 | OPC.AW2002.2TAI.AI261407.PNT | 2TAI:AI261407.PNT | 20BFC01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 387.1472 | ok
1521 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610-12 | OPC.AW2002.2TAI.AI261405.PNT | 2TAI:AI261405.PNT | 20BFD01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 381.6699 | ok
1522 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610- | OPC.AW2002.2TAI.AI262102.PNT | 2TAI:AI262102.PNT | 20BFD02-05 | SPARE（20BFD02 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1523 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610- | OPC.AW2002.2TAI.AI262103.PNT | 2TAI:AI262103.PNT | 20BFD03-05 | SPARE（20BFD03 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1524 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610- | OPC.AW2002.2TAI.AI262101.PNT | 2TAI:AI262101.PNT | 20BFD04-05 | SPARE（20BFD04 BREAKER CURRENT MEASUREMENT） | AI | 0 | 600 | A | [8 empty] | TIDAK DIPAKAI
1525 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610-12 | OPC.AW2002.2TAI.AI261406.PNT | 2TAI:AI261406.PNT | 20BFE01-01 | VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 382.0113 | ok
1526 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610- | OPC.AW2002.2TAI.AI262104.PNT | 2TAI:AI262104.PNT | 20BFE02-05 | SPARE（20BFE02 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1527 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610- | OPC.AW2002.2TAI.AI262105.PNT | 2TAI:AI262105.PNT | 20BFE03-05 | SPARE（20BFE03 BREAKER CURRENT MEASUREMENT） | AI | 0 | 2000 | A | [8 empty] | TIDAK DIPAKAI
1528 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0610-11 | OPC.AW2002.2TAI.AI261402.PNT | 2TAI:AI261402.PNT | 20BFE04-06 | 20BFE03 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | -8.8477 | no
1529 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255101.PNT | 2SAI:AI255101.PNT | 20BFT01-05 | 20BBA11 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 26.0801 | ok
1530 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255102.PNT | 2SAI:AI255102.PNT | 20BFT01-10 | 20BFA01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 310.7812 | ok
1531 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-06 | OPC.AW2002.2SAI.AI255103.PNT | 2SAI:AI255103.PNT | 20BFT02-05 | 20BBB11 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 42.9785 | ok
1532 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-06 | OPC.AW2002.2SAI.AI255104.PNT | 2SAI:AI255104.PNT | 20BFT02-10 | 20BFB01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 474.1406 | ok
1533 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255105.PNT | 2SAI:AI255105.PNT | 20BFT03-05 | 20BBA18 BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 8.0566 | ok
1534 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255106.PNT | 2SAI:AI255106.PNT | 20BFT03-10 | 20BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 52.8809 | ok
1535 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255107.PNT | 2SAI:AI255107.PNT | 20BFT03-11 | 20BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 62.5781 | ok
1536 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 3 | LOW VOLTAGE SYSTEM #2 | F296S-D0609-05 | OPC.AW2002.2SAI.AI255108.PNT | 2SAI:AI255108.PNT | 20BFT03-12 | 20BFC01 BREAKER CURRENT MEASUREMENT | AI | 0 | 3000 | A | [6 empty] | 67.5 | ok
1537 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-03 | OPC.AW2002.2TAI.AI261502.PNT | 2TAI:AI261502.PNT | 20BFB03B-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 114.5801 | ok
1538 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261706.PNT | 2TAI:AI261706.PNT | 20BFD03I-05 | 20BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 27.4902 | ok
1539 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261607.PNT | 2TAI:AI261607.PNT | 20BFD03I-06 | 20BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 22.168 | ok
1540 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0609-09 | OPC.AW2002.2TAI.AI261608.PNT | 2TAI:AI261608.PNT | 20BFD03I-07 | 20BFD03I BREAKER CURRENT MEASUREMENT | AI | 0 | 250 | A | [6 empty] | 33.1299 | ok
1541 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-12 | OPC.AW2002.2TAI.AI261508.PNT | 2TAI:AI261508.PNT | 20BMA01A-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 0.37852 | ok
1542 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-11 | OPC.AW2002.2TAI.AI261506.PNT | 2TAI:AI261506.PNT | 20BMA02-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 1.1426 | ok
1543 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-11 | OPC.AW2002.2TAI.AI261507.PNT | 2TAI:AI261507.PNT | 20BMA03-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 7.3242 | ok
1544 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-07 | OPC.AW2002.2TAI.AI261504.PNT | 2TAI:AI261504.PNT | 20BMB01B-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 381.6625 | ok
1545 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-09 | OPC.AW2002.2TAI.AI261707.PNT | 2TAI:AI261707.PNT | 20BMB02D-05 | 20BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 0.10254 | ok
1546 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-09 | OPC.AW2002.2TAI.AI262107.PNT | 2TAI:AI262107.PNT | 20BMB02D-06 | 20BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 0.11719 | ok
1547 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-09 | OPC.AW2002.2TAI.AI262108.PNT | 2TAI:AI262108.PNT | 20BMB02D-07 | 20BMB02D BREAKER CURRENT MEASUREMENT | AI | 0 | 300 | A | [6 empty] | 0.19531 | ok
1548 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615- | OPC.AW2002.2TAI.AI262106.PNT | 2TAI:AI262106.PNT | 20BMB03-01 | SPARE（CURRENT MEASUREMENT） | AI | 0 | 150 | A | [8 empty] | TIDAK DIPAKAI
1549 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-07 | OPC.AW2002.2TAI.AI261505.PNT | 2TAI:AI261505.PNT | 20BMC01A-01 | BUSBAR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | 380.8387 | ok
1550 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 4 | LOW VOLTAGE EMERGENCY SYSTEM #2 | F296S-D0615-06 | OPC.AW2002.2TAI.AI261503.PNT | 2TAI:AI261503.PNT | 20BMC02-01 | CURRENT MEASUREMENT | AI | 0 | 1500 | A | [6 empty] | 3.1641 | ok
1551 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 5 | UPS #2 | F296S-D0614-07 | OPC.AW2002.2TAI.AI262201.PNT | 2TAI:AI262201.PNT | 20BRA-01 | BUSBAR VOLTAGE | AI | 0 | 300 | V | [6 empty] | 221.0273 | ok
1552 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 5 | UPS #2 | F296S-D0614-07 | OPC.AW2002.2TAI.AI262202.PNT | 2TAI:AI262202.PNT | 20BRA-02 | BUSBAR FREQUENCY | AI | 0 | 60 | Hz | [6 empty] | 50.0498 | ok
1553 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 5 | UPS #2 | F296S-D0614-07 | OPC.AW2002.2TAI.AI262203.PNT | 2TAI:AI262203.PNT | 20BRA-03 | OUTPUT CURRENT | AI | 0 | 500 | A | [6 empty] | 16.9434 | ok
1554 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-05 | OPC.AW2002.2TAI.AI262204.PNT | 2TAI:AI262204.PNT | 20BTA01-01 | #1 CHARGER CURRENT | AI | 0 | 300 | A | [6 empty] | -3.5039 | no
1555 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-05 | OPC.AW2002.2TAI.AI262205.PNT | 2TAI:AI262205.PNT | 20BTA01-02 | COMMON CHARGER CURRENT | AI | 0 | 300 | A | [6 empty] | 0 | ok
1556 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-05 | OPC.AW2002.2TAI.AI262206.PNT | 2TAI:AI262206.PNT | 20BTA01-03 | BATERY BANK CURRENT | AI | 0 | 1250 | A | [6 empty] | 8.0078 | ok
1557 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-05 | OPC.AW2002.2TAI.AI262207.PNT | 2TAI:AI262207.PNT | 20BTA01-04 | ML VOLTAGE | AI | 0 | 300 | V | [6 empty] | 234.9492 | ok
1558 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262301.PNT | 2TAI:AI262301.PNT | 20BTB-01 | #1 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 7.582 | ok
1559 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262302.PNT | 2TAI:AI262302.PNT | 20BTB-02 | #2 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 0.52344 | ok
1560 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262303.PNT | 2TAI:AI262303.PNT | 20BTB-03 | #2 CHARGER CURRENT | AI | 0 | 200 | A | [6 empty] | 0 | ok | OUT OFF RANGE
1561 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262304.PNT | 2TAI:AI262304.PNT | 20BTB-04 | BATERY BANK 1 CURRENT | AI | 0 | 400 | A | [6 empty] | -3.8438 | no
1562 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262305.PNT | 2TAI:AI262305.PNT | 20BTB-05 | ML 1 VOLTAGE(0~150V) | AI | 0 | 150 | V | [6 empty] | 113.5547 | ok
1563 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262306.PNT | 2TAI:AI262306.PNT | 20BTB-06 | BATERY BANK 2 CURRENT | AI | 0 | 400 | A | [6 empty] | -4.5312 | no
1564 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 6 | DC POWER SYSTEM #2 | F296S-D0612-16 | OPC.AW2002.2TAI.AI262307.PNT | 2TAI:AI262307.PNT | 20BTB-07 | ML 2 VOLTAGE(0~150V) | AI | 0 | 150 | V | [6 empty] | 113.8799 | ok
1565 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 7 | EMERGENCY DIESEL GENERATOR #2 | F296S-D0615-13 | OPC.AW2002.2TAI.AI261601.PNT | 2TAI:AI261601.PNT | 20MJAGC001-01 | STATOR CURRENT MEASUREMENT | AI | 0 | 1200 | A | [6 empty] | 0.59375 | ok
1566 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 7 | EMERGENCY DIESEL GENERATOR #2 | F296S-D0615-13 | OPC.AW2002.2TAI.AI261602.PNT | 2TAI:AI261602.PNT | 20MJAGC001-02 | STATOR VOLTAGE MEASUREMENT | AI | 0 | 450 | V | [6 empty] | -0.050742 | no
1567 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 7 | EMERGENCY DIESEL GENERATOR #2 | F296S-D0615-13 | OPC.AW2002.2TAI.AI261603.PNT | 2TAI:AI261603.PNT | 20MJAGC001-03 | FREQUENCY MEASUREMENT | AI | 0 | 60 | Hz | [6 empty] | 45.2115 | ok
1568 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 7 | EMERGENCY DIESEL GENERATOR #2 | F296S-D0615-13 | OPC.AW2002.2TAI.AI261604.PNT | 2TAI:AI261604.PNT | 20MJAGC001-04 | ACTIVE POWER MEASUREMENT | AI | 0 | 800 | kW | [6 empty] | 8.1504 | ok
1569 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 7 | EMERGENCY DIESEL GENERATOR #2 | F296S-D0615-13 | OPC.AW2002.2TAI.AI261605.PNT | 2TAI:AI261605.PNT | 20MJAGC001-05 | REACTIVE POWER MEASUREMENT | AI | 0 | 800 | kVar | [6 empty] | 7.0459 | ok
1570 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2M_FULSTM2.AO162502.OUT | 2M_FULSTM2:AO162502.OUT | 00LCE13AA101XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1571 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2M_FULSTM.AO162802.OUT | 2M_FULSTM:AO162802.OUT | 00LCE13AA102XB11 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1572 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161504.PNT | 2MAI:AI161504.PNT | 00LCE13AA101XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1573 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2M_CNCURT.AO162503.OUT | 2M_CNCURT:AO162503.OUT | 20LCE13AA102XB11 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1574 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161505.PNT | 2MAI:AI161505.PNT | 20LCE13AA102XB12 | CONDENSER WATER CURTAIN PROTECTION WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok
1575 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161408.PNT | 2MAI:AI161408.PNT | 00LCE13AA102XB12 | FUEL OIL SYSTEM STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1576 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2EAI.AI051706.PNT | 2EAI:AI051706.PNT | 20HJF50CF201 | SUPPLYING OIL FLOW | AI | 0 | 40 | t/h | [6 empty] | 0 | ok
1577 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2EAI.AI051406.PNT | 2EAI:AI051406.PNT | 20HJF50CP201 | SUPPLYING OIL PRESSURE | AI | 0 | 4.0 | MPa | [6 empty] | 0.11164 | ok
1578 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2EAI.AI052303.PNT | 2EAI:AI052303.PNT | 20HJF60AA101XB12 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.83398 | no
1579 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2EAI.AI052104.PNT | 2EAI:AI052104.PNT | 20HJF60CF201 | RETURNED OIL FLOW | AI | 0 | 40 | t/h | [6 empty] | 0.0039062 | ok
1580 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2LAI.AI140607.PNT | 2LAI:AI140607.PNT | 20HJF60CP201 | RETURN OIL PRESSURE | AI | 0 | 1.0 | MPa | [6 empty] | 0.10617 | ok
1581 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2E_FUELOIL.AO052706.OUT | 2E_FUELOIL:AO052706.OUT | 20HJF60AA101XB11 | RETURN FUEL OIL PNEUMATIC CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1582 | 2 | UJPCT #2 | 11 | FUEL OIL SYSTEM #2 | 1 | FUEL OIL #2 | 50-F296S-J0201-17 | OPC.AW2002.2IAI.AI100304.PNT | 2IAI:AI100304.PNT | 20HJF50CT001 | SUPPLYING OIL TEMPERATURE | RTD | 0 | 100 | °C | [6 empty] | 30.2928 | ok
1583 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | F296S-J0201-06 | OPC.AW2002.2QAI.AI212101.PNT | 2QAI:AI212101.PNT | 20(20)LBG10CT001 | AUXILIARY STEAM HEADER TEMP | TC | 0 | 350 | C | [6 empty] | 0 | ok | OUT OFF RANGE
1584 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | F296S-J0201-06 | OPC.AW2002.2MAI.AI160603.PNT | 2MAI:AI160603.PNT | 20LBG10CP201 | AUXILIARY STEAM HEADER PRESS | AI | 0 | 1.2 | MPa | [6 empty] | 0.84832 | ok
1585 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | F296S-J0201-06 | OPC.AW2002.2M_AUXHDR.AO162401.OUT | 2M_AUXHDR:AO162401.OUT | 20LBG13AA101 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 63.9469 | ok
1586 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 1 | AUXILIARY STEAM #2 | F296S-J0201-06 | OPC.AW2002.2MAI.AI161401.PNT | 2MAI:AI161401.PNT | 20LBG13AA101XB12 | COLD REHEAT TO AUXILIARY HEADER SUPPLY STEAM CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 64.2676 | ok
1587 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | F296S-J0201-11 | OPC.AW2002.2OAI.AI191304.PNT | 2OAI:AI191304.PNT | 20MAW10AA001XB12 | REGULATING FLOW VALVE (RFV) POSITION | AI | 0 | 100 | % | [8 empty] | TIDAK DIPAKAI
1588 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | F296S-J0201-11 | OPC.AW2002.2QAI.AI213106.PNT | 2QAI:AI213106.PNT | 20MAW10CP201 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX PRESS | AI | 0 | 6.5 | MPa | [6 empty] | 0.13432 | ok
1589 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | F296S-J0201-11 | OPC.AW2002.2QAI.AI212201.PNT | 2QAI:AI212201.PNT | 20MAW10CT001 | TURBINE CYLINDER INTERLAYER HEAT INLET BOX TEMP | TC | 0 | 600 | C | [6 empty] | 221.0784 | ok
1590 | 2 | UJPCT #2 | 12 | AUXILIARY STEAM SYSTEM #2 | 2 | TURBINE PROPER AUXILIARY STEAM #2 | F296S-J0201-11 | OPC.AW2002.2MAI.AI163306.PNT | 2MAI:AI163306.PNT | 20MAW10CT002 | IP CYLINDER START STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 286.7881 | ok
1591 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2IAI.AI100601.PNT | 2IAI:AI100601.PNT | 20HJF71CB201B | 1# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.0097656 | ok
1592 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2IAI.AI100602.PNT | 2IAI:AI100602.PNT | 20HJF72CB201B | 2# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.052734 | ok
1593 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2IAI.AI100603.PNT | 2IAI:AI100603.PNT | 20HJF73CB201B | 3# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.18164 | no
1594 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2IAI.AI100604.PNT | 2IAI:AI100604.PNT | 20HJF74CB201B | 4# CORNER AB LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | -0.16992 | no
1595 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2HAI.AI091201.PNT | 2HAI:AI091201.PNT | 20HJF71CB202B | 1# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.22656 | ok
1596 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2HAI.AI091202.PNT | 2HAI:AI091202.PNT | 20HJF72CB202B | 2# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.13086 | ok
1597 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2HAI.AI091203.PNT | 2HAI:AI091203.PNT | 20HJF73CB202B | 3# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.25 | ok
1598 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2HAI.AI091204.PNT | 2HAI:AI091204.PNT | 20HJF74CB202B | 4# CORNER BC LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.27148 | ok
1599 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2GAI.AI071201.PNT | 2GAI:AI071201.PNT | 20HJF71CB203B | 1# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.30273 | ok
1600 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2GAI.AI071202.PNT | 2GAI:AI071202.PNT | 20HJF72CB203B | 2# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.34766 | ok
1601 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2GAI.AI071203.PNT | 2GAI:AI071203.PNT | 20HJF73CB203B | 3# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.30078 | ok
1602 | 2 | UJPCT #2 | 13 | IGNITION FIRING SYSYTEM#2 | 1 | FUEL OIL BURNER #2 | 50-F296S-J0201-17 | OPC.AW2002.2GAI.AI071204.PNT | 2GAI:AI071204.PNT | 20HJF74CB203B | 4# CORNER DE LAYER OIL FLAME INTENSITY | AI | 0 | 100 | % | [6 empty] | 0.16016 | ok
1603 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 1 | INTERMITTENT BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2JAI.AI112701.PNT | 2JAI:AI112701.PNT | 20EGR11AP001XB13 | INTERMITTENT BLOWDOWN PIT DISCHARGE PUMP A CURRENT | AI | 0 | 500 | A | [6 empty] | -1.2695 | no
1604 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 1 | INTERMITTENT BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2JAI.AI112702.PNT | 2JAI:AI112702.PNT | 20EGR12AP001XB13 | INTERMITTENT BLOWDOWN PIT DISCHARGE PUMP B CURRENT | AI | 0 | 500 | A | [6 empty] | -0.0097656 | no
1605 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 1 | INTERMITTENT BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI062105.PNT | 2FAI:AI062105.PNT | 20ERG00CL201 | INTERMITTENT BLOWDOWN PIT LEVEL | AI | 0 | 2050 | mm | [6 empty] | 1500 | ok
1606 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 1 | INTERMITTENT BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI060101.PNT | 2FAI:AI060101.PNT | 20ERG00CT001 | INTERMITTENT BLOWDOWN PIT TEMP. | RTD | 0 | 100 | ℃ | [6 empty] | 204 | ok
1607 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI062106.PNT | 2FAI:AI062106.PNT | 20LCQ10AA101XB12 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.0039062 | ok
1608 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI060506.PNT | 2FAI:AI060506.PNT | 20LCQ10CF201 | DRUM CONTINUOUS BLOWDOWN FLOW | AI | 0 | 30 | t/h | [6 empty] | 0 | ok
1609 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI060604.PNT | 2FAI:AI060604.PNT | 20LCQ10CL201 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL | AI | 0 | 10 | KPa | [6 empty] | 237.5977 | ok
1610 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI062107.PNT | 2FAI:AI062107.PNT | 20LCQ11AA101XB12 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -1.4121 | no
1611 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2FAI.AI062201.PNT | 2FAI:AI062201.PNT | 20LCQ20AA101XB12 | INTERMITTENT BLOWDOWN PIT INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 7.2812 | ok
1612 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2F_BLFLOW.AO063505.OUT | 2F_BLFLOW:AO063505.OUT | 20LCQ10AA101XB11 | DRUM CONTINUOUS BLOWDOWN CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1613 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2F_BLLVL.AO063506.OUT | 2F_BLLVL:AO063506.OUT | 20LCQ11AA101XB11 | BOILER CONTINUOUS BLOWDOWN FLASH TANK LEVEL CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 100 | ok
1614 | 2 | UJPCT #2 | 14 | DRAIN SYSTEM#2 | 2 | CONTINUOUS BLOWDOWN #2 | 50-F296S-J0201-16 | OPC.AW2002.2F_BLDPV.AO063507.OUT | 2F_BLDPV:AO063507.OUT | 20LCQ20AA101XB11 | INTERMITTENT BLOWDOWN PIT INLET CONTROL VALVE CONTROL | AO | 0 | 100 | % | [6 empty] | 0 | ok
1615 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2M_GLDHDRP.AO163204.OUT | 2M_GLDHDRP:AO163204.OUT | 20LBW12AA101XB11 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 22.0559 | ok | REVISI TAG
1616 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI162301.PNT | 2MAI:AI162301.PNT | 20LBW12AA101XB12 | AUXILIARY STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 20.6172 | ok
1617 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2M_GLDHDRP.AO163203.OUT | 2M_GLDHDRP:AO163203.OUT | 20LBW13AA101XB11 | HP STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1618 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI162205.PNT | 2MAI:AI162205.PNT | 20LBW13AA101XB12 | HP STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.11719 | ok
1619 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2M_GLDHDRP.AO163205.OUT | 2M_GLDHDRP:AO163205.OUT | 20LBW14AA101XB11 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1620 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI162302.PNT | 2MAI:AI162302.PNT | 20LBW14AA101XB12 | OVERFLOW STEAM CONTROL STATION INLET CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 90.4355 | ok
1621 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2M_GLDESUP.AO163206.OUT | 2M_GLDESUP:AO163206.OUT | 20LBW15AA101XB11 | LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 94.3489 | ok
1622 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI162303.PNT | 2MAI:AI162303.PNT | 20LBW15AA101XB12 | LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 93.0664 | ok
1623 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2M_GLDEBFP.AO162708.OUT | 2M_GLDEBFP:AO162708.OUT | 20LBW30AA404XB11 | BFP TURBINELP LP GLAND DESUPERHEAT WATER CONTROL VALVE CONTROL COMMANDBFP | AO | 0 | 100 | % | [6 empty] | 9.5539 | ok
1624 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI161302.PNT | 2MAI:AI161302.PNT | 20LBW30AA404XB12 | BFP TURBINELP LP GLAND DESUPERHEAT WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 9.9668 | ok
1625 | 2 | UJPCT #2 | 15 | GLAND SEAL STEAM SYSTEM #2 | 1 | GLAND SEAL STEAM #2 | F296S-J0201-10 | OPC.AW2002.2MAI.AI163304.PNT | 2MAI:AI163304.PNT | 20LBW30CT001 | BFP TURBINE GLAND MAIN PIPE TEMP(AFTER TEMPERATURE REDUCING DEVICE) | TC | 0 | 300 | C | [6 empty] | 153.1688 | ok
1626 | 2 | UJPCT #2 | 81 | TURBINE SEALING #2 | 3 | IP CYLINDER STARTUP STEAM PIPE #2 | F296S-J0201-07 | OPC.AW2002.2M_IPSTDESUP.AO162407.OUT | 2M_IPSTDESUP:AO162407.OUT | 20LCE12AA101XB11 | IP CYLINDER STARTUP STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1627 | 2 | UJPCT #2 | 81 | TURBINE SEALING #2 | 3 | IP CYLINDER STARTUP STEAM PIPE #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161503.PNT | 2MAI:AI161503.PNT | 20LCE12AA101XB12 | IP CYLINDER STARTUP STEAM DESUPERHEATER DESUPERHEATING WATER MOTORIZED CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.14258 | no
1628 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | MOT #2 | F296S-J0201-19 | OPC.AW2002.2OAI.AI191305.PNT | 2OAI:AI191305.PNT | 20MAV00CL201 | MAIN OIL TANK LEVEL | AI | 0 | 2200 | mm |  | 1240 | 1320 | 1820 | 2000 |  | 1388.9062 | ok
1629 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | MOT #2 | F296S-J0201-19 | OPC.AW2002.2OAI.AI192507.PNT | 2OAI:AI192507.PNT | 20MAV00CT001 | MAIN OIL TANK OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 52.546 | ok
1630 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 1 | MOT #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD116AIN.PNT_2 | 2ATC:2BD116AIN.PNT_2 | 20MAV00CT002 | MAIN OIL TANK OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 53.2735 | ok
1631 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | OIL COOLER #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI213305.PNT | 2QAI:AI213305.PNT | 20MAV15CP201 | OIL COOLER OUTLET MAIN PIPE OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.22003 | ok
1632 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | OIL COOLER #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI210504.PNT | 2QAI:AI210504.PNT | 20MAV15CT001 | OIL COOLER INLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 53.923 | ok
1633 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | OIL COOLER #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI210405.PNT | 2QAI:AI210405.PNT | 20MAV15CT002 | OIL COOLER OUTLET MAIN PIPE OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 39.828 | ok
1634 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | OIL COOLER #2 | F296S-J0201-14 | OPC.AW2002.2NAI.AI172403.PNT | 2NAI:AI172403.PNT | 20PGA34AA001XB12 | TURBINE LUBE-OIL COOLER COOLING RETURN WATER MANIFOLD MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 17.2891 | ok
1635 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 4 | OIL COOLER #2 | F296S-J0201-14 | OPC.AW2002.2RAI.AI230107.PNT | 2RAI:AI230107.PNT | 20PGA34CT001 | TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 34.6058 | ok
1636 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 6 | MOP #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI213304.PNT | 2QAI:AI213304.PNT | 20MAV00CP201 | MAIN OIL PUMP OUTLET PRESS | AI | 0 | 2.5 | MPa |  |  | 1.65 | 2.5 |  |  | 1.8622 | ok
1637 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 7 | AOP AC #2 | F296S-J0201-19 | OPC.AW2002.2OAI.AI191307.PNT | 2OAI:AI191307.PNT | 20MAV20AP101XB13 | TURBINE AC OIL PUMP CURRENT | AI | 0 | 150 | A |  |  |  | 82.1 |  |  | -0.087891 | no
1638 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 7 | AOP AC #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI213403.PNT | 2QAI:AI213403.PNT | 20MAV20CP201 | A.C. LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.00065625 | ok
1639 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 8 | JACKING OIL A #2 | F296S-J0201-40 | OPC.AW2002.2RAI.AI231205.PNT | 2RAI:AI231205.PNT | 20MAV18CP216 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 0.025879 | ok
1640 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 8 | JACKING OIL A #2 | F296S-J0201-40 | OPC.AW2002.2PAI.AI202802.PNT | 2PAI:AI202802.PNT | 20MAV30AP101XB13 | TURBINE JACKING OIL PUMP A CURRENT | AI | 0 | 150 | A |  |  |  | 103.3 |  |  | -0.16992 | no
1641 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 9 | JACKING OIL B #2 | F296S-J0201-40 | OPC.AW2002.2PAI.AI202803.PNT | 2PAI:AI202803.PNT | 20MAV40AP101XB13 | TURBINE JACKING OIL PUMP B CURRENT | AI | 0 | 150 | A |  |  |  | 103.3 |  |  | -0.046875 | no
1642 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 10 | LUBE OIL PIPE #2 | F296S-J0201-19 | OPC.AW2002.2VALVE.2AD111AIN.PNT_2 | 2VALVE:2AD111AIN.PNT_2 | 20MAV00CP204 | LUBE OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.18396 | ok
1643 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 10 | LUBE OIL PIPE #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD116AIN.PNT_1 | 2ATC:2BD116AIN.PNT_1 | 20MAV00CT042 | LUBE OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 39.7761 | ok
1644 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 11 | AOP DC #2 | F296S-J0201-19 | OPC.AW2002.2OAI.AI191306.PNT | 2OAI:AI191306.PNT | 20MAV10AP101XB13 | TURBINE DC EMERGENCY OIL PUMP CURRENT | AI | 0 | 150 | A |  |  |  | 114.2 |  |  | -0.079102 | no
1645 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 11 | AOP DC #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI213303.PNT | 2QAI:AI213303.PNT | 20MAV10CP201 | D.C. EMERGENCY LUBE-OIL PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.0016641 | ok
1646 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_1 | 2ATC:2BD115AIN.PNT_1 | 20MAV00CT005 | #1 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 50.4285 | ok
1647 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD116AIN.PNT_5 | 2ATC:2BD116AIN.PNT_5 | 20MAV00CT012 | #1 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 90.8947 | ok
1648 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD116AIN.PNT_6 | 2ATC:2BD116AIN.PNT_6 | 20MAV00CT013 | #1 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 76.7998 | ok
1649 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD103AIN.PNT_7 | 2ATC:2BD103AIN.PNT_7 | 20TSIDEH08 | SHAFT NO.1 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 39.3125 | ok
1650 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD103AIN.PNT_8 | 2ATC:2BD103AIN.PNT_8 | 20TSIDEH09 | SHAFT NO.1 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 67.7266 | ok
1651 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 1 | BEARING TURBIN NO.1 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_3 | 2ATC:2BD105AIN.PNT_3 | 20TSIDEH20 | BEARING COVER NO.1 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 35.0684 | ok
1652 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_2 | 2ATC:2BD115AIN.PNT_2 | 20MAV00CT006 | #2 BEARING OIL DRAIN TEMP | RTD | 0 | 120 | C | [6 empty] | 51.7795 | ok
1653 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD116AIN.PNT_7 | 2ATC:2BD116AIN.PNT_7 | 20MAV00CT014 | #2 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 99.0727 | ok
1654 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_1 | 2ATC:2BD117AIN.PNT_1 | 20MAV00CT015 | #2 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 88.2576 | ok
1655 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_1 | 2ATC:2BD104AIN.PNT_1 | 20TSIDEH10 | SHAFT NO.2 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 79.0312 | ok
1656 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_2 | 2ATC:2BD104AIN.PNT_2 | 20TSIDEH11 | SHAFT NO.2 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 133.5547 | ok
1657 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 2 | BEARING TURBIN NO.2 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_4 | 2ATC:2BD105AIN.PNT_4 | 20TSIDEH21 | BEARING COVER NO.2 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 10.5835 | ok
1658 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_3 | 2ATC:2BD115AIN.PNT_3 | 20MAV00CT010 | #3 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 56.8849 | ok
1659 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_2 | 2ATC:2BD117AIN.PNT_2 | 20MAV00CT016 | #3 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 63.0685 | ok
1660 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_3 | 2ATC:2BD117AIN.PNT_3 | 20MAV00CT017 | #3 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 56.5601 | ok
1661 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_3 | 2ATC:2BD104AIN.PNT_3 | 20TSIDEH12 | SHAFT NO.3 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 87.5156 | ok
1662 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_4 | 2ATC:2BD104AIN.PNT_4 | 20TSIDEH13 | SHAFT NO.3 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 85.9688 | ok
1663 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 3 | BEARING TURBIN NO.3 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_5 | 2ATC:2BD105AIN.PNT_5 | 20TSIDEH22 | BEARING COVER NO.3 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 33.9087 | ok
1664 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD115AIN.PNT_4 | 2ATC:2BD115AIN.PNT_4 | 20MAV00CT011 | #4 BEARING OIL RETURN TEMP | RTD | 0 | 120 | C | [6 empty] | 56.8459 | ok
1665 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_4 | 2ATC:2BD117AIN.PNT_4 | 20MAV00CT018 | #4 BEARING METAL TEMP(LEFT) | RTD | 0 | 120 | C | [6 empty] | 69.5639 | ok
1666 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD117AIN.PNT_5 | 2ATC:2BD117AIN.PNT_5 | 20MAV00CT019 | #4 BEARING METAL TEMP(RIGHT) | RTD | 0 | 120 | C | [6 empty] | 56.8979 | ok
1667 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_5 | 2ATC:2BD104AIN.PNT_5 | 20TSIDEH14 | SHAFT NO.4 (X DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 89.4609 | ok
1668 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD104AIN.PNT_6 | 2ATC:2BD104AIN.PNT_6 | 20TSIDEH15 | SHAFT NO.4 (Y DIRECTION)VIBRATION OUTPUT (4~20mA) | AI | 0 | 400 | um | [6 empty] | 58.7109 | ok
1669 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 4 | BEARING TURBIN NO.4 #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD105AIN.PNT_6 | 2ATC:2BD105AIN.PNT_6 | 20TSIDEH23 | BEARING COVER NO.4 VIBRATION OUTPUT (4~20mA) | AI | 0 | 125 | um | [6 empty] | 19.314 | ok
1670 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI210804.PNT | 2QAI:AI210804.PNT | 20MAV00CT007 | POSITION THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 47.0639 | ok
1671 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI210505.PNT | 2QAI:AI210505.PNT | 20MAV00CT008 | THRUST BEARING OIL DRAIN TEMP | RTD | 0 | 150 | C | [8 empty] | TIDAK DIPAKAI
1672 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2QAI.AI210805.PNT | 2QAI:AI210805.PNT | 20MAV00CT009 | WORK THRUST PAD OIL DRAIN TEMP | RTD | 0 | 100 | C | [6 empty] | 48.6488 | ok
1673 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_4 | 2ATC:2BD113AIN.PNT_4 | 20MAV00CT020 | #1 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 60.8731 | ok
1674 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_5 | 2ATC:2BD113AIN.PNT_5 | 20MAV00CT021 | #2 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 58.158 | ok
1675 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_6 | 2ATC:2BD113AIN.PNT_6 | 20MAV00CT022 | #3 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 56.1185 | ok
1676 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_7 | 2ATC:2BD113AIN.PNT_7 | 20MAV00CT023 | #4 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 55.8976 | ok
1677 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_8 | 2ATC:2BD113AIN.PNT_8 | 20MAV00CT024 | #5 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 58.5997 | ok
1678 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_1 | 2ATC:2BD114AIN.PNT_1 | 20MAV00CT025 | #6 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 63.0815 | ok
1679 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_2 | 2ATC:2BD114AIN.PNT_2 | 20MAV00CT026 | #7 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 73.5131 | ok
1680 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_3 | 2ATC:2BD114AIN.PNT_3 | 20MAV00CT027 | #8 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 66.7059 | ok
1681 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_4 | 2ATC:2BD114AIN.PNT_4 | 20MAV00CT028 | #9 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 67.0177 | ok
1682 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_5 | 2ATC:2BD114AIN.PNT_5 | 20MAV00CT029 | #10 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 61.1589 | ok
1683 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD114AIN.PNT_6 | 2ATC:2BD114AIN.PNT_6 | 20MAV00CT030 | #11 WORK THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 63.0815 | ok
1684 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_1 | 2ATC:2BD112AIN.PNT_1 | 20MAV00CT031 | #1 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 47.7784 | ok
1685 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_2 | 2ATC:2BD112AIN.PNT_2 | 20MAV00CT032 | #2 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 47.1289 | ok
1686 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_3 | 2ATC:2BD112AIN.PNT_3 | 20MAV00CT033 | #3 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 50.6623 | ok
1687 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_4 | 2ATC:2BD112AIN.PNT_4 | 20MAV00CT034 | #4 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 49.2334 | ok
1688 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_5 | 2ATC:2BD112AIN.PNT_5 | 20MAV00CT035 | #5 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 52.507 | ok
1689 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_6 | 2ATC:2BD112AIN.PNT_6 | 20MAV00CT036 | #6 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 47.5316 | ok
1690 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_7 | 2ATC:2BD112AIN.PNT_7 | 20MAV00CT037 | #7 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 46.2585 | ok
1691 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD112AIN.PNT_8 | 2ATC:2BD112AIN.PNT_8 | 20MAV00CT038 | #8 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 47.1548 | ok
1692 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_1 | 2ATC:2BD113AIN.PNT_1 | 20MAV00CT039 | #9 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 46.3884 | ok
1693 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_2 | 2ATC:2BD113AIN.PNT_2 | 20MAV00CT040 | #10 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 46.6612 | ok
1694 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD113AIN.PNT_3 | 2ATC:2BD113AIN.PNT_3 | 20MAV00CT041 | #11 POSITION THRUST PAD TEMP | RTD | 0 | 120 | C | [6 empty] | 50.9611 | ok
1695 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD124AIN.PNT_1 | 2ATC:2BD124AIN.PNT_1 | 20TSIDEH03 | AXIAL DISPLACEMENT NO.1 OUTPUT | AI | -2 | 2 | um | [6 empty] | -0.32531 | ok
1696 | 2 | UJPCT #2 | 83 | TURBINE BEARING #2 | 5 | THRUST BEARING TURBIN #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD124AIN.PNT_2 | 2ATC:2BD124AIN.PNT_2 | 20TSIDEH04 | AXIAL DISPLACEMENT NO.2 OUTPUT (4~20mA) | AI | -2 | 2 | um | [6 empty] | -0.31109 | ok
1697 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-08 | OPC.AW2002.2R_HBP.AO232404.OUT | 2R_HBP:AO232404.OUT | 20LAB21AA101XB11 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1698 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-08 | OPC.AW2002.2RAI.AI232206.PNT | 2RAI:AI232206.PNT | 20LAB21AA101XB12 | HP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.57422 | no
1699 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-08 | OPC.AW2002.2RAI.AI231304.PNT | 2RAI:AI231304.PNT | 20LAB21CP201 | HP BYPASS DESUPERHEATING WATER PRESS | AI | 0 | 25 | MPa | [6 empty] | 2.4443 | ok
1700 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231207.PNT | 2RAI:AI231207.PNT | 20LBA30CP201 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 25 | MPa | [6 empty] | 10.022 | ok
1701 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231302.PNT | 2RAI:AI231302.PNT | 20LBA30CP202 | HP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 25 | MPa | [6 empty] | 10.022 | ok
1702 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230606.PNT | 2RAI:AI230606.PNT | 20LBA30CT001 | HP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 522.3323 | ok
1703 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231303.PNT | 2RAI:AI231303.PNT | 20LBC30CP201 | HP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.3961 | ok
1704 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230706.PNT | 2RAI:AI230706.PNT | 20LBC30CT001 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 309.4772 | ok
1705 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230607.PNT | 2RAI:AI230607.PNT | 20LBC30CT002 | HP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 310.4586 | ok
1706 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2R_HBP.AO232401.OUT | 2R_HBP:AO232401.OUT | 20LBF10AA101XB11 | HP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1707 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 9 | HP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI232304.PNT | 2RAI:AI232304.PNT | 20LBF10AA101XB12 | HP BYPASS PRESS CONTROL VALVE CONTROL POSITION | AI | 0 | 100 | % | [6 empty] | 0.50039 | ok
1708 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231206.PNT | 2RAI:AI231206.PNT | 20LBB30CP201 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.2386 | ok
1709 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231107.PNT | 2RAI:AI231107.PNT | 20LBB30CP202 | LP BYPASS VALVE FRONT STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.2405 | ok
1710 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230704.PNT | 2RAI:AI230704.PNT | 20LBB30CT001 | LP BYPASS VALVE FRONT STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 326.3849 | ok
1711 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231301.PNT | 2RAI:AI231301.PNT | 20LBB40CP201 | LP BYPASS VALVE REAR STEAM PRESS | AI | 0 | 1 | MPa | [6 empty] | -0.0029492 | no
1712 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230605.PNT | 2RAI:AI230605.PNT | 20LBB40CT001 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 44.6454 | ok
1713 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI230705.PNT | 2RAI:AI230705.PNT | 20LBB40CT002 | LP BYPASS VALVE REAR STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 44.6905 | ok
1714 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI163301.PNT | 2MAI:AI163301.PNT | 20LBB41CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CONDENSER PIPE 1 TEMP | TC | 0 | 600 | C | [6 empty] | 44.537 | ok
1715 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI163302.PNT | 2MAI:AI163302.PNT | 20LBB42CT001 | THE THIRD-STAGE LP-BYPASS TEMPERATURE AND PRESSURE REDUCER TO CONDENSER PIPE 2 TEMP | TC | 0 | 600 | C | [6 empty] | 44.5067 | ok
1716 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2M_LP3RD_1.AO162504.OUT | 2M_LP3RD_1:AO162504.OUT | 20LCE16AA101XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 1 CONTROL COMM | AO | 0 | 100 | % | [6 empty] | 100 | ok
1717 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161506.PNT | 2MAI:AI161506.PNT | 20LCE16AA101XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 1 POSITION | AI | 0 | 100 | % | [6 empty] | 100 | ok
1718 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2M_LP3RD_2.AO162601.OUT | 2M_LP3RD_2:AO162601.OUT | 20LCE16AA102XB11 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 2 CONTROL COMMA | AO | 0 | 100 | % | [6 empty] | 100 | ok
1719 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2MAI.AI161603.PNT | 2MAI:AI161603.PNT | 20LCE16AA102XB12 | 3rd STAGE LP BYPASS TEMPERATURE AND PRESSURE REDUCER DESUPERHEATING WATER CONTROL VALVE 2 POSITION | AI | 0 | 100 | % | [6 empty] | 0 | ok
1720 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2R_LBP.AO232403.OUT | 2R_LBP:AO232403.OUT | 20LCE17AA101XB11 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1721 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-07 | OPC.AW2002.2RAI.AI232305.PNT | 2RAI:AI232305.PNT | 20LCE17AA101XB12 | LP BYPASS DESUPERHEATING WATER CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | -0.082031 | no
1722 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2R_LBP.AO232402.OUT | 2R_LBP:AO232402.OUT | 20MAN10AA101XB11 | LP BYPASS PRESS CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1723 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 10 | LP BYPASS VALVE #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI232205.PNT | 2RAI:AI232205.PNT | 20MAN10AA101XB12 | LP BYPASS PRESS CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.54648 | ok
1724 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 11 | BY PASS HYDRAULIC STATION #2 | F296S-J0201-41 | OPC.AW2002.2RAI.AI232306.PNT | 2RAI:AI232306.PNT | 20LBF20GC001AI01 | BYPASS HYDRAULIC OIL STATION OIL LEVEL | AI | 0 | 580 | mm | [6 empty] | 419.6844 | ok
1725 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 11 | BY PASS HYDRAULIC STATION #2 | F296S-J0201-41 | OPC.AW2002.2RAI.AI232207.PNT | 2RAI:AI232207.PNT | 20LBF20GC001AI02 | BYPASS HYDRAULIC OIL STATION OIL PRESS. | AI | 0 | 27.6 | MPa | [6 empty] | 15.4123 | ok
1726 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 11 | BY PASS HYDRAULIC STATION #2 | F296S-J0201-41 | OPC.AW2002.2RAI.AI230502.PNT | 2RAI:AI230502.PNT | 20LBF20GC001AI03 | BYPASS HYDRAULIC OIL STATION OIL TANK TEMP | RTD | 0 | 100 | C | [6 empty] | 54.3777 | ok
1727 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 13 | FLUID CONTROL SYSTEM #2 | F296S-J0201-23(2) | OPC.AW2002.2VALVE.2AD112AIN.PNT_2 | 2VALVE:2AD112AIN.PNT_2 | 20MAX10CP201 | CONTROL FLUID MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 14.2603 | ok
1728 | 2 | UJPCT #2 | 84 | HYDRAULIC SYSTEM #2 | 13 | FLUID CONTROL SYSTEM #2 | F296S-J0201-23(2) | OPC.AW2002.2ATC.2BD115AIN.PNT_7 | 2ATC:2BD115AIN.PNT_7 | 20MAX10CT001 | CONTROL FLUID TANK OIL TEMP | RTD | 0 | 120 | C | [6 empty] | 44.8555 | ok
1729 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 2 | FLUID CONTROL SYSTEM #2 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.AW2002.2ATC.2BD124AIN.PNT_4 | 2ATC:2BD124AIN.PNT_4 | 20MAX20AA001XB12 | MSV2 POSITION | AI | 0 | 100 | % | [6 empty] | 99.6855 | ok
1730 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 2 | FLUID CONTROL SYSTEM #2 - HP MAIN STOP VALVE NO.2 (MSV2) | F296S-J0201-04 | OPC.AW2002.2ATC.2BD12405AOUT.OUT | 2ATC:2BD12405AOUT.OUT | 20MAX20AA001XB11 | MSV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1731 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 3 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD111AIN.PNT_4 | 2VALVE:2AD111AIN.PNT_4 | 20MAX10AA102XB12 | CV4 POSITION | AI | 0 | 100 | % | [6 empty] | -0.10156 | no
1732 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 3 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.4 (CV4) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD11105AOUT.OUT | 2VALVE:2AD11105AOUT.OUT | 20MAX10AA102XB11 | CV4 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | -0.044537 | no
1733 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 4 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD106AIN.PNT_4 | 2VALVE:2AD106AIN.PNT_4 | 20MAX10AA101XB12 | CV1 POSITION | AI | 0 | 100 | % | [6 empty] | 99.1074 | ok
1734 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 4 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.1 (CV1) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD10605AOUT.OUT | 2VALVE:2AD10605AOUT.OUT | 20MAX10AA101XB11 | CV1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1735 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 5 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD107AIN.PNT_4 | 2VALVE:2AD107AIN.PNT_4 | 20MAX20AA101XB12 | CV2 POSITION | AI | 0 | 100 | % | [6 empty] | 99.7637 | ok
1736 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 5 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.2 (CV2) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD10705AOUT.OUT | 2VALVE:2AD10705AOUT.OUT | 20MAX20AA101XB11 | CV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1737 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI212301.PNT | 2QAI:AI212301.PNT | 20LBA12CP202 | HP GOV VALVE STEAM PRESS | AI | 0 | 18 | MPa | [6 empty] | 9.8902 | ok
1738 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 6 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD108AIN.PNT_4 | 2VALVE:2AD108AIN.PNT_4 | 20MAX20AA102XB12 | CV3 POSITION | AI | 0 | 100 | % | [6 empty] | 31.9668 | ok
1739 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 6 | FLUID CONTROL SYSTEM #2 - HP CONTROL VALVE NO.3 (CV3) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD10805AOUT.OUT | 2VALVE:2AD10805AOUT.OUT | 20MAX20AA102XB11 | CV3 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 31.9401 | ok
1740 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 7 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW2002.2QAI.AI212302.PNT | 2QAI:AI212302.PNT | 20LBB11CP202 | IP GOV VALVE REAR STEAM PRESS (LEFT) | AI | 0 | 6 | MPa | [6 empty] | 2.1933 | ok
1741 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 7 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD112AIN.PNT_4 | 2VALVE:2AD112AIN.PNT_4 | 20MAB10AA001XB12 | ICV1 POSITION | AI | 0 | 100 | % | [6 empty] | 99.8359 | ok
1742 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 7 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD11205AOUT.OUT | 2VALVE:2AD11205AOUT.OUT | 20MAB10AA001XB11 | ICV1 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1743 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 8 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW2002.2QAI.AI212402.PNT | 2QAI:AI212402.PNT | 20LBB12CP202 | IP GOV VALVE REAR STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa | [6 empty] | 2.196 | ok
1744 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 8 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD113AIN.PNT_4 | 2VALVE:2AD113AIN.PNT_4 | 20MAB20AA001XB12 | ICV2 POSITION | AI | 0 | 100 | % | [6 empty] | 100.5605 | no
1745 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 8 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296S-J0201-04 | OPC.AW2002.2VALVE.2AD11305AOUT.OUT | 2VALVE:2AD11305AOUT.OUT | 20MAB20AA001XB11 | ICV2 CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 100 | ok
1746 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-K0606 | OPC.AW2002.2VALVE.2AD11106AOUT.OUT | 2VALVE:2AD11106AOUT.OUT | 20DEHDCSAO01 | TURBINE POSITION | AO | 0 | 100 | % | [6 empty] | 89.0352 | ok
1747 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-K0606 | OPC.AW2002.2EAI.AI052406.PNT | 2EAI:AI052406.PNT | 20DEHDCSAI01 | TURBINE LOAD | AI | 0 | 100 | % | [6 empty] | 89.1016 | ok
1748 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2VALVE.2AD111AIN.PNT_1 | 2VALVE:2AD111AIN.PNT_1 | 20LBA11CP201 | MAIN STEAM PRESS(LEFT) | AI | 0 | 18 | MPa | [6 empty] | 9.9893 | ok
1749 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD106AIN.PNT_1 | 2ATC:2BD106AIN.PNT_1 | 20LBA11CT001 | MAIN STEAM TEMPERATURE (LEFT) | TC | 0 | 600 | C | [6 empty] | 537.9603 | ok
1750 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2VALVE.2AD112AIN.PNT_1 | 2VALVE:2AD112AIN.PNT_1 | 20LBA12CP201 | MAIN STEAM PRESS(RIGHT) | AI | 0 | 18 | MPa | [6 empty] | 10.0016 | ok
1751 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD106AIN.PNT_2 | 2ATC:2BD106AIN.PNT_2 | 20LBA12CT001 | MAIN STEAM TEMPERATURE (RIGHT) | TC | 0 | 600 | C | [6 empty] | 539.3135 | ok
1752 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211101.PNT | 2QAI:AI211101.PNT | 20LBC11CT001 | HP EXHAUSTING PIPE(LEFT) TOP TEMP | TC | 0 | 600 | C | [6 empty] | 314.1952 | ok
1753 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211201.PNT | 2QAI:AI211201.PNT | 20LBC11CT002 | HP EXHAUSTING PIPE(LEFT) BOTTOM TEMP | TC | 0 | 600 | C | [6 empty] | 323.5114 | ok
1754 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211102.PNT | 2QAI:AI211102.PNT | 20LBC12CT001 | HP EXHAUSTING PIPE(RIGHT) TOP TEMP | TC | 0 | 600 | C | [6 empty] | 356.0208 | ok
1755 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211202.PNT | 2QAI:AI211202.PNT | 20LBC12CT002 | HP EXHAUSTING PIPE(RIGHT) BOTTOM TEMP | TC | 0 | 600 | C | [6 empty] | 282.6921 | ok
1756 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2VALVE.2AD107AIN.PNT_2 | 2VALVE:2AD107AIN.PNT_2 | 20MAA10CP201 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.1734 | ok
1757 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2M_MSTFLOW_1.SIGSEL2OUT.PNT | 2M_MSTFLOW_1:SIGSEL2OUT.PNT | 20MAA10CP202C1 | STEAM PRESSURE AFTER GOV STAGE SIGSEL | AI | 0 | 20 | MPa | [6 empty] | 7.1722 | ok
1758 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160402.PNT | 2MAI:AI160402.PNT | 20MAA10CP202 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.1722 | ok
1759 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160502.PNT | 2MAI:AI160502.PNT | 20MAA10CP203 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.1816 | ok
1760 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2MAI.AI160602.PNT | 2MAI:AI160602.PNT | 20MAA10CP204 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.1609 | ok
1761 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2RAI.AI231106.PNT | 2RAI:AI231106.PNT | 20MAA10CP205 | STEAM PRESS AFTER HP GOV STAGE | AI | 0 | 16 | MPa | [6 empty] | 7.1703 | ok
1762 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI212401.PNT | 2QAI:AI212401.PNT | 20MAA10CP206 | HP SIXTH STAGE STEAM PRESS | AI | 0 | 10 | MPa | [6 empty] | 3.7854 | ok
1763 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2VALVE.2AD108AIN.PNT_2 | 2VALVE:2AD108AIN.PNT_2 | 20MAA10CP207 | HP EXHAUSTING STEAM PRESS | AI | 0 | 5 | MPa | [6 empty] | 2.4586 | ok
1764 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD107AIN.PNT_2 | 2ATC:2BD107AIN.PNT_2 | 20MAA10CT001 | HP EXHAUSTING TEMP (UPPER) | TC | 0 | 600 | C | [6 empty] | 359.7934 | ok
1765 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD111AIN.PNT_1 | 2ATC:2BD111AIN.PNT_1 | 20MAA10CT002 | HP EXHAUSTING TEMP (LOWER) | TC | 0 | 600 | C | [6 empty] | 360.1323 | ok
1766 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD107AIN.PNT_1 | 2ATC:2BD107AIN.PNT_1 | 20MAA10CT003 | STEAM TEMP AFTER HP GOV STAGE | TC | 0 | 600 | C | [6 empty] | 500.6067 | ok
1767 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_5 | 2ATC:2BD108AIN.PNT_5 | 20MAA10CT004 | HP EXHAUSTING UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 686.2982 | no
1768 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_6 | 2ATC:2BD108AIN.PNT_6 | 20MAA10CT005 | HP EXHAUSTING BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 332.2417 | ok
1769 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD107AIN.PNT_4 | 2ATC:2BD107AIN.PNT_4 | 20MAA10CT006 | HP INNER CYLINDER UPPER HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 749.7255 | no
1770 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD107AIN.PNT_6 | 2ATC:2BD107AIN.PNT_6 | 20MAA10CT007 | HP INNER CYLINDER UPPER HALF OUTER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 518.2 | ok
1771 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD107AIN.PNT_5 | 2ATC:2BD107AIN.PNT_5 | 20MAA10CT008 | HP INNER CYLINDER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 516.6995 | ok
1772 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD107AIN.PNT_7 | 2ATC:2BD107AIN.PNT_7 | 20MAA10CT009 | HP INNER CYLINDER BOTTOM HALF OUTER WALL TEMP | TC | 0 | 600 | C | [6 empty] | 634.7625 | no
1773 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224101.PNT | 2QAI:AI224101.PNT | 20MAA10CT010 | HP INNER & OUTER CYLINDER INTERLAY BAFFLE PLATE FRONT TEMP | TC | 0 | 600 | C | [6 empty] | 364.1927 | ok
1774 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224102.PNT | 2QAI:AI224102.PNT | 20MAA10CT011 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 511.1064 | ok
1775 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224103.PNT | 2QAI:AI224103.PNT | 20MAA10CT012 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 510.0178 | ok
1776 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224104.PNT | 2QAI:AI224104.PNT | 20MAA10CT013 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 526.0518 | ok
1777 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224105.PNT | 2QAI:AI224105.PNT | 20MAA10CT014 | HP INNER CYLINDER UPPER HALF FLANGE INNER WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 503.2218 | ok
1778 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224106.PNT | 2QAI:AI224106.PNT | 20MAA10CT015 | HP INNER CYLINDER UPPER HALF FLANGE MIDDLE WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 510.2238 | ok
1779 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224107.PNT | 2QAI:AI224107.PNT | 20MAA10CT016 | HP INNER CYLINDER UPPER HALF FLANGE OUTER WALL TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 511.1652 | ok
1780 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD106AIN.PNT_7 | 2ATC:2BD106AIN.PNT_7 | 20MAA10CT017 | HP MSV INNER WALL METAL TEMP (LEFT) | TC | 0 | 600 | C | [6 empty] | 537.1659 | ok
1781 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD106AIN.PNT_5 | 2ATC:2BD106AIN.PNT_5 | 20MAA10CT018 | HP MSV OUTER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 521.8086 | ok
1782 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD106AIN.PNT_8 | 2ATC:2BD106AIN.PNT_8 | 20MAA10CT019 | HP MSV INNER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 537.0483 | ok
1783 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD106AIN.PNT_6 | 2ATC:2BD106AIN.PNT_6 | 20MAA10CT020 | HP MSV OUTER WALL METAL TEMP (RIGHT) | TC | 0 | 600 | C | [6 empty] | 500.3319 | ok
1784 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD111AIN.PNT_4 | 2ATC:2BD111AIN.PNT_4 | 20MAA10CT021 | HP MSCV INNER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 532.8039 | ok
1785 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD111AIN.PNT_5 | 2ATC:2BD111AIN.PNT_5 | 20MAA10CT022 | HP MSCV OUTER WALL METAL TEMP | TC | 0 | 600 | C | [6 empty] | 532.2155 | ok
1786 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224108.PNT | 2QAI:AI224108.PNT | 20MAA10CT023 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 527.0521 | ok
1787 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224201.PNT | 2QAI:AI224201.PNT | 20MAA10CT024 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 483.8947 | ok
1788 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224202.PNT | 2QAI:AI224202.PNT | 20MAA10CT025 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 468.2431 | ok
1789 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224203.PNT | 2QAI:AI224203.PNT | 20MAA10CT026 | HP/IP OUTER CYLINDER UPPER HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 494.8683 | ok
1790 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224204.PNT | 2QAI:AI224204.PNT | 20MAA10CT027 | HP/IP OUTER CYLINDER UPPER HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 531.3494 | ok
1791 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224205.PNT | 2QAI:AI224205.PNT | 20MAA10CT028 | HP/IP OUTER CYLINDER UPPER HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 478.5696 | ok
1792 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224206.PNT | 2QAI:AI224206.PNT | 20MAA10CT029 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 526.6421 | ok
1793 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224207.PNT | 2QAI:AI224207.PNT | 20MAA10CT030 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 403.4323 | ok
1794 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224208.PNT | 2QAI:AI224208.PNT | 20MAA10CT031 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 457.9008 | ok
1795 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224301.PNT | 2QAI:AI224301.PNT | 20MAA10CT032 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE INNER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 529.6191 | ok
1796 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224302.PNT | 2QAI:AI224302.PNT | 20MAA10CT033 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE MIDDLE TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 494.0208 | ok
1797 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-43 | OPC.AW2002.2QAI.AI224303.PNT | 2QAI:AI224303.PNT | 20MAA10CT034 | HP/IP OUTER CYLINDER BOTTOM HALF FLANGE OUTER TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 465.1596 | ok
1798 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-K0610 | OPC.AW2002.2RAI.AI231606.PNT | 2RAI:AI231606.PNT | 20TSIDCSAI01 | TURBINE SPEED (4~20mA) | AI | 0 | 4000 | rpm |  |  | 2850 | 3390 |  |  | 3003.8633 | ok
1799 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-19 | OPC.AW2002.2VALVE.2AD113AIN.PNT_1 | 2VALVE:2AD113AIN.PNT_1 | 20TSIDEH01 | ECCENTRICITY OUTPUT (4~20mA) | AI | 0 | 100 | um | [6 empty] | 78.0176 | ok
1800 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-19 | OPC.AW2002.2VALVE.2AD111AIN.PNT_3 | 2VALVE:2AD111AIN.PNT_3 | 20TSIDEH02 | HP/IP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | -7 | 9 | um | [6 empty] | 1.815 | ok
1801 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD103AIN.PNT_5 | 2ATC:2BD103AIN.PNT_5 | 20TSIDEH06 | HP CYLINDER(LEFT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm | [6 empty] | 12.1715 | ok
1802 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD103AIN.PNT_6 | 2ATC:2BD103AIN.PNT_6 | 20TSIDEH07 | HP CYLINDER(RIGHT) HEAT EXPANSION OUTPUT (4~20mA) | AI | 0 | 50 | mm | [6 empty] | 23.3834 | ok
1803 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 7 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD103AIN.PNT_1 | 2ATC:2BD103AIN.PNT_1 | 20LBB11CP201 | IP GOV VALVE FRONT STEAM PRESS (LEFT) | AI | 0 | 6 | MPa | [6 empty] | 2.2113 | ok
1804 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 7 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.1 (RCV1-ICV1) | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD106AIN.PNT_3 | 2ATC:2BD106AIN.PNT_3 | 20LBB11CT001 | REHEAT STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 540.5492 | ok
1805 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 8 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD103AIN.PNT_2 | 2ATC:2BD103AIN.PNT_2 | 20LBB12CP201 | IP GOV VALVE FRONT STEAM PRESS (RIGHT) | AI | 0 | 6 | MPa | [6 empty] | 2.2171 | ok
1806 | 2 | UJPCT #2 | 85 | TURBINE VALVE #2 | 8 | IP TURBINE #2 - REHEAT COMBINE VALVE NO.2 (RCV2-ICV2) | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD106AIN.PNT_4 | 2ATC:2BD106AIN.PNT_4 | 20LBB12CT001 | REHEAT STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 540.9611 | ok
1807 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2VALVE.2AD108AIN.PNT_3 | 2VALVE:2AD108AIN.PNT_3 | 20MAB10CP201 | IP EXHAUSTING STEAM PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.56861 | ok
1808 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI212303.PNT | 2QAI:AI212303.PNT | 20MAB10CP202 | IP THIRD STAGE STEAM PRESS | AI | 0 | 2 | MPa | [6 empty] | 1.1728 | ok
1809 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD107AIN.PNT_3 | 2ATC:2BD107AIN.PNT_3 | 20MAB10CT001 | IP EXHAUSTING STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 355.2717 | ok
1810 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_2 | 2ATC:2BD108AIN.PNT_2 | 20MAB10CT002 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 523.0787 | ok
1811 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_4 | 2ATC:2BD108AIN.PNT_4 | 20MAB10CT003 | HP/IP OUTER CYLINDER IP STEAM INLET BOTTOM HALF OUTER TEMP | TC | 0 | 600 | C | [6 empty] | 489.2749 | ok
1812 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_1 | 2ATC:2BD108AIN.PNT_1 | 20MAB10CT004 | HP/IP OUTER CYLINDER IP STEAM INLET UPPER HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 534.1406 | ok
1813 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_3 | 2ATC:2BD108AIN.PNT_3 | 20MAB10CT005 | HP/IP OUTER CYLINDER IP STEAM INLETA UPPER HALF OUTER TEMP | TC | 0 | 600 | C | [6 empty] | 524.2849 | ok
1814 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_8 | 2ATC:2BD108AIN.PNT_8 | 20MAB10CT006 | IP EXHAUSTING BOTTOM HALF INNER METAL TEMP | TC | 0 | 600 | C | [6 empty] | 318.4908 | ok
1815 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD108AIN.PNT_7 | 2ATC:2BD108AIN.PNT_7 | 20MAB10CT007 | IP EXHAUSTING UPPER HALF INNER METAL TEMP | TC | 0 | 600 | C | [6 empty] | 352.9985 | ok
1816 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD111AIN.PNT_3 | 2ATC:2BD111AIN.PNT_3 | 20MAB10CT008 | CLAPBOARD BOTTOM HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 532.8627 | ok
1817 | 2 | UJPCT #2 | 86 | TURBINE #2 | 2 | IP TURBINE SYSTEM #2 | F296Z-J0201-43 | OPC.AW2002.2ATC.2BD111AIN.PNT_2 | 2ATC:2BD111AIN.PNT_2 | 20MAB10CT009 | CLAPBOARD UPPER HALF INNER TEMP | TC | 0 | 600 | C | [6 empty] | 538.3643 | ok
1818 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD116AIN.PNT_3 | 2ATC:2BD116AIN.PNT_3 | 20MAC10CT001A | LP EXHAUSTING STEAM TEMP（FRONT & RIGHT） | RTD | 0 | 120 | C | [6 empty] | 45.479 | ok
1819 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2NAI.AI172501.PNT | 2NAI:AI172501.PNT | 20MAC10CT001B | LP EXHAUSTING STEAM TEMP(FRONT & RIGHT) | RTD | 0 | 150 | C |  |  |  | 80 | 110 |  | 45.6869 | ok
1820 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296Z-J0201-04 | OPC.AW2002.2ATC.2BD116AIN.PNT_4 | 2ATC:2BD116AIN.PNT_4 | 20MAC10CT002A | LP EXHAUSTING STEAM TEMP（BACK & LEFT） | RTD | 0 | 120 | C | [6 empty] | 45.5959 | ok
1821 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2NAI.AI172502.PNT | 2NAI:AI172502.PNT | 20MAC10CT002B | LP EXHAUSTING STEAM TEMP(REAR & LEFT) | RTD | 0 | 150 | C |  |  |  | 80 | 110 |  | 45.5959 | ok
1822 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211103.PNT | 2QAI:AI211103.PNT | 20MAC10CT003 | BACKWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 612 | no
1823 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211203.PNT | 2QAI:AI211203.PNT | 20MAC10CT004 | FORWARD 3st STAGE OUTLET EXTRACTION STEAM TEMP | TC | 0 | 600 | C | [6 empty] | 612 | no
1824 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211104.PNT | 2QAI:AI211104.PNT | 20MAC10CT005 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 120.511 | ok
1825 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211204.PNT | 2QAI:AI211204.PNT | 20MAC10CT006 | LP BACKWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 127.6204 | ok
1826 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211105.PNT | 2QAI:AI211105.PNT | 20MAC10CT007 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(LEFT) | TC | 0 | 600 | C | [6 empty] | 612 | no
1827 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-04 | OPC.AW2002.2QAI.AI211205.PNT | 2QAI:AI211205.PNT | 20MAC10CT008 | LP FORWARD 4st STAGE OUTLET EXTRACTION STEAM TEMP(RIGHT) | TC | 0 | 600 | C | [6 empty] | 612 | no
1828 | 2 | UJPCT #2 | 86 | TURBINE #2 | 3 | LP TURBINE SYSTEM #2 | F296S-J0201-19 | OPC.AW2002.2ATC.2BD124AIN.PNT_3 | 2ATC:2BD124AIN.PNT_3 | 20TSIDEH05 | LP CYLINDER DIFFERENTIAL EXPANSION OUTPUT (4~20mA) | AI | 0 | 16 | um | [6 empty] | 9.9234 | ok
1829 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI060703.PNT | 0DAI:AI060703.PNT | 20PAC11AP001XB13 | UNIT #2 CWP A CURRENT | AI | 0 | 300 | A | [6 empty] | 223.9277 | ok
1830 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104605.PNT | 0DAI:AI104605.PNT | 20PAA21CL201 | BEFORE UNIT #2 BAR SCREEN A WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 7 | ok
1831 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104605.PNT | 0DAI:AI104605.PNT | 20PAA21CL202 | AFTER UNIT #2 BAR SCREEN A WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 7 | ok | REVISI TAG
1832 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104603.PNT | 0DAI:AI104603.PNT | 20PAA31CL201 | BEFORE UNIT #2 TRAVELLING BAND A SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 8.2824 | ok
1833 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104604.PNT | 0DAI:AI104604.PNT | 20PAA31CL202 | AFTER UNIT #2 TRAVELLING BAND A SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 7 | ok
1834 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI105103.PNT | 0DAI:AI105103.PNT | 20PAB11CF201 | UNIT 2 CIRCULATING WATER OUTLET WATER FLOW | AI | 0 |  | t/h | [6 empty] | -1.5742 | no
1835 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104607.PNT | 0DAI:AI104607.PNT | 20PAB11GC001AI01 | UNIT #2 HYDRAULIC CONTROL BUTTERFLY VALVE A POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0.36914 | ok
1836 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104501.PNT | 0DAI:AI104501.PNT | 20PAC11CP201 | 2A# CIRCULATING WATER PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.19002 | ok
1837 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104101.PNT | 0DAI:AI104101.PNT | 20PAC11CT001 | 2A# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 85.3607 | ok
1838 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104201.PNT | 0DAI:AI104201.PNT | 20PAC11CT002 | 2A# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 84.828 | ok
1839 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104102.PNT | 0DAI:AI104102.PNT | 20PAC11CT003 | 2A# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 81.8792 | ok
1840 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104202.PNT | 0DAI:AI104202.PNT | 20PAC11CT004 | 2A# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 81.7492 | ok
1841 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104103.PNT | 0DAI:AI104103.PNT | 20PAC11CT005 | 2A# CIRCULATING WATER PUMP W PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 82.2039 | ok
1842 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104203.PNT | 0DAI:AI104203.PNT | 20PAC11CT006 | 2A# CIRCULATING WATER PUMP W PHASE STATOR WINGDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 82.7365 | ok
1843 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104106.PNT | 0DAI:AI104106.PNT | 20PAC11CT007 | 2A# CIRCULATING WATER PUMP LOWER BEARING TEMP | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 49.9348 | ok
1844 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104104.PNT | 0DAI:AI104104.PNT | 20PAC11CT008 | 2A# CIRCULATING WATER PUMP THRUST BEARING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 57.0798 | ok
1845 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104204.PNT | 0DAI:AI104204.PNT | 20PAC11CT009 | 2A# CIRCULATING WATER PUMP THRUST BEARING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 56.833 | ok
1846 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104105.PNT | 0DAI:AI104105.PNT | 20PAC11CT010 | 2A# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 73.0194 | ok
1847 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104205.PNT | 0DAI:AI104205.PNT | 20PAC11CT011 | 2A# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 72.9025 | ok
1848 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104601.PNT | 0DAI:AI104601.PNT | 20PAC11CY201X | 2A# CIRCULATING WATER PUMP BEARING X DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 9.9788 | no
1849 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 3 | CIRCULATING WATER PUMP #2 A | K0802-02 | OPC.AW0003.0DAI.AI104602.PNT | 0DAI:AI104602.PNT | 20PAC11CY201Y | 2A# CIRCULATING WATER PUMP BEARING Y DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 11.649 | no
1850 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI060608.PNT | 0DAI:AI060608.PNT | 20PAC12AP001XB13 | UNIT #2 CWP B CURRENT | AI | 0 | 300 | A | [6 empty] | -0.42188 | no
1851 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104705.PNT | 0DAI:AI104705.PNT | 20PAA22CL201 | BEFORE UNIT #2 BAR SCREEN B WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 7 | ok
1852 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104705.PNT | 0DAI:AI104705.PNT | 20PAA22CL202 | AFTER UNIT #2 BAR SCREEN B WITH RAKING DEVICE LEVEL | AI | 0 | 10 | m | [6 empty] | 7 | ok | REVISI TAG
1853 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104704.PNT | 0DAI:AI104704.PNT | 20PAA32CL201 | BEFORE UNIT #2 TRAVELLING BAND B SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 7 | ok | REVISI TAG
1854 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104704.PNT | 0DAI:AI104704.PNT | 20PAA32CL202 | AFTER UNIT #2 TRAVELLING BAND B SCREEN LEVEL | AI | 0 | 12 | m | [6 empty] | 7 | ok
1855 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104707.PNT | 0DAI:AI104707.PNT | 20PAB12GC001AI01 | UNIT #2 HYDRAULIC BUTTERFLY VAVLE B POSITION FEEDBACK | AI | 0 | 100 | % | [6 empty] | 0.43359 | ok
1856 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104502.PNT | 0DAI:AI104502.PNT | 20PAC12CP201 | 2B# CIRCULATING WATER PUMP OUTLET PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.0025195 | ok
1857 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104301.PNT | 0DAI:AI104301.PNT | 20PAC12CT001 | 2B# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 36.8012 | ok
1858 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104401.PNT | 0DAI:AI104401.PNT | 20PAC12CT002 | 2B# CIRCULATING WATER PUMP U PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 33.9042 | ok
1859 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104302.PNT | 0DAI:AI104302.PNT | 20PAC12CT003 | 2B# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 34.0601 | ok
1860 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104402.PNT | 0DAI:AI104402.PNT | 20PAC12CT004 | 2B# CIRCULATING WATER PUMP V PHASE STATOR WINDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 36.3335 | ok
1861 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104303.PNT | 0DAI:AI104303.PNT | 20PAC12CT005 | 2B# CIRCULATING WATER PUMP W PHASE STATOR WINDING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 34.0342 | ok
1862 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104403.PNT | 0DAI:AI104403.PNT | 20PAC12CT006 | 2B# CIRCULATING WATER PUMP W PHASE STATOR WINGDING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 130 | 140 |  | 33.5925 | ok
1863 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104306.PNT | 0DAI:AI104306.PNT | 20PAC12CT007 | 2B# CIRCULATING WATER PUMP LOWER BEARING TEMP | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 30.1239 | ok
1864 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104304.PNT | 0DAI:AI104304.PNT | 20PAC12CT008 | 2B# CIRCULATING WATER PUMP THRUST BEARING TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 31.3321 | ok
1865 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104404.PNT | 0DAI:AI104404.PNT | 20PAC12CT009 | 2B# CIRCULATING WATER PUMP THRUST BEARING TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 31.7478 | ok
1866 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104305.PNT | 0DAI:AI104305.PNT | 20PAC12CT010 | 2B# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP1 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 31.2281 | ok
1867 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104405.PNT | 0DAI:AI104405.PNT | 20PAC12CT011 | 2B# CIRCULATING WATER PUMP UPPER BEARING BUSH TEMP2 | RTD | 0 | 150 | ℃ |  |  |  | 80 | 85 |  | 25.6941 | ok
1868 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104701.PNT | 0DAI:AI104701.PNT | 20PAC12CY201X | 2B# CIRCULATING WATER PUMP BEARING X DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | 21.0252 | no
1869 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI104702.PNT | 0DAI:AI104702.PNT | 20PAC12CY201Y | 2B# CIRCULATING WATER PUMP BEARING Y DIRECTION VIBRATION | AI | 0 | 7 | mm/s | [6 empty] | -0.3665 | no
1870 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2E_IDF.SIGSEL1OUT.PNT | 2E_IDF:SIGSEL1OUT.PNT | 20H10CP201C1 | FURNACE PRESSURE | AI | -250 | 250 | Pa | [6 empty] | -39.3662 | ok
1871 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2E_AIRFLOW.FURA1AIN.PNT | 2E_AIRFLOW:FURA1AIN.PNT | 20H10CF205C1 | SEC A OUT FLOW | AI | 0 | 600 | T/H |  | 45 | 180 |  |  |  | 282.9879 | ok
1872 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2E_AIRFLOW.FURB1AIN.PNT | 2E_AIRFLOW:FURB1AIN.PNT | 20H20CF205C1 | SEC B OUT FLOW | AI | 0 | 600 | T/H |  | 45 | 180 |  |  |  | 248.3401 | ok
1873 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2E_FDF.CHARC1OUT.PNT | 2E_FDF:CHARC1OUT.PNT | 20H10CF201C1 | TOTAL AIR FLOW | AI | 0 | 1400 | T/H | [6 empty] | 972.2937 | ok
1874 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 | 50-F296S-J0201-33 | OPC.AW2002.2E_FUELC.CALCA1OUT.PNT | 2E_FUELC:CALCA1OUT.PNT | 20HFB10GC001C1 | COAL FLOW | AI | 0 | 300 | T/H | [6 empty] | 116.2145 | ok
1875 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 |  | 20H10CT907 | 20H10CT907 | 20H10CT907 | Diff Temp Side A Side B | CALC | 0 | 700 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI142206.PNT)-(OPC.AW2002.2LAI.AI142306.PNT)
1876 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 |  | 20H10CT908 | 20H10CT908 | 20H10CT908 | Diff Temp Side A Side B | CALC | 0 | 700 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI142207.PNT)-(OPC.AW2002.2LAI.AI142307.PNT)
1877 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 7 | FURNACE #2 |  | 20H10CP904 | 20H10CP904 | 20H10CP904 | Diff Pressure Side A Side B | CALC | -300 | 300 | Pa | [8 empty] | (OPC.AW2002.2LAI.AI140304.PNT)-(OPC.AW2002.2LAI.AI140404.PNT)
1878 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20HAH11CT901 | 20HAH11CT901 | 20HAH11CT901 | Diff temp First stage superheated steam desupp | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI141701.PNT)-(AVG(OPC.AW2002.2FAI.AI060201.PNT);(OPC.AW2002.2FAI.AI060301.PNT))
1879 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20LAE41AA901XB | 20LAE41AA901XB | 20LAE41AA901XB | Diff ctrl and Poss of first stage desup | CALC | -100 | 100 | % | [8 empty] | (OPC.AW2002.2F_SH1.AO063502.OUT)-(OPC.AW2002.2FAI.AI061706.PNT)
1880 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20HAH21CT901 | 20HAH21CT901 | 20HAH21CT901 | Diff temp second stage superheated steam desupp A side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI141702.PNT)-(AVG(OPC.AW2002.2FAI.AI060202.PNT);(OPC.AW2002.2FAI.AI060203.PNT))
1881 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20HAH22CT901 | 20HAH22CT901 | 20HAH22CT901 | Diff temp second stage superheated steam desupp B side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI141703.PNT)-(AVG(OPC.AW2002.2FAI.AI060401.PNT);(OPC.AW2002.2FAI.AI060203.PNT))
1882 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20HAH21CT904 | 20HAH21CT904 | 20HAH21CT904 | Diff temp third stage superheated steam desupp A side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI141704.PNT)-(AVG(OPC.AW2002.2FAI.AI060204.PNT);(OPC.AW2002.2FAI.AI060303.PNT))
1883 | 2 | UJPCT #2 | 6 | BOILER & FURNACE SYSTEM #2 | 4 | SUPERHEATER #2 |  | 20HAH22CT904 | 20HAH22CT904 | 20HAH22CT904 | Diff temp third stage superheated steam desupp B side | CALC | -100 | 600 | ℃ | [8 empty] | (OPC.AW2002.2LAI.AI141705.PNT)-(AVG(OPC.AW2002.2FAI.AI060402.PNT);(OPC.AW2002.2FAI.AI060205.PNT))
1884 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 7 | GLAND STEAM CONDENSER #2 |  | 20LBW22CT901 | 20LBW22CT901 | 20LBW22CT901 | Delta Gland Main Pipe Temp | CALC | -100 | 300 | C | [8 empty] | (OPC.AW2002.2MAI.AI160102.PNT)-(OPC.AW2002.2QAI.AI212205.PNT)
1885 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 |  | 20LBS50CP901 | 20LBS50CP901 | 20LBS50CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.6 | 0.6 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212602.PNT)-(OPC.AW2002.2QAI.AI212503.PNT)
1886 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 |  | 20LCJ50CT902 | 20LCJ50CT902 | 20LCJ50CT902 | DCA LPH5 #2 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW2002.2QAI.AI212105.PNT )-(OPC.AW2002.2QAI.AI210106.PNT)
1887 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 14 | LP HEATER NO.5 #2 |  | 20LBS50CT902 | 20LBS50CT902 | 20LBS50CT902 | TTD LPH5 #2 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW2002.2QAI.AI211503.PNT)-(OPC.AW2002.2QAI.AI210107.PNT)
1888 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 |  | 20LBS60CP901 | 20LBS60CP901 | 20LBS60CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.4 | 0.4 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212603.PNT)-(OPC.AW2002.2QAI.AI212504.PNT)
1889 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 |  | 20LCJ60CT902 | 20LCJ60CT902 | 20LCJ60CT902 | DCA LPH6 #2 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW2002.2QAI.AI211706.PNT)-(OPC.AW2002.2QAI.AI210105.PNT)
1890 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 12 | LP HEATER NO.6 #2 |  | 20LBS60CT902 | 20LBS60CT902 | 20LBS60CT902 | TTD LPH6 #2 | CALC | -100 | 500 | C | [8 empty] | (OPC.AW2002.2QAI.AI211505.PNT)-(OPC.AW2002.2QAI.AI210106.PNT)
1891 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 |  | 20LBS70CP901 | 20LBS70CP901 | 20LBS70CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.1 | 0.15 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212604.PNT)-(OPC.AW2002.2QAI.AI212505.PNT)
1892 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 |  | 20LCJ70CT902 | 20LCJ70CT902 | 20LCJ70CT902 | DCA LPH7 #2 | CALC | -100 | 140 | C | [8 empty] | (OPC.AW2002.2QAI.AI212106.PNT)-(OPC.AW2002.2QAI.AI210105.PNT)
1893 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 10 | LP HEATER NO.7 #2 |  | 20LBS70CT902 | 20LBS70CT902 | 20LBS70CT902 | TTD LPH7 #2 | CALC | -100 | 140 | C | [8 empty] | (OPC.AW2002.2QAI.AI211606.PNT)-(OPC.AW2002.2QAI.AI210105.PNT)
1894 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 |  | 20LBS80CP901 | 20LBS80CP901 | 20LBS80CP901 | Diff steam press LP turbine side and LPH side | CALC | -0.1 | 0.15 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212605.PNT)-(OPC.AW2002.2QAI.AI212506.PNT)
1895 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 |  | 20LCJ80CT902 | 20LCJ80CT902 | 20LCJ80CT902 | DCA LPH8#2 | CALC | -100 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211707.PNT)-(OPC.AW2002.2QAI.AI210105.PNT)
1896 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 9 | LP HEATER NO.8 #2 |  | 20LBS80CT902 | 20LBS80CT902 | 20LBS80CT902 | TTD LPH8#2 | CALC | -100 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211607.PNT)-(OPC.AW2002.2QAI.AI210105.PNT)
1897 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 |  | 20PAH31CP901 | 20PAH31CP901 | 20PAH31CP901 | CONDENSER SIDE A CIRCULATING WATER DELTA PRESS | CALC | 0 | 0.2 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI213201.PNT)-(OPC.AW2002.2QAI.AI212707.PNT)
1898 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 |  | 20PAH31CT901 | 20PAH31CT901 | 20PAH31CT901 | CONDENSER SIDE A CIRCULATING WATER DELTA TEMP | CALC | 0 | 100 | C | [8 empty] | (OPC.AW2002.2QAI.AI210203.PNT)-(OPC.AW2002.2QAI.AI210202.PNT)
1899 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 |  | 20PAH32CP901 | 20PAH32CP901 | 20PAH32CP901 | CONDENSER SIDE B CIRCULATING WATER DELTA PRESS | CALC | 0 | 0.2 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI213107.PNT)-(OPC.AW2002.2QAI.AI213202.PNT)
1900 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 1 | CONDENSER #2 |  | 20PAH32CT901 | 20PAH32CT901 | 20PAH32CT901 | CONDENSER SIDE B CIRCULATING WATER DELTA TEMP | CALC | 0 | 100 | C | [8 empty] | (OPC.AW2002.2QAI.AI210302.PNT)-(OPC.AW2002.2QAI.AI210301.PNT)
1901 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A |  | 20PCC21CT905 | 20PCC21CT905 | 20PCC21CT905 | Average coil temp phase A CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI171105.PNT);(OPC.AW2002.2NAI.AI173404.PNT))
1902 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A |  | 20PCC21CT906 | 20PCC21CT906 | 20PCC21CT906 | Average coil temp phase B CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI171106.PNT);(OPC.AW2002.2NAI.AI173405.PNT))
1903 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 1 | SWBP #2A |  | 20PCC21CT907 | 20PCC21CT907 | 20PCC21CT907 | Average coil temp phase C CWB A | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI171107.PNT);(OPC.AW2002.2NAI.AI173406.PNT))
1904 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B |  | 20PCC22CT905 | 20PCC22CT905 | 20PCC22CT905 | Average coil temp phase A CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI173303.PNT);(OPC.AW2002.2NAI.AI173304.PNT))
1905 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B |  | 20PCC22CT906 | 20PCC22CT906 | 20PCC22CT906 | Average coil temp phase B CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI173305.PNT);(OPC.AW2002.2NAI.AI173306.PNT))
1906 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B |  | 20PCC22CT907 | 20PCC22CT907 | 20PCC22CT907 | Average coil temp phase C CWB B | CALC | -100 | 150 | C | [8 empty] | AVG((OPC.AW2002.2NAI.AI173307.PNT);(OPC.AW2002.2NAI.AI173308.PNT))
1907 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 |  | 20PGA40CT901 | 20PGA40CT901 | 20PGA40CT901 | Delta T BOILER#2 | CALC | 0 | 50 | C | [8 empty] | (OPC.AW2002.2RAI.AI230103.PNT)-(OPC.AW2002.2RAI.AI230203.PNT)
1908 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 7 | CLOSED COOLING WATER PIPE #2 |  | 20PGA31CT901 | 20PGA31CT901 | 20PGA31CT901 | Delta T TURBINE#2 | CALC | 0 | 50 | C | [8 empty] | (OPC.AW2002.2RAI.AI230204.PNT)-(OPC.AW2002.2RAI.AI230106.PNT)
1909 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 1 | CIRCULATING WATER PUMP #2 A |  | 20PAA21CL901 | 20PAA21CL901 | 20PAA21CL901 | DP LEVEL UNIT #2 BAR SCREEN A WITH RAKING DEVICE LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0DAI.AI104603.PNT)-(OPC.AW0003.0DAI.AI104604.PNT)
1910 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 1 | CIRCULATING WATER PUMP #2 A |  | 20PAA31CL901 | 20PAA31CL901 | 20PAA31CL901 | DP LEVEL UNIT #2 TRAVELLING BAND B SCREEN LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0DAI.AI104704.PNT)-(OPC.AW0003.0DAI.AI104704.PNT)
1911 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 2 | CIRCULATING WATER PUMP #2 B |  | 20PAA22CL901 | 20PAA22CL901 | 20PAA22CL901 | DP LEVEL UNIT #2 BAR SCREEN A WITH RAKING DEVICE LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0DAI.AI104705.PNT)-(OPC.AW0003.0DAI.AI104705.PNT)
1912 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 2 | CIRCULATING WATER PUMP #2 B |  | 20PAA32CL901 | 20PAA32CL901 | 20PAA32CL901 | DP LEVEL UNIT #2 TRAVELLING BAND B SCREEN LEVEL | CALC | -10 | 12 | m | [8 empty] | (OPC.AW0003.0DAI.AI104704.PNT)-(OPC.AW0003.0DAI.AI104704.PNT)
1913 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 |  | 20BBT01-901 | 20BBT01-901 | 20BBT01-901 | UAT HV SIDE CURRENT UNBALANCE PHASE A | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW2002.2SAI.AI242504.PNT)-(((OPC.AW2002.2SAI.AI242504.PNT)+(OPC.AW2002.2SAI.AI242505.PNT)+(OPC.AW2002.2SAI.AI242506.PNT))/3))/(((OPC.AW2002.2SAI.AI242504.PNT)+(OPC.AW2002.2SAI.AI242505.PNT)+(OPC.AW2002.2SAI.AI242506.PNT))/3))*100%
1914 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 |  | 20BBT01-902 | 20BBT01-902 | 20BBT01-902 | UAT HV SIDE CURRENT UNBALANCE PHASE B | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW2002.2SAI.AI242505.PNT)-((OPC.AW2002.2SAI.AI242504.PNT+OPC.AW2002.2SAI.AI242505.PNT+OPC.AW2002.2SAI.AI242506.PNT)/3))/((OPC.AW2002.2SAI.AI242504.PNT+OPC.AW2002.2SAI.AI242505.PNT+OPC.AW2002.2SAI.AI242506.PNT)/3))*100%
1915 | 2 | UJPCT #2 | 10 | ELECTRICAL SYSTEM #2 | 1 | TRANSFORMER UAT #2 |  | 20BBT01-903 | 20BBT01-903 | 20BBT01-903 | UAT HV SIDE CURRENT UNBALANCE PHASE C | CALC | 0 | 4 | % | [8 empty] | (((OPC.AW2002.2SAI.AI242506.PNT)-((OPC.AW2002.2SAI.AI242504.PNT+OPC.AW2002.2SAI.AI242505.PNT+OPC.AW2002.2SAI.AI242506.PNT)/3))/((OPC.AW2002.2SAI.AI242504.PNT+OPC.AW2002.2SAI.AI242505.PNT+OPC.AW2002.2SAI.AI242506.PNT)/3))*100%
1916 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 |  | 20LBQ10CP901 | 20LBQ10CP901 | 20LBQ10CP901 | Diff steam press HP turbine side and HPH side | CALC | 0 | 6.6 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212304.PNT)-(OPC.AW2002.2QAI.AI212404.PNT)
1917 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 |  | 20LAB30CT901 | 20LAB30CT901 | 20LAB30CT901 | DCA HPH1 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211704.PNT)-(OPC.AW2002.2QAI.AI211703.PNT)
1918 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 10 | HP HEATER NO.1 #2 |  | 20LBQ10CT904 | 20LBQ10CT904 | 20LBQ10CT904 | TTD HPH1 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211206.PNT)-(OPC.AW2002.2QAI.AI212103.PNT)
1919 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 |  | 20LBQ20CP901 | 20LBQ20CP901 | 20LBQ20CP901 | Diff steam press HPH2 side | CALC | 0 | 4 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212305.PNT)-(OPC.AW2002.2QAI.AI212405.PNT)
1920 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 |  | 20LAB20CT903 | 20LAB20CT903 | 20LAB20CT903 | DCA HPH2 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI212104.PNT)-(OPC.AW2002.2QAI.AI212102.PNT)
1921 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 8 | HP HEATER NO.2 #2 |  | 20LBQ20CT902 | 20LBQ20CT902 | 20LBQ20CT902 | TTD HPH2 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211401.PNT)-(OPC.AW2002.2QAI.AI212102.PNT)
1922 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 |  | 20LBQ30CP901 | 20LBQ30CP901 | 20LBQ30CP901 | Diff steam press HPH3 side | CALC | 0 | 1.9 | MPa | [8 empty] | (OPC.AW2002.2QAI.AI212306.PNT)-(OPC.AW2002.2QAI.AI212406.PNT)
1923 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 |  | 20LAB30CT903 | 20LAB30CT903 | 20LAB30CT903 | DCA HPH3 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211705.PNT)-(OPC.AW2002.2QAI.AI212102.PNT)
1924 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 6 | HP HEATER NO.3 #2 |  | 20LBQ30CT904 | 20LBQ30CT904 | 20LBQ30CT904 | TTD HPH3 #2 | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI211403.PNT)-(OPC.AW2002.2QAI.AI212102.PNT)
1925 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A |  | 20MAV50CT901 | 20MAV50CT901 | 20MAV50CT901 | DIFFERENTIAL TEMPERATUR BFP TURBINE A LUBE-OIL COOLER | CALC | -50 | 100 | C | [8 empty] | (OPC.AW2002.2QAI.AI210406.PNT)-(OPC.AW2002.2QAI.AI210506.PNT)
1926 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A |  | 20LAC11CT909 | 20LAC11CT909 | 20LAC11CT909 | T-BFP A WATER END MAIN BODY TOP DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2OAI.AI193305.PNT)-(OPC.AW2002.2OAI.AI193303.PNT)
1927 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 2 | T-BFP #2A |  | 20LAC11CT910 | 20LAC11CT910 | 20LAC11CT910 | T-BFP A WATER END MAIN BODY BOTTOM DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2OAI.AI193306.PNT)-(OPC.AW2002.2OAI.AI193304.PNT)
1928 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B |  | 20MAV60CT901 | 20MAV60CT901 | 20MAV60CT901 | DIFFERENTIAL TEMPERATUR BFP TURBINE B LUBE-OIL COOLER | CALC | -50 | 100 | C | [8 empty] | (OPC.AW2002.2PAI.AI202704.PNT)-(OPC.AW2002.2PAI.AI202702.PNT)
1929 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B |  | 20LAC12CT909 | 20LAC12CT909 | 20LAC12CT909 | T-BFP B WATER END MAIN BODY TOP DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2PAI.AI202705.PNT)-(OPC.AW2002.2PAI.AI202703.PNT)
1930 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B |  | 20LAC12CT910 | 20LAC12CT910 | 20LAC12CT910 | T-BFP B WATER END MAIN BODY BOTTOM DIFF TEMP | CALC | -50 | 200 | C | [8 empty] | (OPC.AW2002.2QAI.AI210604.PNT)-(OPC.AW2002.2QAI.AI210705.PNT)
1931 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2QAI.AI210101.PNT | 2QAI:AI210101.PNT | 20LCA11CT001 | CONDENSATE WATER PUMP INLET MAIN PIPE TEMPERATURE | RTD | 0 | 200 | C | [6 empty] | 44.7515 | ok
1932 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 3 | CEP #2B | F296S-J0201-07 | OPC.AW2002.2NAI.AI173803.PNT | 2NAI:AI173803.PNT | 20LCA13CP202 | CONDENSATE PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 4 | MPa |  |  | 1.3 |  |  |  | 2.7473 | ok
1933 | 2 | UJPCT #2 | 2 | CONDENSATE SYSTEM #2 | 5 | AIR REMOVAL #2 - VACUUM PUMP B | F296S-J0201-14 | OPC.AW2002.2RAI.AI230201.PNT | 2RAI:AI230201.PNT | 20PCB43CT001 | VACUUM PUMP COOLER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 26.2137 | ok
1934 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173804.PNT | 2NAI:AI173804.PNT | 20PCB22CP201 | CIRCULATING WATER BOOSTER PUMP OUTLET MAIN PIPE PRESS | AI | 0 | 0.4 | MPa | [6 empty] | 0.074227 | ok
1935 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 2 | SWBP #2B | F296S-J0201-14 | OPC.AW2002.2RAI.AI230101.PNT | 2RAI:AI230101.PNT | 20PCB22CT001 | MOTOR-DRIVERN FILTER OUTLET TEMP | RTD | 0 | 100 | C | [6 empty] | 25.4862 | ok
1936 | 2 | UJPCT #2 | 3 | CLOSE COOLING SYSTEM #2 | 6 | CCWP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI173805.PNT | 2NAI:AI173805.PNT | 20PGA20CP201 | CLOSED CIRCULATING-WATER PUMP MAIN PIPE OUTLET PRESS | AI | 0 | 0.8 | MPa |  |  | 0.5 |  |  |  | 0.54278 | ok
1937 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-04 | OPC.AW2002.2Q_FLOW.BFPSTMAIN.PNT | 2Q_FLOW:BFPSTMAIN.PNT | 20LBR10CF201 | BFP TURBINE INLET MAIN PIPE STEAM FLOW(COLD REHEAT STEAM) | AI | 0 | 25 | t/h | [6 empty] | -0.1191 | no
1938 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI212307.PNT | 2QAI:AI212307.PNT | 20LBS41CP201 | #4 EXTRACTION STEAM PIPE 2 PRESS | AI | 0 | 1 | MPa | [6 empty] | 0.5192 | ok
1939 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI211405.PNT | 2QAI:AI211405.PNT | 20LBS41CT001 | #4 EXTRACTION STEAM PIPE 1 TEMP (TURBINE SIDE) | TC | 0 | 500 | C | [6 empty] | 343.1463 | ok
1940 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI211307.PNT | 2QAI:AI211307.PNT | 20LBS41CT002 | #4 EXTRACTION STEAM PIPE 2 TOP TEMP | TC | 0 | 500 | C | [6 empty] | 222.2734 | ok
1941 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-05 | OPC.AW2002.2QAI.AI211407.PNT | 2QAI:AI211407.PNT | 20LBS41CT003 | #4 EXTRACTION STEAM PIPE 2 BOTTOM TEMP | TC | 0 | 500 | C | [6 empty] | 297.7211 | ok
1942 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-14 | OPC.AW2002.2NAI.AI172404.PNT | 2NAI:AI172404.PNT | 20PGA31AA001XB12 | BFP TURBINE LUBE-OIL COOLER RETURN WATER MOTORIZED VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 85.9727 | ok
1943 | 2 | UJPCT #2 | 4 | FEEDWATER SYSTEM #2 | 4 | T-BFP #2B | F296S-J0201-14 | OPC.AW2002.2RAI.AI230205.PNT | 2RAI:AI230205.PNT | 20PGA31CT003 | BFP TURBINE LUBE-OIL COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 30.2798 | ok
1944 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-19 | OPC.AW2002.2QAI.AI213404.PNT | 2QAI:AI213404.PNT | 20MAV00CP203 | HYDROGEN SEAL OIL PRESS | AI | 0 | 0.6 | MPa | [6 empty] | 0.023895 | ok
1945 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2PAI.AI203602.PNT | 2PAI:AI203602.PNT | 20MKW10CL201 | GENERATOR H2 SIDE SEAL OIL TANK LEVEL | AI | 0 | 1000 | mm |  |  | 300 | 600 |  |  | 367.6289 | ok
1946 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2RAI.AI231204.PNT | 2RAI:AI231204.PNT | 20MKW10CP201 | GENERATOR H2 SIDE SEAL OIL PRESS | AI | 0 | 2 | MPa | [6 empty] | 0.38125 | ok
1947 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230305.PNT | 2RAI:AI230305.PNT | 20MKW10CT002 | GENERATOR H2 SIDE RETURN OIL TEMP(TURBINE SIDE) | RTD | 0 | 100 | C | [6 empty] | 51.9094 | ok
1948 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230405.PNT | 2RAI:AI230405.PNT | 20MKW10CT003 | GENERATOR H2 SIDE RETURN OIL TEMP(EXCITER SIDE) | RTD | 0 | 100 | C | [6 empty] | 60.7172 | ok
1949 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 2 | GENERATOR SEAL OIL - H2 SIDE #2B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230307.PNT | 2RAI:AI230307.PNT | 20MKW20CT001 | GENERATOR H2 SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 30.6046 | ok
1950 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 4 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230404.PNT | 2RAI:AI230404.PNT | 20MKW10CT001 | GENERATOR AIR SIDE SEAL OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 40.2048 | ok
1951 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 4 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230306.PNT | 2RAI:AI230306.PNT | 20MKW10CT004 | GENERATOR TURBINE SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 55.0532 | ok
1952 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 4 | GENERATOR SEAL OIL #2 - AIR SIDE PUMP B | F296S-J0201-25 | OPC.AW2002.2RAI.AI230406.PNT | 2RAI:AI230406.PNT | 20MKW10CT005 | GENERATOR EXCITER SIDE AIR SIDE SEAL RETURN OIL TEMP | RTD | 0 | 100 | C | [6 empty] | 51.0261 | ok
1953 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2M_GESTAT.AO162608.OUT | 2M_GESTAT:AO162608.OUT | 20MKF10AA101XB11 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE CONTROL COMMAND | AO | 0 | 100 | % | [6 empty] | 0 | ok
1954 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2MAI.AI162304.PNT | 2MAI:AI162304.PNT | 20MKF10AA101XB12 | GENERATOR STATOR COOLING WATER TEMP CONTROL VALVE POSITION | AI | 0 | 100 | % | [6 empty] | 0.25781 | ok
1955 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2R_FLOW.GENAIN.PNT | 2R_FLOW:GENAIN.PNT | 20MKF10CF201 | GENERATOR STATOR COOLING WATER INLET FLOW | AI | 0 | 50 | t/h |  |  | 5 | 45 |  |  | 50.4966 | no
1956 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2RAI.AI231501.PNT | 2RAI:AI231501.PNT | 20MKF10CQ201 | GENERATOR STATOR COOLING WATER CONDUCTIVITY | AI | 0 | 10 | μs/cm |  |  |  | 2 |  |  | 1.3152 | ok
1957 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2RAI.AI231402.PNT | 2RAI:AI231402.PNT | 20MKF10CQ202 | GENERATOR DEMINERALIZER COOLING WATER CONDUCTIVITY | AI | 0 | 2.5 | μs/cm |  |  |  | 0.5 |  |  | 12.6789 | no
1958 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2MAI.AI160101.PNT | 2MAI:AI160101.PNT | 20MKF10CT001 | GENERATOR STATOR COOLING WATER INLET TEMP | RTD | 0 | 50 | C |  |  |  | 48 |  |  | 43.7512 | ok
1959 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2NAI.AI172206.PNT | 2NAI:AI172206.PNT | 20MKF11AH001XB12 | TURBINE FLAGE&BOLT HEATER CURRENT | AI | 0 | 100 | A | [8 empty] | TIDAK DIPAKAI
1960 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2RAI.AI231103.PNT | 2RAI:AI231103.PNT | 20MKF12CP201 | GENERATOR STATOR COOLING WATER INLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.1945 | ok
1961 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2RAI.AI231203.PNT | 2RAI:AI231203.PNT | 20MKF21CP201 | GENERATOR STATOR COOLING WATER OUTLET PRESS | AI | 0 | 0.25 | MPa | [6 empty] | 0.045176 | ok
1962 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-24 | OPC.AW2002.2RAI.AI230304.PNT | 2RAI:AI230304.PNT | 20MKF21CT001 | GENERATOR STATOR COOLING WATER OUTLET TEMP | RTD | 0 | 100 | C |  |  |  | 80 |  |  | 47.5445 | ok
1963 | 2 | UJPCT #2 | 9 | GENERATOR SYSTEM #2 | 7 | GENERATOR STATOR COOLING #2B | F296S-J0201-14 | OPC.AW2002.2RAI.AI230206.PNT | 2RAI:AI230206.PNT | 20PGA32CT001 | GENERATOR STATOR WATER COOLER OUTLET TEMP | RTD | 0 | 50 | C | [6 empty] | 44.5827 | ok
1964 | 2 | UJPCT #2 | 82 | LUBRICATION SUPPLY SYSTEM #2 | 9 | JACKING OIL B #2 | F296S-J0201-40 | OPC.AW2002.2RAI.AI231205.PNT | 2RAI:AI231205.PNT | 20MAV18CP216 | JACKING PUMP OUTLET MAIN PIPE OIL PRESS | AI | 0 | 25 | MPa | [6 empty] | 0.025879 | ok
1965 | 3 | UJPCT COMMON | 2 | COOLING WATER SYSTEM #2 | 4 | CIRCULATING WATER PUMP #2 B | K0802-02 | OPC.AW0003.0DAI.AI105103.PNT | 0DAI:AI105103.PNT | 20PAB11CF201 | UNIT 2 CIRCULATING WATER OUTLET WATER FLOW | AI | 0 |  | t/h | [6 empty] | -1.5742 | no
1769 | 2 | UJPCT #2 | 86 | TURBINE #2 | 1 | HP TURBINE SYSTEM #2 | F296Z-J0201-43 | 20MAA10CT906 | 20MAA10CT906 | 20MAA10CT906 | DELTA HP INNER CYLINDER UPPER BOTTOM HALF INNER WALL TEMP | TC | 0 | 600 | C | [8 empty] | AVG((OPC.AW2002.2ATC.2BD107AIN.PNT_4);(OPC.AW2002.2ATC.2BD107AIN.PNT_5))